## BuildingSummary
Building Summary Large Office new construction version 1.1_3.1
|  | Value | Data Source
Program
| Building Name | Benchmark Large Office
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 46320 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 12 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.38
| East | 0.38
| North | 0.38
| West | 0.38
| Total | 0.38
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor
| Floor to Ceiling Height (m) | 2.74
| Floor to Floor Height (m) | 3.96
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 11589.72
| Net Dimensions - Total Area (m2) | 6953.64
| Wall to Skin Ratio | 0.765
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 3563
| Net Dimensions - Total Area (m2) | 3563
| Roof to Skin Ratio | 0.235
Window Dimensions (m2)
| South | 1390.85
| East | 927.23
| North | 1390.85
| West | 927.23
| Total Area (m2) | 4636.16
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 3563
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 8523.53
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 92640.76
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.11 | See Benchmark Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Gas boiler | 2003 CBECS
| Cooling Type | Water cooled chiller | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | boiler
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 1504

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 3563.11 | 8690.42 | 2.439 | 0 | 0 | 37.1613 | 95.8824 | 10.76 | 4.842 | 0 | 0 | 10 | 0 | 958.824 | 0 | 0
Perimeter_bot_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8676 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6757 | 0 | 0.25388
Perimeter_bot_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.26264
Perimeter_bot_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8681 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6811 | 0 | 0.25387
Perimeter_bot_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.26264
Core_bottom | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 10.76 | 8.07 | 0 | 80.629 | 10 | 0 | 1362.882 | 0 | 0
Perimeter_mid_ZN_3 | Yes | 10 | 313.41 | 860 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8676 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6757 | 0 | 0.25388
Perimeter_mid_ZN_2 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.26264
Perimeter_mid_ZN_1 | Yes | 10 | 313.42 | 860.02 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8681 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6811 | 0 | 0.25387
Perimeter_mid_ZN_4 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.26264
Core_mid | Yes | 10 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 10.76 | 8.07 | 0 | 80.629 | 10 | 0 | 1362.882 | 0 | 0
Perimeter_top_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8676 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6757 | 0 | 0.65051
Perimeter_top_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.65928
Perimeter_top_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8681 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6811 | 0 | 0.65051
Perimeter_top_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.65928
Core_top | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 10.76 | 8.07 | 0 | 80.629 | 10 | 0 | 1362.882 | 0 | 0.39663
Groundfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.11 | 0 | [10 empty] | 0.074437
Midfloor_plenum | No | 10 | 3563.11 | 4344.14 | 1.2192 | 297.11 | 0 | [10 empty] | 0.074437
Topfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.11 | 0 | [10 empty] | 0.96713
Total Conditioned Zones |  |  | 46320.43 | 178145.9 |  | 11589.72 | 4636.08 |  | 2397.06 |  |  |  | 967.5482 |  |  | 23970.5998
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 4.7 | 40.9 | 9.2 | 45.9 | 52.3 | 5.8 | 2.4 | 104 | 2.6 | 13.1 | 92.3 | 20.8 | 26.2 | 3.1 | 3.6 | 0.18
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.38314 | 0.38314 | 0.38314 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9531 | 2.2026
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 0.38314 | 0.38314 | 0.38314 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9531 | 2.2026
Window
| U-Factor (W / m2·K) | 6.49 | 6.49 | 6.49 | 3.18 | 3.18 | 3.18 | 6.49 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 2.58
| SHGC | 0.441 | 0.61 | 0.61 | 0.402 | 0.402 | 0.402 | 0.61 | 0.501 | 0.501 | 0.501 | 0.501 | 0.501 | 0.501 | 0.501 | 0.651 | 0.654
| Visible transmittance | 0.44 | 0.61 | 0.61 | 0.622 | 0.622 | 0.622 | 0.61 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.64 | 0.64
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 4280.1017 | 4252.3868 | 4264.5411 | 3978.8472 | 3296.7473 | 6975.159 | 3159.9195 | 4305.9416 | 6531.0028 | 3511.7169 | 4249.8228 | 3346.1064 | 4162.5622 | 6129.0938 | 3924.4059 | 3695.4517
Heating (kW)
| HEATSYS1 BOILER | 4477.3937 | 4884.1924 | 5251.6616 | 4755.7204 | 4264.2559 | 4908.8737 | 4322.0532 | 5306.8816 | 4860.5214 | 4839.7664 | 5493.8784 | 5011.579 | 5636.8311 | 5334.6893 | 5708.4793 | 6391.9251
HVAC Efficiency
| Air Conditioning (COP) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
| Heating Efficiency (%) | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
HVAC Control - Economizer
| VAV_5_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| VAV_5_FAN | 7.57 | 7.39 | 5.89 | 7.24 | 6.96 | 5.56 | 4.41 | 6.99 | 6.82 | 5.23 | 6.79 | 6.57 | 6.72 | 6.07 | 5.24 | 4.17
| VAV_1_FAN | 16.65 | 17.4 | 19.62 | 17.3 | 16.27 | 18.86 | 15.99 | 18.36 | 21.22 | 17.64 | 18.53 | 20.82 | 18.67 | 19.94 | 19.19 | 19.33
| VAV_2_FAN | 183 | 191.06 | 226.64 | 185.24 | 174.27 | 212.89 | 174.98 | 200.67 | 229.06 | 191.25 | 200.95 | 226.17 | 202.87 | 217.41 | 210 | 217.12
| VAV_3_FAN | 26.92 | 28.02 | 32.65 | 27.85 | 25.15 | 31.45 | 24.46 | 28.44 | 33.83 | 26.64 | 28.46 | 32.56 | 28.46 | 30.93 | 28.79 | 27.83
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.085532 | 0.10925 | 0.07973 | 0.097758 | 0.059096 | 0.099126 | 0.15528 | 0.070978 | 0.036967 | 0.074208 | 0.085932 | 0.036972 | 0.062615 | 0.080082 | 0.063064 | 0.1013
| Total Cost ($/m2) | 10.24 | 12.58 | 8.96 | 10.38 | 5.74 | 11.25 | 13.56 | 7.69 | 3.93 | 6.44 | 8.4 | 3.47 | 6.1 | 7.81 | 5.85 | 9.22
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011406 | 0.0080534 | 0.0081793 | 0.0095675 | 0.0086278 | 0.0076699 | 0.0085728 | 0.0096897 | 0.0068935 | 0.0084297 | 0.0083181 | 0.0069107 | 0.0078882 | 0.0080669 | 0.0078744 | 0.0041125
| Total Cost ($/m2) | 0.1 | 0.52 | 0.45 | 0.58 | 0.17 | 0.31 | 0.63 | 1 | 0.43 | 0.87 | 1.16 | 0.66 | 1.46 | 1.2 | 1.73 | 1.54
Total Utility Costs
| Cost Intensity ($/m2) | 10.34 | 13.1 | 9.41 | 10.96 | 5.9 | 11.57 | 14.19 | 8.69 | 4.36 | 7.31 | 9.56 | 4.13 | 7.56 | 9.01 | 7.58 | 10.77
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 1404316.6667 | 1191177.7778 | 1032563.8889 | 861297.2222 | 583908.3333 | 913175 | 250450 | 875866.6667 | 666763.8889 | 243413.8889 | 559277.7778 | 437244.4444 | 529275 | 398947.2222 | 363119.4444 | 307777.7778
| Interior Lighting | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889
| Exterior Lighting | 17477.7778 | 17447.2222 | 17444.4444 | 17472.2222 | 17469.4444 | 17452.7778 | 17433.3333 | 17450 | 17447.2222 | 17422.2222 | 17427.7778 | 17430.5556 | 17441.6667 | 17419.4444 | 17413.8889 | 17311.1111
| Interior Equipment | 1857736.1111 | 1857736.1111 | 1857736.1111 | 1857736.1111 | 1857736.1111 | 1857736.1111 | 1857736.1111 | 1857736.1111 | 1857736.1111 | 1857736.1111 | 1857736.1111 | 1857736.1111 | 1857736.1111 | 1857736.1111 | 1857736.1111 | 1857736.1111
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 264669.4444 | 265002.7778 | 328455.5556 | 247633.3333 | 218936.1111 | 302288.8889 | 215311.1111 | 268975 | 325302.7778 | 241738.8889 | 275488.8889 | 310063.8889 | 288763.8889 | 300319.4444 | 300925 | 320894.4444
| Pumps | 318597.2222 | 327841.6667 | 300552.7778 | 296763.8889 | 214058.3333 | 418988.8889 | 156213.8889 | 359647.2222 | 389994.4444 | 134716.6667 | 269180.5556 | 198633.3333 | 278644.4444 | 375588.8889 | 254366.6667 | 229800
| Heat Rejection | 257144.4444 | 246516.6667 | 243500 | 211425 | 176505.5556 | 321488.8889 | 120080.5556 | 209080.5556 | 241361.1111 | 94627.7778 | 123152.7778 | 105172.2222 | 114919.4444 | 142630.5556 | 77022.2222 | 57177.7778
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 5546980.5556 | 5332763.8889 | 5207291.6667 | 4919366.6667 | 4495650 | 5258172.2222 | 4044266.6667 | 5015797.2222 | 4925647.2222 | 4016697.2222 | 4529302.7778 | 4353322.2222 | 4513822.2222 | 4519683.3333 | 4297625 | 4217738.8889
Gas (MJ)
| Heating | 235590 | 2776280 | 2336610 | 2578660 | 664640 | 1684080 | 3140690 | 4512870 | 2647540 | 4512830 | 6173790 | 4108620 | 8259400 | 6580590 | 9828000 | 16990650
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 172390 | 206270 | 186700 | 239000 | 232760 | 210220 | 260730 | 264720 | 259860 | 278190 | 287320 | 286140 | 306840 | 310390 | 339030 | 377930
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 407980 | 2982550 | 2523310 | 2817660 | 897390 | 1894300 | 3401420 | 4777580 | 2907400 | 4791030 | 6461110 | 4394760 | 8566240 | 6890980 | 10167020 | 17368580
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 20377110 | 22180500 | 21269560 | 20527380 | 17081740 | 20823720 | 17960780 | 22834460 | 20639730 | 19251140 | 22766600 | 20066730 | 24816000 | 23161850 | 25638480 | 32552440
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 109.1429 | 92.5778 | 80.2504 | 66.9396 | 45.3811 | 70.9716 | 19.4649 | 68.072 | 51.8206 | 18.918 | 43.4668 | 33.9825 | 41.135 | 31.006 | 28.2215 | 23.9204
| Interior Lighting (elec) | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088
| Exterior Lighting (elec) | 1.3584 | 1.356 | 1.3558 | 1.3579 | 1.3577 | 1.3564 | 1.3549 | 1.3562 | 1.356 | 1.354 | 1.3545 | 1.3547 | 1.3556 | 1.3538 | 1.3534 | 1.3454
| Interior Equipment (elec) | 144.3825 | 144.3825 | 144.3825 | 144.3825 | 144.3825 | 144.3825 | 144.3825 | 144.3825 | 144.3825 | 144.3825 | 144.3825 | 144.3825 | 144.3825 | 144.3825 | 144.3825 | 144.3825
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 20.57 | 20.5959 | 25.5274 | 19.246 | 17.0156 | 23.4938 | 16.7339 | 20.9046 | 25.2824 | 18.7878 | 21.4109 | 24.098 | 22.4426 | 23.3407 | 23.3878 | 24.9398
| Pumps (elec) | 24.7612 | 25.4797 | 23.3588 | 23.0644 | 16.6365 | 32.5636 | 12.1409 | 27.9516 | 30.3102 | 10.4701 | 20.9206 | 15.4377 | 21.6561 | 29.1906 | 19.7693 | 17.86
| Heat Rejection (elec) | 19.9852 | 19.1592 | 18.9247 | 16.4319 | 13.7179 | 24.986 | 9.3326 | 16.2497 | 18.7585 | 7.3544 | 9.5714 | 8.1739 | 8.9315 | 11.0852 | 5.9861 | 4.4438
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 431.1089 | 414.4601 | 404.7085 | 382.3311 | 349.4 | 408.6629 | 314.3187 | 389.8256 | 382.8192 | 312.176 | 352.0155 | 338.3383 | 350.8123 | 351.2678 | 334.0096 | 327.8009
Gas (MJ/m2)
| Heating (gas) | 5.0861 | 59.9365 | 50.4445 | 55.6701 | 14.3488 | 36.3572 | 67.8036 | 97.4273 | 57.1571 | 97.4264 | 133.2845 | 88.7 | 178.3103 | 142.0668 | 212.1744 | 366.8072
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 3.7217 | 4.4531 | 4.0306 | 5.1597 | 5.025 | 4.5384 | 5.6288 | 5.715 | 5.6101 | 6.0058 | 6.2029 | 6.1774 | 6.6243 | 6.7009 | 7.3192 | 8.159
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 8.8078 | 64.3896 | 54.4752 | 60.8298 | 19.3735 | 40.8956 | 73.4325 | 103.1421 | 62.7672 | 103.4324 | 139.4874 | 94.8775 | 184.9346 | 148.7678 | 219.4934 | 374.9663
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 439.9167 | 478.8497 | 459.1836 | 443.1609 | 368.7737 | 449.5585 | 387.7511 | 492.9679 | 445.5864 | 415.6084 | 491.5029 | 433.216 | 535.7469 | 500.0358 | 553.5032 | 702.7671
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 1378.7681 | 1345.809 | 1266.4538 | 1214.5901 | 1215.4727 | 1306.5138 | 1055.3746 | 1242.1522 | 1205.6801 | 1053.8598 | 1080.4101 | 1167.6818 | 1073.9676 | 1122.2746 | 1062.6637 | 1087.4318
| Feb | 1400.6952 | 1299.6461 | 1285.2282 | 1243.287 | 1203.5533 | 1355.6213 | 1171.809 | 1208.2507 | 1365.6133 | 1139.8168 | 1079.4273 | 1107.5666 | 1051.1268 | 1131.6427 | 1079.439 | 1074.4204
| Mar | 1408.4073 | 1344.7973 | 1337.763 | 1255.2954 | 1213.6108 | 1407.7615 | 1126.5829 | 1284.665 | 1384.98 | 1185.1789 | 1237.6239 | 1223.6709 | 1166.5087 | 1335.6883 | 1083.3847 | 1065.4018
| Apr | 1454.4439 | 1376.4286 | 1358.4752 | 1307.8027 | 1241.5091 | 1464.3787 | 1184.1031 | 1296.5591 | 1448.9398 | 1150.2711 | 1250.1342 | 1258.1905 | 1248.1497 | 1283.3273 | 1170.7567 | 1103.9851
| May | 1543.9018 | 1531.1105 | 1435.2867 | 1390.4311 | 1343.0811 | 1512.3882 | 1196.2983 | 1385.458 | 1480.7964 | 1258.9139 | 1463.021 | 1299.2315 | 1364.9617 | 1379.3612 | 1277.6162 | 1227.3463
| Jun | 1608.6474 | 1520.2318 | 1566.2057 | 1427.9368 | 1294.773 | 1665.6337 | 1216.0063 | 1519.8182 | 1620.4234 | 1284.4103 | 1515.1116 | 1420.5602 | 1483.2547 | 1492.0413 | 1395.6721 | 1333.8287
| Jul | 1593.7439 | 1647.3617 | 1601.8067 | 1514.1804 | 1339.8378 | 1670.215 | 1264.4592 | 1571.584 | 1613.8681 | 1317.006 | 1513.8766 | 1412.9004 | 1502.4398 | 1574.1756 | 1541.5797 | 1329.2927
| Aug | 1623.8058 | 1590.8821 | 1559.7852 | 1475.8828 | 1444.0362 | 1662.0392 | 1234.0948 | 1607.2585 | 1619.8067 | 1305.7634 | 1558.9088 | 1429.2773 | 1514.1855 | 1542.6813 | 1410.174 | 1296.3595
| Sep | 1555.9773 | 1541.677 | 1529.7257 | 1428.249 | 1335.0362 | 1649.8286 | 1296.3403 | 1382.8335 | 1565.9501 | 1297.8367 | 1453.1545 | 1398.8035 | 1400.2645 | 1445.6083 | 1425.4374 | 1145.4729
| Oct | 1524.7177 | 1454.7694 | 1442.4674 | 1314.4268 | 1268.5495 | 1481.028 | 1206.36 | 1354.4565 | 1439.6787 | 1214.5794 | 1363.5327 | 1288.3494 | 1262.9289 | 1377.489 | 1204.3196 | 1096.6308
| Nov | 1437.9539 | 1375.5111 | 1321.8287 | 1254.6256 | 1224.3044 | 1382.9131 | 1144.9768 | 1311.504 | 1318.3688 | 1127.1363 | 1383.5916 | 1219.2116 | 1191.7347 | 1144.5835 | 1080.2935 | 1097.9638
| Dec | 1366.5163 | 1333.7747 | 1262.4763 | 1263.7091 | 1223.4011 | 1359.406 | 1062.691 | 1186.6339 | 1196.3746 | 1058.3682 | 1073.8643 | 1091.7942 | 1068.1508 | 1122.1531 | 1073.5573 | 1049.3694
Time of Peak Electrical Demand
| Jan | 23-JAN-08:00 | 03-JAN-08:00 | 27-JAN-13:00 | 24-JAN-16:00 | 26-JAN-13:15 | 18-JAN-13:00 | 17-JAN-13:00 | 09-JAN-08:00 | 26-JAN-16:15 | 31-JAN-08:00 | 24-JAN-08:45 | 24-JAN-13:00 | 30-JAN-08:15 | 20-JAN-08:00 | 13-JAN-08:00 | 18-JAN-08:15
| Feb | 23-FEB-13:30 | 21-FEB-08:45 | 28-FEB-16:30 | 21-FEB-08:00 | 13-FEB-12:30 | 08-FEB-13:00 | 14-FEB-13:15 | 15-FEB-13:00 | 14-FEB-16:15 | 21-FEB-13:00 | 13-FEB-08:30 | 07-FEB-13:00 | 28-FEB-08:15 | 03-FEB-15:15 | 24-FEB-08:00 | 27-FEB-08:00
| Mar | 13-MAR-15:30 | 29-MAR-07:00 | 17-MAR-15:00 | 30-MAR-07:00 | 31-MAR-15:15 | 31-MAR-15:15 | 01-MAR-13:30 | 10-MAR-08:00 | 02-MAR-13:00 | 29-MAR-15:30 | 31-MAR-15:15 | 30-MAR-15:00 | 23-MAR-15:00 | 30-MAR-15:00 | 17-MAR-07:00 | 31-MAR-07:15
| Apr | 03-APR-15:15 | 24-APR-07:00 | 17-APR-15:30 | 20-APR-15:00 | 11-APR-15:00 | 21-APR-15:15 | 13-APR-15:15 | 04-APR-07:45 | 21-APR-15:30 | 14-APR-15:15 | 07-APR-12:00 | 26-APR-15:45 | 14-APR-15:45 | 06-APR-15:00 | 04-APR-15:15 | 28-APR-07:45
| May | 15-MAY-07:00 | 30-MAY-07:00 | 31-MAY-15:00 | 31-MAY-15:00 | 30-MAY-12:00 | 31-MAY-15:00 | 26-MAY-12:00 | 31-MAY-15:00 | 31-MAY-15:00 | 04-MAY-15:15 | 30-MAY-07:00 | 23-MAY-15:00 | 31-MAY-07:00 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-15:15
| Jun | 26-JUN-15:30 | 29-JUN-15:00 | 28-JUN-15:00 | 08-JUN-15:30 | 29-JUN-07:00 | 28-JUN-12:00 | 16-JUN-15:00 | 30-JUN-15:00 | 29-JUN-15:30 | 28-JUN-15:15 | 08-JUN-12:00 | 27-JUN-15:15 | 29-JUN-15:15 | 30-JUN-12:00 | 14-JUN-10:45 | 20-JUN-15:00
| Jul | 05-JUL-07:00 | 18-JUL-12:00 | 11-JUL-15:00 | 03-JUL-12:15 | 24-JUL-15:15 | 26-JUL-12:00 | 03-JUL-12:00 | 25-JUL-12:00 | 03-JUL-15:45 | 31-JUL-15:00 | 14-JUL-12:00 | 17-JUL-12:45 | 14-JUL-07:30 | 21-JUL-15:45 | 07-JUL-07:45 | 12-JUL-15:30
| Aug | 21-AUG-15:15 | 31-AUG-15:00 | 02-AUG-15:15 | 14-AUG-15:30 | 16-AUG-15:00 | 02-AUG-15:30 | 15-AUG-12:30 | 09-AUG-15:15 | 01-AUG-15:30 | 07-AUG-15:15 | 04-AUG-15:30 | 30-AUG-15:30 | 17-AUG-07:00 | 09-AUG-15:00 | 11-AUG-15:30 | 15-AUG-15:15
| Sep | 11-SEP-15:15 | 15-SEP-15:30 | 05-SEP-07:15 | 05-SEP-15:00 | 08-SEP-07:00 | 01-SEP-12:00 | 28-SEP-15:15 | 13-SEP-15:30 | 21-SEP-15:30 | 01-SEP-15:45 | 07-SEP-12:00 | 01-SEP-15:30 | 22-SEP-15:00 | 01-SEP-15:00 | 08-SEP-12:15 | 07-SEP-15:00
| Oct | 06-OCT-15:30 | 30-OCT-08:00 | 03-OCT-07:00 | 02-OCT-12:00 | 05-OCT-15:00 | 06-OCT-12:00 | 31-OCT-13:15 | 03-OCT-07:00 | 11-OCT-15:30 | 17-OCT-12:00 | 31-OCT-08:00 | 05-OCT-15:15 | 06-OCT-15:15 | 06-OCT-15:30 | 27-OCT-12:00 | 05-OCT-07:45
| Nov | 01-NOV-08:00 | 27-NOV-08:00 | 13-NOV-13:00 | 22-NOV-08:00 | 08-NOV-08:00 | 10-NOV-13:45 | 16-NOV-16:15 | 03-NOV-13:00 | 01-NOV-13:00 | 03-NOV-13:00 | 02-NOV-08:00 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-08:00 | 17-NOV-08:15 | 14-NOV-08:45
| Dec | 15-DEC-08:00 | 20-DEC-08:00 | 11-DEC-13:00 | 26-DEC-08:00 | 19-DEC-13:15 | 05-DEC-13:00 | 01-DEC-13:00 | 08-DEC-08:00 | 05-DEC-13:00 | 29-DEC-08:45 | 11-DEC-08:45 | 06-DEC-08:30 | 26-DEC-08:15 | 21-DEC-08:45 | 26-DEC-08:15 | 19-DEC-08:15
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 21463.36 | 18283.91 | 29705.1 | 14437.85 | 9912.9 | 37009.02 | 5186.06 | 14321.5 | 23064.77 | 4981.03 | 9507.83 | 10929.48 | 8497.49 | 11770.58 | 5297.76 | 4135.01
| Water Systems | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95
| Total Building | 22967.31 | 19787.86 | 31209.05 | 15941.79 | 11416.85 | 38512.97 | 6690 | 15825.45 | 24568.72 | 6484.97 | 11011.78 | 12433.42 | 10001.44 | 13274.52 | 6801.71 | 5638.95
Emissions
| Carbon Equivalent (kg) | 1528620 | 1832590 | 1617460 | 1566160 | 541570.3592 | 1807610 | 533973.2655 | 1439690 | 2064550 | 378947.8383 | 2531310 | 1857570 | 1699520 | 1775930 | 1654390 | 1500020
| CO2 (kg) | 3543810 | 4618910 | 3828220 | 3586030 | 1449450 | 4299130 | 1439070 | 3284270 | 4839900 | 944565.5942 | 5908210 | 4372630 | 4008250 | 4200570 | 3921040 | 3877900
| NOX (kg) | 6231.6947 | 6007.9683 | 6367.4779 | 6774.4214 | 1242.8396 | 6978.0166 | 1240.7547 | 6294.8948 | 8363.5466 | 1343.2256 | 10450.887 | 7478.0957 | 6905.0856 | 7145.0621 | 6669.4819 | 4546.1346
| SO2 (kg) | 23743.4089 | 25438.0836 | 20940.2389 | 17267.7348 | 13082.0465 | 28924.6616 | 11769.2418 | 18310.95 | 21510.092 | 3105.8706 | 30525.6115 | 19011.2682 | 10655.6359 | 12069.9459 | 10145.8101 | 21474.6321
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.1082 | 0.0718 | 0.057 | 0.0633 | 0.0059 | 0.0544 | 0.0056 | 0.0743 | 0.0841 | 0.0126 | 0.0927 | 0.0745 | 0.0786 | 0.0844 | 0.0751 | 0.0745
| Water for Electricity (m3) | 2938.56 | 8677.03 | 154679 | 30714.6 | 78933.6 | 144253 | 71008.3 | 1138.77 | 22366.4 | 41037.8 | 7026.94 | 19767.6 | 7002.92 | 286296 | 6667.51 | 4309.18

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 20377.11 | 439.92 | 439.92
Net Site Energy | 20377.11 | 439.92 | 439.92
Total Source Energy | 66683.13 | 1439.61 | 1439.61
Net Source Energy | 66683.13 | 1439.61 | 1439.61
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 235.59 | 0 | 0 | 0 | 0
Cooling | 5055.54 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.92 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6687.85 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 952.81 | 0 | 0 | 0 | 0 | 0
Pumps | 1146.95 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 925.72 | 0 | 0 | 0 | 0 | 21463.36
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 172.39 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 19969.13 | 407.98 | 0 | 0 | 0 | 22967.31
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.17 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 95.067
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.17 | 6.5404
Conditioned Total | 46320.38 |  | 126016.37 |  | 8024.24 | 4636.15 | 10.76 | 19.33 | 12.5776
Unconditioned Total | 42757.27 |  | 52129.67 |  | 3565.29 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 115.9 | 115.9 | 6.49 | 0.441 | 0.44 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 77.27 | 77.27 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 115.9 | 115.9 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 77.27 | 77.27 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 115.9 | 1159.04 | 6.49 | 0.441 | 0.44 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 77.27 | 772.69 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 115.9 | 1159.04 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 77.27 | 772.69 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 115.9 | 115.9 | 6.49 | 0.441 | 0.44 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 77.27 | 77.27 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 115.9 | 115.9 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 77.27 | 77.27 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 6.49 | 0.307 | 0.307
North Total or Average |  |  | 1390.85 | 6.49 | 0.441 | 0.44
Non-North Total or Average |  |  | 3245.31 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4280101.7 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 4477393.74 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 4046641.61
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_5_COOLC | Coil:Cooling:Water | 142434.93 | - | - | - | -
VAV_1_COOLC | Coil:Cooling:Water | 313913.05 | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water | 3369697.91 | - | - | - | -
VAV_3_COOLC | Coil:Cooling:Water | 454055.81 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_5_HEATC | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_3_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_5_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 7.57 | 17499.63 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 16.65 | 37997.84 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 183 | 411428.26 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.61 | 1572.42 | 26.92 | 68917.59 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 25589.38 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 39221.21 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 57112.7 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 279274.1184 | 487.3138 | 1841.3592 | 0 | 0.0084 | 227889.4836 | 120085.3216
February | 253610.3546 | 444.6012 | 1688.4317 | 0 | 0.0077 | 208964.5091 | 109257.4372
March | 296051.7237 | 519.8248 | 1977.4434 | 0 | 0.009 | 244733.9458 | 127623.706
April | 278368.6489 | 490.2166 | 1870.6716 | 0 | 0.0085 | 231520.6485 | 120145.1534
May | 311729.1692 | 549.103 | 2095.9392 | 0 | 0.0096 | 259400.631 | 134557.4624
June | 317075.0059 | 558.5997 | 2132.5136 | 0 | 0.0097 | 263927.2624 | 136873.0207
July | 317074.3206 | 558.6337 | 2132.7857 | 0 | 0.0097 | 263960.9652 | 136876.2477
August | 338863.0881 | 597.005 | 2279.2134 | 0 | 0.0104 | 282083.3524 | 146280.4343
September | 305968.4155 | 539.0067 | 2057.6087 | 0 | 0.0094 | 254656.7527 | 132075.9644
October | 298376.9779 | 525.4926 | 2005.4499 | 0 | 0.0091 | 248201.2874 | 128784.9087
November | 278460.9454 | 490.205 | 1869.921 | 0 | 0.0085 | 231427.623 | 120167.5371
December | 268957.9246 | 471.6926 | 1792.0714 | 0 | 0.0082 | 221791.3621 | 115887.9102
Annual Sum or Average | 3543810 | 6231.6947 | 23743.4089 | 0 | 0.1082 | 2938560 | 1528620
Minimum of Months | 253610.3546 | 444.6012 | 1688.4317 | 0 | 0.0077 | 208964.5091 | 109257.4372
Maximum of Months | 338863.0881 | 597.005 | 2279.2134 | 0 | 0.0104 | 282083.3524 | 146280.4343
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1548640000000 | 1378768.127 | 23-JAN-08:00 | 448566.543 | 473785.475 | 53375.024 | 0 | 284136.591 | 0 | 65792.322 | 53112.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1420030000000 | 1400695.157 | 23-FEB-13:30 | 448566.543 | 423230.021 | 66996.539 | 0 | 341109.587 | 0 | 67680.296 | 53112.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1663100000000 | 1408407.264 | 13-MAR-15:30 | 448566.543 | 418415.216 | 66448.48 | 0 | 353971.365 | 0 | 67893.489 | 53112.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1573310000000 | 1454443.896 | 03-APR-15:15 | 448566.543 | 418415.216 | 83992.212 | 0 | 381028.857 | 0 | 69328.897 | 53112.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1762770000000 | 1543901.774 | 15-MAY-07:00 | 448566.543 | 473785.475 | 78652.662 | 0 | 419889.948 | 0 | 69894.975 | 53112.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1793530000000 | 1608647.393 | 26-JUN-15:30 | 448566.543 | 418415.216 | 87400.09 | 0 | 529222.73 | 0 | 71930.643 | 53112.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1793760000000 | 1593743.942 | 05-JUL-07:00 | 448566.543 | 473785.475 | 86541.084 | 0 | 460588.204 | 0 | 71150.464 | 53112.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 1916910000000 | 1623805.764 | 21-AUG-15:15 | 448566.543 | 418415.216 | 100453.778 | 0 | 530642.295 | 0 | 72615.761 | 53112.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1730530000000 | 1555977.282 | 11-SEP-15:15 | 448566.543 | 418415.216 | 96321.99 | 0 | 468122.873 | 0 | 71438.49 | 53112.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1686670000000 | 1524717.728 | 06-OCT-15:30 | 448566.543 | 418415.216 | 85041.25 | 0 | 448905.126 | 0 | 70677.422 | 53112.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1572680000000 | 1437953.914 | 01-NOV-08:00 | 448566.543 | 473785.475 | 55029.383 | 0 | 340524.395 | 0 | 66935.947 | 53112.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1507200000000 | 1366516.316 | 15-DEC-08:00 | 448566.543 | 473785.475 | 51927.362 | 0 | 273696.255 | 0 | 65428.508 | 53112.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 19969100000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1420030000000 | 1366516.316 |  | 448566.543 | 418415.216 | 51927.362 | 0 | 273696.255 | 0 | 65428.508 | 53112.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1916910000000 | 1623805.764 |  | 448566.543 | 473785.475 | 100453.778 | 0 | 530642.295 | 0 | 72615.761 | 53112.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 474442.75 | 4653.35 | 0 | 479096.11
Cost per Total Building Area ($/m2) | 10.24 | 0.1 | 0 | 10.34
Cost per Net Conditioned Building Area ($/m2) | 10.24 | 0.1 | 0 | 10.34

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 22180.5 | 478.85 | 478.85
Net Site Energy | 22180.5 | 478.85 | 478.85
Total Source Energy | 3256.95 | 70.31 | 70.31
Net Source Energy | 3256.95 | 70.31 | 70.31
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2776.28 | 0 | 0 | 0 | 0
Cooling | 4288.24 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6687.85 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 954.01 | 0 | 0 | 0 | 0 | 0
Pumps | 1180.23 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 887.46 | 0 | 0 | 0 | 0 | 18283.91
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 206.27 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 19197.95 | 2982.55 | 0 | 0 | 0 | 19787.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.17 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 95.067
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.17 | 6.5404
Conditioned Total | 46320.38 |  | 126016.37 |  | 8024.24 | 4636.15 | 10.76 | 19.33 | 12.5776
Unconditioned Total | 42757.27 |  | 52129.67 |  | 3565.29 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 115.9 | 115.9 | 6.49 | 0.61 | 0.61 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 77.27 | 77.27 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 115.9 | 115.9 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 77.27 | 77.27 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 115.9 | 1159.04 | 6.49 | 0.61 | 0.61 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 77.27 | 772.69 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 115.9 | 1159.04 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 77.27 | 772.69 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 115.9 | 115.9 | 6.49 | 0.61 | 0.61 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 77.27 | 77.27 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 115.9 | 115.9 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 77.27 | 77.27 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 6.49 | 0.358 | 0.358
North Total or Average |  |  | 1390.85 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 3245.31 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4252386.81 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 4884192.42 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 4020438.44
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_5_COOLC | Coil:Cooling:Water | 133192.41 | - | - | - | -
VAV_1_COOLC | Coil:Cooling:Water | 310326.48 | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water | 3343216.79 | - | - | - | -
VAV_3_COOLC | Coil:Cooling:Water | 465651.12 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_5_HEATC | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_3_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_5_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 7.39 | 17089.71 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 17.4 | 39704.58 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 191.06 | 429548.79 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.61 | 1572.42 | 28.02 | 71715.54 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 27914.33 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 38967.24 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 56742.88 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 376438.2462 | 478.1985 | 1912.8704 | 0 | 0.0055 | 652436.6072 | 147878.95
February | 336622.1763 | 427.6056 | 1710.3546 | 0 | 0.0049 | 583363.0295 | 132235.9636
March | 385467.4357 | 500.0848 | 2104.6377 | 0 | 0.0059 | 717894.5026 | 152768.5973
April | 353737.6548 | 462.8519 | 1986.4586 | 0 | 0.0056 | 677601.167 | 140700.2184
May | 396663.6718 | 520.8208 | 2252.7499 | 0 | 0.0063 | 768443.736 | 158006.4181
June | 419504.1658 | 551.0806 | 2386.2508 | 0 | 0.0067 | 813983.8855 | 167139.4938
July | 422528.2519 | 555.0822 | 2403.8586 | 0 | 0.0068 | 819990.2805 | 168348.0914
August | 448989.0485 | 589.8315 | 2554.2228 | 0 | 0.0072 | 871281.5744 | 178889.2449
September | 383160.3847 | 503.3011 | 2179.0056 | 0 | 0.0061 | 743289.4547 | 152654.6351
October | 371775.2518 | 487.421 | 2101.3019 | 0 | 0.0059 | 716779.623 | 147999.4417
November | 353388.6288 | 460.5013 | 1957.9729 | 0 | 0.0055 | 667876.1373 | 140317.2659
December | 370639.4451 | 471.1889 | 1888.4 | 0 | 0.0054 | 644092.0386 | 145646.9473
Annual Sum or Average | 4618910 | 6007.9683 | 25438.0836 | 0 | 0.0718 | 8677030 | 1832590
Minimum of Months | 336622.1763 | 427.6056 | 1710.3546 | 0 | 0.0049 | 583363.0295 | 132235.9636
Maximum of Months | 448989.0485 | 589.8315 | 2554.2228 | 0 | 0.0072 | 871281.5744 | 178889.2449
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1443520000000 | 1345809.014 | 03-JAN-08:00 | 448566.543 | 473785.475 | 49618.145 | 0 | 256313.221 | 0 | 64757.374 | 52768.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1290690000000 | 1299646.064 | 21-FEB-08:45 | 448566.543 | 473785.475 | 49037.858 | 0 | 212365.815 | 0 | 63122.118 | 52768.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1588340000000 | 1344797.312 | 29-MAR-07:00 | 448566.543 | 473785.475 | 52081.713 | 0 | 253115.109 | 0 | 64480.217 | 52768.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1499190000000 | 1376428.595 | 24-APR-07:00 | 448566.543 | 473785.475 | 55376.562 | 0 | 280451.006 | 0 | 65480.754 | 52768.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1700180000000 | 1531110.5 | 30-MAY-07:00 | 448566.543 | 473785.475 | 77412.607 | 0 | 409088.176 | 0 | 69489.443 | 52768.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1800940000000 | 1520231.765 | 29-JUN-15:00 | 448566.543 | 418415.216 | 81369.354 | 0 | 449027.899 | 0 | 70084.499 | 52768.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1814230000000 | 1647361.695 | 18-JUL-12:00 | 448566.543 | 423230.021 | 91373.474 | 0 | 559196.689 | 0 | 72226.714 | 52768.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 1927710000000 | 1590882.071 | 31-AUG-15:00 | 448566.543 | 418415.216 | 99574.645 | 0 | 499584.297 | 0 | 71973.115 | 52768.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1644530000000 | 1541677.037 | 15-SEP-15:30 | 448566.543 | 418415.216 | 70354.111 | 0 | 481801.394 | 0 | 69771.519 | 52768.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1585880000000 | 1454769.443 | 30-OCT-08:00 | 448566.543 | 473785.475 | 54587.67 | 0 | 358219.548 | 0 | 66841.952 | 52768.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1477680000000 | 1375511.086 | 27-NOV-08:00 | 448566.543 | 473785.475 | 52248.375 | 0 | 282711.758 | 0 | 65430.68 | 52768.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1425050000000 | 1333774.663 | 20-DEC-08:00 | 448566.543 | 473785.475 | 50814.089 | 0 | 243588.668 | 0 | 64251.633 | 52768.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 19198000000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1290690000000 | 1299646.064 |  | 448566.543 | 418415.216 | 49037.858 | 0 | 212365.815 | 0 | 63122.118 | 52768.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1927710000000 | 1647361.695 |  | 448566.543 | 473785.475 | 99574.645 | 0 | 559196.689 | 0 | 72226.714 | 52768.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 582614.71 | 24019.57 | 0 | 606634.28
Cost per Total Building Area ($/m2) | 12.58 | 0.52 | 0 | 13.1
Cost per Net Conditioned Building Area ($/m2) | 12.58 | 0.52 | 0 | 13.1

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 21269.56 | 459.18 | 459.18
Net Site Energy | 21269.56 | 459.18 | 459.18
Total Source Energy | 62049.84 | 1339.58 | 1339.58
Net Source Energy | 62049.84 | 1339.58 | 1339.58
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2336.61 | 0 | 0 | 0 | 0
Cooling | 3717.23 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.8 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6687.85 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1182.44 | 0 | 0 | 0 | 0 | 0
Pumps | 1081.99 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 876.6 | 0 | 0 | 0 | 0 | 29705.1
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 186.7 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 18746.25 | 2523.31 | 0 | 0 | 0 | 31209.05
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.17 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 95.067
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.17 | 6.5404
Conditioned Total | 46320.38 |  | 126016.37 |  | 8024.24 | 4636.15 | 10.76 | 19.33 | 12.5776
Unconditioned Total | 42757.27 |  | 52129.67 |  | 3565.29 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 115.9 | 115.9 | 6.49 | 0.61 | 0.61 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 77.27 | 77.27 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 115.9 | 115.9 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 77.27 | 77.27 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 115.9 | 1159.04 | 6.49 | 0.61 | 0.61 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 77.27 | 772.69 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 115.9 | 1159.04 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 77.27 | 772.69 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 115.9 | 115.9 | 6.49 | 0.61 | 0.61 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 77.27 | 77.27 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 115.9 | 115.9 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 77.27 | 77.27 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 6.49 | 0.358 | 0.358
North Total or Average |  |  | 1390.85 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 3245.31 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4264541.07 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 5251661.57 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 4031929.74
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_5_COOLC | Coil:Cooling:Water | 91335.37 | - | - | - | -
VAV_1_COOLC | Coil:Cooling:Water | 299340.32 | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water | 3410149.52 | - | - | - | -
VAV_3_COOLC | Coil:Cooling:Water | 463715.86 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_5_HEATC | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_3_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1388.3 | 5.89 | 13828.03 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 19.62 | 44542.88 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 226.64 | 509545.72 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.61 | 1572.42 | 32.65 | 83590.17 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 30014.51 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 39078.62 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 56905.06 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 281742.0204 | 450.3327 | 1408.8201 | 0 | 0.0039 | 10405600 | 117188.9212
February | 256872.4458 | 413.9768 | 1309.0242 | 0 | 0.0036 | 9668720 | 107187.9078
March | 313151.0717 | 520.0243 | 1706.8533 | 0 | 0.0047 | 12608000 | 132223.9755
April | 296128.4093 | 497.9838 | 1659.1213 | 0 | 0.0045 | 12255700 | 125666.1325
May | 335565.3456 | 566.3507 | 1894.8892 | 0 | 0.0051 | 13997400 | 142608.8174
June | 366516.636 | 618.9657 | 2072.3936 | 0 | 0.0056 | 15308600 | 155800.6387
July | 371375.4299 | 627.2451 | 2100.4018 | 0 | 0.0057 | 15515500 | 157873.5188
August | 385269.739 | 650.6719 | 2178.6917 | 0 | 0.0059 | 16093900 | 163775.9668
September | 335004.8027 | 565.6909 | 1893.7947 | 0 | 0.0051 | 13989300 | 142399.5437
October | 314759.8916 | 529.6685 | 1766.0624 | 0 | 0.0048 | 13045700 | 133608.3622
November | 286570.2651 | 475.6324 | 1560.1544 | 0 | 0.0043 | 11524400 | 120975.1583
December | 285268.8998 | 450.935 | 1390.0319 | 0 | 0.0039 | 10266600 | 118146.7483
Annual Sum or Average | 3828220 | 6367.4779 | 20940.2389 | 0 | 0.057 | 154679000 | 1617460
Minimum of Months | 256872.4458 | 413.9768 | 1309.0242 | 0 | 0.0036 | 9668720 | 107187.9078
Maximum of Months | 385269.739 | 650.6719 | 2178.6917 | 0 | 0.0059 | 16093900 | 163775.9668
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1261100000000 | 1266453.751 | 27-JAN-13:00 | 448566.543 | 423230.021 | 59194.919 | 0 | 220893.742 | 0 | 61649.448 | 52919.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1171790000000 | 1285228.229 | 28-FEB-16:30 | 448566.543 | 418415.216 | 61766.771 | 0 | 241409.102 | 0 | 62151.519 | 52919.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1528010000000 | 1337762.975 | 17-MAR-15:00 | 448566.543 | 418415.216 | 71104.096 | 0 | 283453.176 | 0 | 63304.867 | 52919.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1485320000000 | 1358475.164 | 17-APR-15:30 | 448566.543 | 418415.216 | 75862.984 | 0 | 292198.446 | 0 | 70512.897 | 52919.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1696400000000 | 1435286.745 | 31-MAY-15:00 | 448566.543 | 418415.216 | 97610.128 | 0 | 343356.557 | 0 | 74419.224 | 52919.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1855320000000 | 1566205.709 | 28-JUN-15:00 | 448566.543 | 418415.216 | 137830.273 | 0 | 433157.043 | 0 | 75317.556 | 52919.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1880390000000 | 1601806.744 | 11-JUL-15:00 | 448566.543 | 418415.216 | 132109.802 | 0 | 476528.792 | 0 | 73267.314 | 52919.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 1950480000000 | 1559785.231 | 02-AUG-15:15 | 448566.543 | 418415.216 | 120298.873 | 0 | 447406.57 | 0 | 72178.951 | 52919.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1695430000000 | 1529725.72 | 05-SEP-07:15 | 448566.543 | 473785.475 | 77761.255 | 0 | 405874.032 | 0 | 70819.338 | 52919.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1581060000000 | 1442467.409 | 03-OCT-07:00 | 448566.543 | 473785.475 | 61513.735 | 0 | 337601.33 | 0 | 68081.247 | 52919.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1396680000000 | 1321828.696 | 13-NOV-13:00 | 448566.543 | 423230.021 | 66455.756 | 0 | 267811.788 | 0 | 62845.51 | 52919.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1244250000000 | 1262476.26 | 11-DEC-13:00 | 448566.543 | 423230.021 | 58402.009 | 0 | 217791.636 | 0 | 61566.973 | 52919.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 18746300000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1171790000000 | 1262476.26 |  | 448566.543 | 418415.216 | 58402.009 | 0 | 217791.636 | 0 | 61566.973 | 52919.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1950480000000 | 1601806.744 |  | 448566.543 | 473785.475 | 137830.273 | 0 | 476528.792 | 0 | 75317.556 | 52919.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 415176.24 | 20639.03 | 0 | 435815.27
Cost per Total Building Area ($/m2) | 8.96 | 0.45 | 0 | 9.41
Cost per Net Conditioned Building Area ($/m2) | 8.96 | 0.45 | 0 | 9.41

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 20527.38 | 443.16 | 443.16
Net Site Energy | 20527.38 | 443.16 | 443.16
Total Source Energy | 62652.39 | 1352.59 | 1352.59
Net Source Energy | 62652.39 | 1352.59 | 1352.59
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2578.66 | 0 | 0 | 0 | 0
Cooling | 3100.67 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.9 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6687.85 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 891.48 | 0 | 0 | 0 | 0 | 0
Pumps | 1068.35 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 761.13 | 0 | 0 | 0 | 0 | 14437.85
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 239 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17709.72 | 2817.66 | 0 | 0 | 0 | 15941.79
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.17 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 95.067
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.17 | 6.5404
Conditioned Total | 46320.38 |  | 126016.37 |  | 8024.24 | 4636.15 | 10.76 | 19.33 | 12.5776
Unconditioned Total | 42757.27 |  | 52129.67 |  | 3565.29 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.402 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 77.27 | 77.27 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 115.9 | 115.9 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 77.27 | 77.27 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 115.9 | 1159.04 | 3.18 | 0.402 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 77.27 | 772.69 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 115.9 | 1159.04 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 77.27 | 772.69 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.402 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 77.27 | 77.27 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 115.9 | 115.9 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 77.27 | 77.27 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.18 | 0.304 | 0.409
North Total or Average |  |  | 1390.85 | 3.18 | 0.402 | 0.622
Non-North Total or Average |  |  | 3245.31 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3978847.19 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 4755720.4 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3761819.16
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_5_COOLC | Coil:Cooling:Water | 124575.9 | - | - | - | -
VAV_1_COOLC | Coil:Cooling:Water | 294596.05 | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water | 3117515.18 | - | - | - | -
VAV_3_COOLC | Coil:Cooling:Water | 442160.05 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_5_HEATC | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_3_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_5_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 7.24 | 16726.59 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 17.3 | 39472.71 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 185.24 | 416466.9 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.61 | 1572.42 | 27.85 | 71299.35 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 27180.08 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 36460.63 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 53092.83 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 300374.2968 | 535.3262 | 1288.9543 | 0 | 0.0048 | 2292400 | 128218.9772
February | 258449.9732 | 471.5354 | 1162.6131 | 0 | 0.0043 | 2067810 | 111332.0914
March | 304728.3901 | 574.3179 | 1460.7392 | 0 | 0.0054 | 2598240 | 132961.9334
April | 282685.6776 | 539.7435 | 1389.2395 | 0 | 0.0051 | 2471130 | 123987.6807
May | 307824.1357 | 592.6151 | 1536.6716 | 0 | 0.0056 | 2733420 | 135463.6567
June | 319159.238 | 615.3111 | 1597.5414 | 0 | 0.0058 | 2841700 | 140532.5947
July | 318544.8838 | 614.185 | 1594.7517 | 0 | 0.0058 | 2836740 | 140267.4591
August | 339627.3188 | 654.87 | 1700.4748 | 0 | 0.0062 | 3024800 | 149554.1892
September | 301257.1755 | 580.5955 | 1506.9429 | 0 | 0.0055 | 2680540 | 132631.2798
October | 290842.5949 | 557.025 | 1437.6943 | 0 | 0.0053 | 2557330 | 127723.0091
November | 277547.2934 | 521.2074 | 1321.2157 | 0 | 0.0048 | 2350050 | 120928.157
December | 284987.3382 | 517.6893 | 1270.8963 | 0 | 0.0047 | 2260380 | 122554.5712
Annual Sum or Average | 3586030 | 6774.4214 | 17267.7348 | 0 | 0.0633 | 30714600 | 1566160
Minimum of Months | 258449.9732 | 471.5354 | 1162.6131 | 0 | 0.0043 | 2067810 | 111332.0914
Maximum of Months | 339627.3188 | 654.87 | 1700.4748 | 0 | 0.0062 | 3024800 | 149554.1892
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1321770000000 | 1214590.07 | 24-JAN-16:00 | 448566.543 | 418415.216 | 47245.088 | 0 | 192108.892 | 0 | 58880.455 | 49373.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1192280000000 | 1243286.966 | 21-FEB-08:00 | 448566.543 | 473785.475 | 46830.544 | 0 | 166935.876 | 0 | 57794.65 | 49373.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1498120000000 | 1255295.397 | 30-MAR-07:00 | 448566.543 | 473785.475 | 48782.833 | 0 | 176555.858 | 0 | 58230.811 | 49373.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1424830000000 | 1307802.651 | 20-APR-15:00 | 448566.543 | 418415.216 | 63640.715 | 0 | 266002.31 | 0 | 61803.99 | 49373.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1576060000000 | 1390431.126 | 31-MAY-15:00 | 448566.543 | 418415.216 | 74730.72 | 0 | 334925.029 | 0 | 64419.742 | 49373.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1638500000000 | 1427936.843 | 08-JUN-15:30 | 448566.543 | 418415.216 | 69247.511 | 0 | 377538.155 | 0 | 64795.542 | 49373.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1635640000000 | 1514180.411 | 03-JUL-12:15 | 448566.543 | 423230.021 | 84127.437 | 0 | 442175.678 | 0 | 66706.856 | 49373.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 1744070000000 | 1475882.808 | 14-AUG-15:30 | 448566.543 | 418415.216 | 88558.952 | 0 | 404607.792 | 0 | 66360.428 | 49373.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1545580000000 | 1428249.029 | 05-SEP-15:00 | 448566.543 | 418415.216 | 84916.831 | 0 | 361423.055 | 0 | 65553.508 | 49373.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1474530000000 | 1314426.793 | 02-OCT-12:00 | 448566.543 | 423230.021 | 62953.297 | 0 | 268354.542 | 0 | 61948.514 | 49373.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1355020000000 | 1254625.578 | 22-NOV-08:00 | 448566.543 | 473785.475 | 47864.841 | 0 | 176795.501 | 0 | 58239.342 | 49373.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1303320000000 | 1263709.065 | 26-DEC-08:00 | 448566.543 | 473785.475 | 46830.544 | 0 | 186250.677 | 0 | 58901.949 | 49373.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 17709700000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1192280000000 | 1214590.07 |  | 448566.543 | 418415.216 | 46830.544 | 0 | 166935.876 | 0 | 57794.65 | 49373.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1744070000000 | 1514180.411 |  | 448566.543 | 473785.475 | 88558.952 | 0 | 442175.678 | 0 | 66706.856 | 49373.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 480907.26 | 26957.85 | 0 | 507865.11
Cost per Total Building Area ($/m2) | 10.38 | 0.58 | 0 | 10.96
Cost per Net Conditioned Building Area ($/m2) | 10.38 | 0.58 | 0 | 10.96

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17081.74 | 368.77 | 368.77
Net Site Energy | 17081.74 | 368.77 | 368.77
Total Source Energy | 51070.5 | 1102.55 | 1102.55
Net Source Energy | 51070.5 | 1102.55 | 1102.55
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 664.64 | 0 | 0 | 0 | 0
Cooling | 2102.07 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.89 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6687.85 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 788.17 | 0 | 0 | 0 | 0 | 0
Pumps | 770.61 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 635.42 | 0 | 0 | 0 | 0 | 9912.9
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 232.76 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 16184.34 | 897.39 | 0 | 0 | 0 | 11416.85
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.17 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 95.067
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.17 | 6.5404
Conditioned Total | 46320.38 |  | 126016.37 |  | 8024.24 | 4636.15 | 10.76 | 19.33 | 12.5776
Unconditioned Total | 42757.27 |  | 52129.67 |  | 3565.29 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.402 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 77.27 | 77.27 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 115.9 | 115.9 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 77.27 | 77.27 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 115.9 | 1159.04 | 3.18 | 0.402 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 77.27 | 772.69 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 115.9 | 1159.04 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 77.27 | 772.69 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.402 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 77.27 | 77.27 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 115.9 | 115.9 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 77.27 | 77.27 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.18 | 0.304 | 0.409
North Total or Average |  |  | 1390.85 | 3.18 | 0.402 | 0.622
Non-North Total or Average |  |  | 3245.31 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3296747.3 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 4264255.93 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3116924.72
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_5_COOLC | Coil:Cooling:Water | 102953 | - | - | - | -
VAV_1_COOLC | Coil:Cooling:Water | 243360.21 | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water | 2586648.36 | - | - | - | -
VAV_3_COOLC | Coil:Cooling:Water | 363785.74 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_5_HEATC | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_3_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_5_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 6.96 | 16078.07 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 16.27 | 37116.13 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 174.27 | 391804.18 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.61 | 1572.42 | 25.15 | 64388.21 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 24371.25 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 30210.13 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 43991.04 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 115401.3181 | 99.2459 | 988.8676 | 0 | 0.0005 | 5966380 | 42957.586
February | 102249.5782 | 87.8503 | 891.3958 | 0 | 0.0004 | 5378340 | 38108.3643
March | 121549.7497 | 104.3246 | 1078.9491 | 0 | 0.0005 | 6510030 | 45360.4037
April | 112350.4833 | 96.3233 | 1016.2038 | 0 | 0.0005 | 6131510 | 41985.0888
May | 124114.4533 | 106.3439 | 1134.275 | 0 | 0.0005 | 6843960 | 46416.8492
June | 125989.1782 | 107.9064 | 1159.2461 | 0 | 0.0005 | 6994660 | 47141.8805
July | 126861.8665 | 108.6228 | 1172.8278 | 0 | 0.0005 | 7076620 | 47485.3565
August | 141022.0453 | 120.7473 | 1303.7089 | 0 | 0.0006 | 7866340 | 52785.5311
September | 125130.8988 | 107.1525 | 1154.7045 | 0 | 0.0005 | 6967260 | 46830.9723
October | 124343.2264 | 106.5197 | 1139.9918 | 0 | 0.0005 | 6878470 | 46513.4694
November | 116133.7519 | 99.5793 | 1048.2076 | 0 | 0.0005 | 6324600 | 43392.1266
December | 114304.8131 | 98.2236 | 993.6684 | 0 | 0.0005 | 5995400 | 42592.731
Annual Sum or Average | 1449450 | 1242.8396 | 13082.0465 | 0 | 0.0059 | 78933600 | 541570.3592
Minimum of Months | 102249.5782 | 87.8503 | 891.3958 | 0 | 0.0004 | 5378340 | 38108.3643
Maximum of Months | 141022.0453 | 120.7473 | 1303.7089 | 0 | 0.0006 | 7866340 | 52785.5311
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1223330000000 | 1215472.658 | 26-JAN-13:15 | 448566.543 | 423230.021 | 51227.301 | 0 | 203057.808 | 0 | 48481.348 | 40909.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1102760000000 | 1203553.336 | 13-FEB-12:30 | 448566.543 | 413117.969 | 52390.075 | 0 | 195819.795 | 0 | 52749.316 | 40909.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1334800000000 | 1213610.799 | 31-MAR-15:15 | 448566.543 | 418415.216 | 56787.442 | 0 | 200302.324 | 0 | 48629.638 | 40909.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1257190000000 | 1241509.136 | 11-APR-15:00 | 448566.543 | 418415.216 | 56366.9 | 0 | 224122.653 | 0 | 53128.187 | 40909.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1403270000000 | 1343081.052 | 30-MAY-12:00 | 448566.543 | 423230.021 | 59764.147 | 0 | 315987.975 | 0 | 54622.729 | 40909.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1434170000000 | 1294773.044 | 29-JUN-07:00 | 448566.543 | 473785.475 | 50554.033 | 0 | 229488.664 | 0 | 51468.691 | 40909.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1450970000000 | 1339837.835 | 24-JUL-15:15 | 448566.543 | 418415.216 | 64122.985 | 0 | 313170.206 | 0 | 54653.248 | 40909.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 1612890000000 | 1444036.22 | 16-AUG-15:00 | 448566.543 | 418415.216 | 64454.883 | 0 | 414221.474 | 0 | 57468.467 | 40909.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1428550000000 | 1335036.171 | 08-SEP-07:00 | 448566.543 | 473785.475 | 51393.203 | 0 | 267577.877 | 0 | 52803.435 | 40909.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1410340000000 | 1268549.465 | 05-OCT-15:00 | 448566.543 | 418415.216 | 58168.728 | 0 | 250023.52 | 0 | 52465.821 | 40909.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1296780000000 | 1224304.411 | 08-NOV-08:00 | 448566.543 | 473785.475 | 45800.667 | 0 | 167626.547 | 0 | 47615.541 | 40909.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1229280000000 | 1223401.124 | 19-DEC-13:15 | 448566.543 | 423230.021 | 53715.602 | 0 | 208295.196 | 0 | 48684.125 | 40909.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 16184300000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1102760000000 | 1203553.336 |  | 448566.543 | 413117.969 | 45800.667 | 0 | 167626.547 | 0 | 47615.541 | 40909.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1612890000000 | 1444036.22 |  | 448566.543 | 473785.475 | 64454.883 | 0 | 414221.474 | 0 | 57468.467 | 40909.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 265675.64 | 7742.52 | 0 | 273418.16
Cost per Total Building Area ($/m2) | 5.74 | 0.17 | 0 | 5.9
Cost per Net Conditioned Building Area ($/m2) | 5.74 | 0.17 | 0 | 5.9

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 20823.72 | 449.56 | 449.56
Net Site Energy | 20823.72 | 449.56 | 449.56
Total Source Energy | 69779.12 | 1506.45 | 1506.45
Net Source Energy | 69779.12 | 1506.45 | 1506.45
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1684.08 | 0 | 0 | 0 | 0
Cooling | 3287.43 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.83 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6687.85 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1088.24 | 0 | 0 | 0 | 0 | 0
Pumps | 1508.36 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1157.36 | 0 | 0 | 0 | 0 | 37009.02
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 210.22 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 18929.42 | 1894.3 | 0 | 0 | 0 | 38512.97
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.17 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 95.067
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.17 | 6.5404
Conditioned Total | 46320.38 |  | 126016.37 |  | 8024.24 | 4636.15 | 10.76 | 19.33 | 12.5776
Unconditioned Total | 42757.27 |  | 52129.67 |  | 3565.29 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.402 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 77.27 | 77.27 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 115.9 | 115.9 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 77.27 | 77.27 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 115.9 | 1159.04 | 3.18 | 0.402 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 77.27 | 772.69 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 115.9 | 1159.04 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 77.27 | 772.69 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.402 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 77.27 | 77.27 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 115.9 | 115.9 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 77.27 | 77.27 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.18 | 0.304 | 0.409
North Total or Average |  |  | 1390.85 | 3.18 | 0.402 | 0.622
Non-North Total or Average |  |  | 3245.31 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 6975159.01 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 4908873.71 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 6594695.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_5_COOLC | Coil:Cooling:Water | 138517.35 | - | - | - | -
VAV_1_COOLC | Coil:Cooling:Water | 472929.34 | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water | 5331833.34 | - | - | - | -
VAV_3_COOLC | Coil:Cooling:Water | 765887.4 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_5_HEATC | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_3_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1388.3 | 5.56 | 13038.97 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 18.86 | 43028.08 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 212.89 | 478628.11 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.61 | 1572.42 | 31.45 | 80507.69 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28055.39 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 63917.68 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 93074.93 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 289056.9671 | 453.849 | 1800.73 | 0 | 0.0034 | 8980030 | 119943.7376
February | 273238.6864 | 438.1558 | 1788.1268 | 0 | 0.0034 | 8917530 | 114330.2884
March | 324878.0645 | 523.2503 | 2147.5644 | 0 | 0.004 | 10710200 | 136175.3121
April | 346698.3418 | 566.614 | 2369.0659 | 0 | 0.0044 | 11815100 | 146175.8193
May | 393421.7773 | 644.1878 | 2699.7389 | 0 | 0.0051 | 13464300 | 166001.5488
June | 431209.8004 | 706.5979 | 2964.0865 | 0 | 0.0056 | 14782700 | 182001.6572
July | 434425.7128 | 711.9549 | 2987.0132 | 0 | 0.0056 | 14897000 | 183368.0814
August | 455630.1304 | 746.6796 | 3132.5654 | 0 | 0.0059 | 15622900 | 192315.6141
September | 398854.6076 | 653.5528 | 2741.4307 | 0 | 0.0051 | 13672200 | 168342.667
October | 363684.1472 | 594.4538 | 2485.8821 | 0 | 0.0047 | 12397700 | 153345.6937
November | 302020.2718 | 487.3495 | 2005.058 | 0 | 0.0038 | 9999500 | 126689.2918
December | 286013.0505 | 451.3712 | 1803.3995 | 0 | 0.0034 | 8993430 | 118919.8778
Annual Sum or Average | 4299130 | 6978.0166 | 28924.6616 | 0 | 0.0544 | 144253000 | 1807610
Minimum of Months | 273238.6864 | 438.1558 | 1788.1268 | 0 | 0.0034 | 8917530 | 114330.2884
Maximum of Months | 455630.1304 | 746.6796 | 3132.5654 | 0 | 0.0059 | 15622900 | 192315.6141
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1178400000000 | 1306513.766 | 18-JAN-13:00 | 448566.543 | 423230.021 | 55695.017 | 0 | 195040.289 | 0 | 97426.515 | 86555.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1170190000000 | 1355621.251 | 08-FEB-13:00 | 448566.543 | 423230.021 | 58535.673 | 0 | 240418.817 | 0 | 98314.815 | 86555.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1405430000000 | 1407761.49 | 31-MAR-15:15 | 448566.543 | 418415.216 | 60772.014 | 0 | 293928.989 | 0 | 99523.346 | 86555.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1550430000000 | 1464378.745 | 21-APR-15:15 | 448566.543 | 418415.216 | 72068.21 | 0 | 336208.516 | 0 | 102564.877 | 86555.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1766840000000 | 1512388.16 | 31-MAY-15:00 | 448566.543 | 418415.216 | 85269.997 | 0 | 367291.718 | 0 | 106289.304 | 86555.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1939840000000 | 1665633.695 | 28-JUN-12:00 | 448566.543 | 423230.021 | 168701.427 | 0 | 421982.73 | 0 | 116597.591 | 86555.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1954850000000 | 1670214.961 | 26-JUL-12:00 | 448566.543 | 423230.021 | 165018.376 | 0 | 427063.48 | 0 | 119781.158 | 86555.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 2050110000000 | 1662039.249 | 02-AUG-15:30 | 448566.543 | 418415.216 | 159777.807 | 0 | 430091.814 | 0 | 118632.487 | 86555.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1794130000000 | 1649828.629 | 01-SEP-12:00 | 448566.543 | 423230.021 | 160762.591 | 0 | 399679.657 | 0 | 131034.434 | 86555.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1626880000000 | 1481028.022 | 06-OCT-12:00 | 448566.543 | 423230.021 | 73879.552 | 0 | 341316.733 | 0 | 107479.79 | 86555.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1312170000000 | 1382913.149 | 10-NOV-13:45 | 448566.543 | 423230.021 | 60678.674 | 0 | 264997.507 | 0 | 98885.022 | 86555.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1180150000000 | 1359406.031 | 05-DEC-13:00 | 448566.543 | 423230.021 | 56940.414 | 0 | 245780.562 | 0 | 98333.108 | 86555.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 18929400000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1170190000000 | 1306513.766 |  | 448566.543 | 418415.216 | 55695.017 | 0 | 195040.289 | 0 | 97426.515 | 86555.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2050110000000 | 1670214.961 |  | 448566.543 | 423230.021 | 168701.427 | 0 | 430091.814 | 0 | 131034.434 | 86555.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 521221.46 | 14529.17 | 0 | 535750.63
Cost per Total Building Area ($/m2) | 11.25 | 0.31 | 0 | 11.57
Cost per Net Conditioned Building Area ($/m2) | 11.25 | 0.31 | 0 | 11.57

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17960.78 | 387.75 | 387.75
Net Site Energy | 17960.78 | 387.75 | 387.75
Total Source Energy | 48775.57 | 1053 | 1053
Net Source Energy | 48775.57 | 1053 | 1053
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3140.69 | 0 | 0 | 0 | 0
Cooling | 901.62 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.76 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6687.85 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 775.12 | 0 | 0 | 0 | 0 | 0
Pumps | 562.37 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 432.29 | 0 | 0 | 0 | 0 | 5186.06
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 260.73 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 14559.36 | 3401.42 | 0 | 0 | 0 | 6690
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.17 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 95.067
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.17 | 6.5404
Conditioned Total | 46320.38 |  | 126016.37 |  | 8024.24 | 4636.15 | 10.76 | 19.33 | 12.5776
Unconditioned Total | 42757.27 |  | 52129.67 |  | 3565.29 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 115.9 | 115.9 | 6.49 | 0.61 | 0.61 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 77.27 | 77.27 | 6.49 | 0.34 | 0.34 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 115.9 | 115.9 | 6.49 | 0.34 | 0.34 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 77.27 | 77.27 | 6.49 | 0.34 | 0.34 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 115.9 | 1159.04 | 6.49 | 0.61 | 0.61 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 77.27 | 772.69 | 6.49 | 0.34 | 0.34 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 115.9 | 1159.04 | 6.49 | 0.34 | 0.34 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 77.27 | 772.69 | 6.49 | 0.34 | 0.34 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 115.9 | 115.9 | 6.49 | 0.61 | 0.61 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 77.27 | 77.27 | 6.49 | 0.34 | 0.34 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 115.9 | 115.9 | 6.49 | 0.34 | 0.34 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 77.27 | 77.27 | 6.49 | 0.34 | 0.34 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 6.49 | 0.421 | 0.421
North Total or Average |  |  | 1390.85 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 3245.31 | 6.49 | 0.34 | 0.34
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3159919.52 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 4322053.24 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2987560.27
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_5_COOLC | Coil:Cooling:Water | 60043.43 | - | - | - | -
VAV_1_COOLC | Coil:Cooling:Water | 232029.28 | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water | 2519274.06 | - | - | - | -
VAV_3_COOLC | Coil:Cooling:Water | 348572.75 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_5_HEATC | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_3_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1388.3 | 4.41 | 10345.38 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 15.99 | 36479.97 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 174.98 | 393410.02 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.61 | 1572.42 | 24.46 | 62610.11 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 24701.57 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28956.29 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 42165.25 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 128076.7041 | 111.357 | 880.9626 | 0 | 0.0005 | 5314550 | 47015.3448
February | 108550.0028 | 93.8195 | 846.8304 | 0 | 0.0004 | 5109090 | 40152.9847
March | 125661.2411 | 108.6655 | 970.144 | 0 | 0.0005 | 5853020 | 46451.438
April | 113940.336 | 98.2642 | 927.2006 | 0 | 0.0004 | 5594130 | 42263.7941
May | 121477.639 | 104.4734 | 1040.6237 | 0 | 0.0005 | 6278650 | 45218.5168
June | 120114.8328 | 103.1924 | 1048.4332 | 0 | 0.0005 | 6325840 | 44770.6737
July | 116352.425 | 99.8386 | 1037.3203 | 0 | 0.0005 | 6258870 | 43434.593
August | 127170.4432 | 109.1471 | 1129.1382 | 0 | 0.0005 | 6812850 | 47458.8602
September | 117431.8978 | 100.761 | 1047.6398 | 0 | 0.0005 | 6321140 | 43839.685
October | 119265.9949 | 102.4928 | 1035.7251 | 0 | 0.0005 | 6249150 | 44438.1175
November | 117598.1655 | 101.4704 | 947.7254 | 0 | 0.0005 | 5717930 | 43592.3957
December | 123433.8641 | 107.2729 | 857.4985 | 0 | 0.0005 | 5173030 | 45336.8621
Annual Sum or Average | 1439070 | 1240.7547 | 11769.2418 | 0 | 0.0056 | 71008300 | 533973.2655
Minimum of Months | 108550.0028 | 93.8195 | 846.8304 | 0 | 0.0004 | 5109090 | 40152.9847
Maximum of Months | 128076.7041 | 111.357 | 1129.1382 | 0 | 0.0005 | 6812850 | 47458.8602
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1089680000000 | 1055374.639 | 17-JAN-13:00 | 448566.543 | 423230.021 | 46187.133 | 0 | 54320.047 | 0 | 43859.166 | 39211.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1047560000000 | 1171809.026 | 14-FEB-13:15 | 448566.543 | 423230.021 | 48201.958 | 0 | 166670.629 | 0 | 45928.147 | 39211.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1200090000000 | 1126582.942 | 01-MAR-13:30 | 448566.543 | 423230.021 | 47005.073 | 0 | 122242.728 | 0 | 46326.848 | 39211.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1147010000000 | 1184103.05 | 13-APR-15:15 | 448566.543 | 418415.216 | 53485.789 | 0 | 178121.254 | 0 | 46302.52 | 39211.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1287360000000 | 1196298.334 | 26-MAY-12:00 | 448566.543 | 423230.021 | 47366.298 | 0 | 189650.587 | 0 | 48273.157 | 39211.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1297040000000 | 1216006.313 | 16-JUN-15:00 | 448566.543 | 418415.216 | 56758.56 | 0 | 203725.276 | 0 | 49328.989 | 39211.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1283300000000 | 1264459.202 | 03-JUL-12:00 | 448566.543 | 423230.021 | 62505.986 | 0 | 240738.795 | 0 | 50206.129 | 39211.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 1396890000000 | 1234094.751 | 15-AUG-12:30 | 448566.543 | 423230.021 | 54363.506 | 0 | 219391.535 | 0 | 49331.417 | 39211.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1296070000000 | 1296340.258 | 28-SEP-15:15 | 448566.543 | 418415.216 | 73732.165 | 0 | 263642.133 | 0 | 52772.472 | 39211.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1281310000000 | 1206360.003 | 31-OCT-13:15 | 448566.543 | 423230.021 | 51885.841 | 0 | 194958.457 | 0 | 48507.413 | 39211.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1172390000000 | 1144976.806 | 16-NOV-16:15 | 448566.543 | 418415.216 | 44828.753 | 0 | 147018.2 | 0 | 46936.365 | 39211.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1060670000000 | 1062690.991 | 01-DEC-13:00 | 448566.543 | 423230.021 | 43672.569 | 0 | 63951.352 | 0 | 44058.778 | 39211.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 14559400000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1047560000000 | 1055374.639 |  | 448566.543 | 418415.216 | 43672.569 | 0 | 54320.047 | 0 | 43859.166 | 39211.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1396890000000 | 1296340.258 |  | 448566.543 | 423230.021 | 73732.165 | 0 | 263642.133 | 0 | 52772.472 | 39211.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 627978.37 | 29159.73 | 0 | 657138.1
Cost per Total Building Area ($/m2) | 13.56 | 0.63 | 0 | 14.19
Cost per Net Conditioned Building Area ($/m2) | 13.56 | 0.63 | 0 | 14.19

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 22834.46 | 492.97 | 492.97
Net Site Energy | 22834.46 | 492.97 | 492.97
Total Source Energy | 69788.5 | 1506.65 | 1506.65
Net Source Energy | 69788.5 | 1506.65 | 1506.65
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4512.87 | 0 | 0 | 0 | 0
Cooling | 3153.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.82 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6687.85 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 968.31 | 0 | 0 | 0 | 0 | 0
Pumps | 1294.73 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 752.69 | 0 | 0 | 0 | 0 | 14321.5
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 264.72 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 18056.87 | 4777.58 | 0 | 0 | 0 | 15825.45
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.17 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 95.067
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.17 | 6.5404
Conditioned Total | 46320.38 |  | 126016.37 |  | 8024.24 | 4636.15 | 10.76 | 19.33 | 12.5776
Unconditioned Total | 42757.27 |  | 52129.67 |  | 3565.29 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.501 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 115.9 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 1159.04 | 3.18 | 0.501 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 772.69 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 1159.04 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 772.69 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.501 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 115.9 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 1390.85 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 3245.31 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4305941.61 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 5306881.64 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 4071072.07
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_5_COOLC | Coil:Cooling:Water | 123259.68 | - | - | - | -
VAV_1_COOLC | Coil:Cooling:Water | 316629.21 | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water | 3405376.14 | - | - | - | -
VAV_3_COOLC | Coil:Cooling:Water | 460676.58 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_5_HEATC | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_3_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_5_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 6.99 | 16166.13 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 18.36 | 41900.52 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 200.67 | 451170.65 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.61 | 1572.42 | 28.44 | 72812.6 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 30330.1 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 39458 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 57457.5 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 294424.1854 | 518.6458 | 1389.3425 | 0 | 0.0057 | 86390.0023 | 124887.7511
February | 254016.3222 | 459.5606 | 1265.4511 | 0 | 0.0052 | 78690.9055 | 108853.6885
March | 276930.6741 | 524.4876 | 1509.2007 | 0 | 0.0061 | 93856.5754 | 120819.2831
April | 253257.0593 | 489.7793 | 1436.1077 | 0 | 0.0058 | 89314.2376 | 111417.0306
May | 270110.3373 | 534.2155 | 1597.0684 | 0 | 0.0064 | 99328.3832 | 119914.3167
June | 282823.7995 | 563.814 | 1696.8327 | 0 | 0.0068 | 105534.4731 | 125965.6796
July | 283210.2038 | 565.1014 | 1702.0065 | 0 | 0.0069 | 105856.4129 | 126185.0668
August | 305877.1655 | 610.1172 | 1837.0542 | 0 | 0.0074 | 114255.6487 | 136264.9537
September | 260463.7272 | 516.944 | 1550.0103 | 0 | 0.0062 | 96402.1828 | 115796.9971
October | 263477.7766 | 515.6385 | 1527.7081 | 0 | 0.0062 | 95012.9391 | 116470.6301
November | 260238.9917 | 494.9742 | 1429.828 | 0 | 0.0058 | 88921.1024 | 113729.0126
December | 279442.2714 | 501.6166 | 1370.3398 | 0 | 0.0056 | 85211.9135 | 119388.8421
Annual Sum or Average | 3284270 | 6294.8948 | 18310.95 | 0 | 0.0743 | 1138770 | 1439690
Minimum of Months | 253257.0593 | 459.5606 | 1265.4511 | 0 | 0.0052 | 78690.9055 | 108853.6885
Maximum of Months | 305877.1655 | 610.1172 | 1837.0542 | 0 | 0.0074 | 114255.6487 | 136264.9537
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1369830000000 | 1242152.213 | 09-JAN-08:00 | 448566.543 | 473785.475 | 50109.264 | 0 | 152779.156 | 0 | 63478.954 | 53432.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1247750000000 | 1208250.713 | 15-FEB-13:00 | 448566.543 | 423230.021 | 50109.264 | 0 | 171918.812 | 0 | 60993.252 | 53432.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1488230000000 | 1284664.967 | 10-MAR-08:00 | 448566.543 | 473785.475 | 51843.668 | 0 | 193968.646 | 0 | 63067.814 | 53432.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1416200000000 | 1296559.091 | 04-APR-07:45 | 448566.543 | 473785.475 | 51369.674 | 0 | 205738.402 | 0 | 63666.175 | 53432.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1574990000000 | 1385458.02 | 31-MAY-15:00 | 448566.543 | 418415.216 | 57492.683 | 0 | 339947.67 | 0 | 67603.087 | 53432.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1673400000000 | 1519818.221 | 30-JUN-15:00 | 448566.543 | 418415.216 | 78530.835 | 0 | 450541.601 | 0 | 70331.206 | 53432.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1678500000000 | 1571583.989 | 25-JUL-12:00 | 448566.543 | 423230.021 | 80827.253 | 0 | 494344.694 | 0 | 71182.657 | 53432.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 1811680000000 | 1607258.451 | 09-AUG-15:15 | 448566.543 | 418415.216 | 80938.886 | 0 | 534097.289 | 0 | 71807.696 | 53432.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1528590000000 | 1382833.463 | 13-SEP-15:30 | 448566.543 | 418415.216 | 77892.899 | 0 | 316751.869 | 0 | 67774.116 | 53432.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1506560000000 | 1354456.528 | 03-OCT-07:00 | 448566.543 | 473785.475 | 52990.015 | 0 | 260204.777 | 0 | 65476.896 | 53432.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1409970000000 | 1311504 | 03-NOV-13:00 | 448566.543 | 423230.021 | 58278.779 | 0 | 262405.837 | 0 | 65589.998 | 53432.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1351150000000 | 1186633.906 | 08-DEC-08:00 | 448566.543 | 473785.475 | 50109.264 | 0 | 100442.426 | 0 | 60297.377 | 53432.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 18056900000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1247750000000 | 1186633.906 |  | 448566.543 | 418415.216 | 50109.264 | 0 | 100442.426 | 0 | 60297.377 | 53432.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1811680000000 | 1607258.451 |  | 448566.543 | 473785.475 | 80938.886 | 0 | 534097.289 | 0 | 71807.696 | 53432.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 356013.06 | 46293.38 | 0 | 402306.44
Cost per Total Building Area ($/m2) | 7.69 | 1 | 0 | 8.69
Cost per Net Conditioned Building Area ($/m2) | 7.69 | 1 | 0 | 8.69

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 20639.73 | 445.59 | 445.59
Net Site Energy | 20639.73 | 445.59 | 445.59
Total Source Energy | 62010.74 | 1338.74 | 1338.74
Net Source Energy | 62010.74 | 1338.74 | 1338.74
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2647.54 | 0 | 0 | 0 | 0
Cooling | 2400.35 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6687.85 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1171.09 | 0 | 0 | 0 | 0 | 0
Pumps | 1403.98 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 868.9 | 0 | 0 | 0 | 0 | 23064.77
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 259.86 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17732.33 | 2907.4 | 0 | 0 | 0 | 24568.72
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.17 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 95.067
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.17 | 6.5404
Conditioned Total | 46320.38 |  | 126016.37 |  | 8024.24 | 4636.15 | 10.76 | 19.33 | 12.5776
Unconditioned Total | 42757.27 |  | 52129.67 |  | 3565.29 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.501 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 115.9 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 1159.04 | 3.18 | 0.501 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 772.69 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 1159.04 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 772.69 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.501 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 115.9 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 1390.85 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 3245.31 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 6531002.77 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 4860521.36 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 6174766.25
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_5_COOLC | Coil:Cooling:Water | 129039.63 | - | - | - | -
VAV_1_COOLC | Coil:Cooling:Water | 412926.32 | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water | 4456896.2 | - | - | - | -
VAV_3_COOLC | Coil:Cooling:Water | 653034.87 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_5_HEATC | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_3_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_5_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 6.82 | 15772.45 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 21.22 | 48164.92 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 229.06 | 514998.5 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.61 | 1572.42 | 33.83 | 86601.53 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 27779.05 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 59847.6 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 87148.21 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 369219.1818 | 617.1485 | 1527.9319 | 0 | 0.006 | 1588620 | 155449.0619
February | 318416.1244 | 539.8383 | 1358.8671 | 0 | 0.0053 | 1412890 | 134806.0611
March | 373766.8201 | 640.711 | 1633.1413 | 0 | 0.0064 | 1698120 | 158929.337
April | 356701.2061 | 619.4838 | 1602.019 | 0 | 0.0063 | 1665810 | 152460.2007
May | 444207.7872 | 777.3677 | 2027.0227 | 0 | 0.0079 | 2107780 | 190441.8217
June | 474842.8121 | 832.0406 | 2172.5618 | 0 | 0.0085 | 2259120 | 203679.8469
July | 478968.2482 | 839.521 | 2192.7985 | 0 | 0.0085 | 2280170 | 205474.0918
August | 505515.5813 | 885.9456 | 2313.7592 | 0 | 0.009 | 2405950 | 216852.2486
September | 434891.2488 | 761.4405 | 1986.5483 | 0 | 0.0077 | 2065690 | 186484.5684
October | 379259.6744 | 658.8959 | 1704.604 | 0 | 0.0067 | 1772480 | 162125.0979
November | 342339.5903 | 584.791 | 1484.7409 | 0 | 0.0058 | 1543800 | 145365.3347
December | 361774.6143 | 606.3628 | 1506.0973 | 0 | 0.0059 | 1565930 | 152477.3597
Annual Sum or Average | 4839900 | 8363.5466 | 21510.092 | 0 | 0.0841 | 22366400 | 2064550
Minimum of Months | 318416.1244 | 539.8383 | 1358.8671 | 0 | 0.0053 | 1412890 | 134806.0611
Maximum of Months | 505515.5813 | 885.9456 | 2313.7592 | 0 | 0.009 | 2405950 | 216852.2486
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1259480000000 | 1205680.068 | 26-JAN-16:15 | 448566.543 | 418415.216 | 66042.684 | 0 | 101648.073 | 0 | 89963.745 | 81043.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1120160000000 | 1365613.304 | 14-FEB-16:15 | 448566.543 | 418415.216 | 71748.957 | 0 | 252809.571 | 0 | 93029.21 | 81043.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1346290000000 | 1384980.001 | 02-MAR-13:00 | 448566.543 | 423230.021 | 73507.497 | 0 | 265251.259 | 0 | 93380.873 | 81043.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1320680000000 | 1448939.789 | 21-APR-15:30 | 448566.543 | 418415.216 | 87411.226 | 0 | 316528.285 | 0 | 96974.712 | 81043.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1671070000000 | 1480796.38 | 31-MAY-15:00 | 448566.543 | 418415.216 | 94908.744 | 0 | 338708.493 | 0 | 99153.577 | 81043.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1791060000000 | 1620423.437 | 29-JUN-15:30 | 448566.543 | 418415.216 | 177047.197 | 0 | 374099.514 | 0 | 121251.16 | 81043.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1807740000000 | 1613868.056 | 03-JUL-15:45 | 448566.543 | 418415.216 | 176555.426 | 0 | 378452.692 | 0 | 110834.372 | 81043.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 1907460000000 | 1619806.692 | 01-AUG-15:30 | 448566.543 | 418415.216 | 170818.315 | 0 | 390377.024 | 0 | 110585.787 | 81043.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1637710000000 | 1565950.099 | 21-SEP-15:30 | 448566.543 | 418415.216 | 155733.385 | 0 | 344588.495 | 0 | 117602.653 | 81043.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1405250000000 | 1439678.739 | 11-OCT-15:30 | 448566.543 | 418415.216 | 79716.692 | 0 | 305763.641 | 0 | 106172.841 | 81043.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1223940000000 | 1318368.833 | 01-NOV-13:00 | 448566.543 | 423230.021 | 71358.236 | 0 | 202177.267 | 0 | 91992.958 | 81043.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1241490000000 | 1196374.607 | 05-DEC-13:00 | 448566.543 | 423230.021 | 69381.481 | 0 | 84483.687 | 0 | 89669.068 | 81043.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 17732300000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1120160000000 | 1196374.607 |  | 448566.543 | 418415.216 | 66042.684 | 0 | 84483.687 | 0 | 89669.068 | 81043.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1907460000000 | 1620423.437 |  | 448566.543 | 423230.021 | 177047.197 | 0 | 390377.024 | 0 | 121251.16 | 81043.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 182085.66 | 20042.2 | 0 | 202127.86
Cost per Total Building Area ($/m2) | 3.93 | 0.43 | 0 | 4.36
Cost per Net Conditioned Building Area ($/m2) | 3.93 | 0.43 | 0 | 4.36

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 19251.14 | 415.61 | 415.61
Net Site Energy | 19251.14 | 415.61 | 415.61
Total Source Energy | 30421.32 | 656.76 | 656.76
Net Source Energy | 30421.32 | 656.76 | 656.76
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4512.83 | 0 | 0 | 0 | 0
Cooling | 876.29 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.72 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6687.85 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 870.26 | 0 | 0 | 0 | 0 | 0
Pumps | 484.98 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 340.66 | 0 | 0 | 0 | 0 | 4981.03
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 278.19 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 14460.11 | 4791.03 | 0 | 0 | 0 | 6484.97
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.17 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 95.067
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.17 | 6.5404
Conditioned Total | 46320.38 |  | 126016.37 |  | 8024.24 | 4636.15 | 10.76 | 19.33 | 12.5776
Unconditioned Total | 42757.27 |  | 52129.67 |  | 3565.29 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.501 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 115.9 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 1159.04 | 3.18 | 0.501 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 772.69 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 1159.04 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 772.69 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.501 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 115.9 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 1390.85 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 3245.31 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3511716.91 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 4839766.42 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3320168.72
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_5_COOLC | Coil:Cooling:Water | 74657.33 | - | - | - | -
VAV_1_COOLC | Coil:Cooling:Water | 259742.64 | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water | 2793709.89 | - | - | - | -
VAV_3_COOLC | Coil:Cooling:Water | 383607.05 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_5_HEATC | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_3_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1388.3 | 5.23 | 12276.98 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 17.64 | 40244.92 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 191.25 | 429982.06 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.61 | 1572.42 | 26.64 | 68192.9 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 27660.43 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 32180.03 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 46859.55 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 100093.0402 | 127.6634 | 235.4262 | 0 | 0.001 | 3108740 | 38584.4116
February | 78467.9899 | 104.5397 | 213.0251 | 0 | 0.0009 | 2813770 | 30725.7096
March | 85836.6965 | 117.3387 | 252.0696 | 0 | 0.001 | 3329970 | 33930.4543
April | 70784.8334 | 100.7628 | 233.4071 | 0 | 0.0009 | 3084020 | 28408.991
May | 68624.4489 | 105.0902 | 273.5488 | 0 | 0.0011 | 3615390 | 28334.7801
June | 68918.0103 | 107.8085 | 289.2044 | 0 | 0.0011 | 3822550 | 28698.9723
July | 69145.9154 | 109.2961 | 297.3824 | 0 | 0.0012 | 3930760 | 28915.0147
August | 75044.3748 | 118.5951 | 322.5943 | 0 | 0.0013 | 4264000 | 31378.9769
September | 68967.9752 | 105.692 | 275.4017 | 0 | 0.0011 | 3639880 | 28484.7317
October | 74081.8577 | 106.4169 | 250.4128 | 0 | 0.001 | 3308840 | 29835.1235
November | 85364.7201 | 113.8722 | 232.6696 | 0 | 0.001 | 3073260 | 33441.7146
December | 99235.7317 | 126.1501 | 230.7286 | 0 | 0.001 | 3046630 | 38208.9579
Annual Sum or Average | 944565.5942 | 1343.2256 | 3105.8706 | 0 | 0.0126 | 41037800 | 378947.8383
Minimum of Months | 68624.4489 | 100.7628 | 213.0251 | 0 | 0.0009 | 2813770 | 28334.7801
Maximum of Months | 100093.0402 | 127.6634 | 322.5943 | 0 | 0.0013 | 4264000 | 38584.4116
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1095400000000 | 1053859.836 | 31-JAN-08:00 | 448566.543 | 473785.475 | 47410.049 | 0 | 33880.376 | 0 | 48711.789 | 1505.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 991461000000 | 1139816.841 | 21-FEB-13:00 | 448566.543 | 423230.021 | 47439.714 | 0 | 127278.345 | 0 | 49725.003 | 43577.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1173350000000 | 1185178.908 | 29-MAR-15:30 | 448566.543 | 418415.216 | 53186.445 | 0 | 170737.495 | 0 | 50695.996 | 43577.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1086690000000 | 1150271.075 | 14-APR-15:15 | 448566.543 | 418415.216 | 49067.736 | 0 | 140733.542 | 0 | 49910.823 | 43577.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1273920000000 | 1258913.857 | 04-MAY-15:15 | 448566.543 | 418415.216 | 65652.149 | 0 | 227321.768 | 0 | 55380.967 | 43577.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1346920000000 | 1284410.287 | 28-JUN-15:15 | 448566.543 | 418415.216 | 71868.846 | 0 | 246537.248 | 0 | 55445.22 | 43577.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1385040000000 | 1317006.039 | 31-JUL-15:00 | 448566.543 | 418415.216 | 72489.184 | 0 | 277614.079 | 0 | 56343.803 | 43577.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 1502470000000 | 1305763.412 | 07-AUG-15:15 | 448566.543 | 418415.216 | 74839.868 | 0 | 264394.937 | 0 | 55969.634 | 43577.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1282550000000 | 1297836.731 | 01-SEP-15:45 | 448566.543 | 418415.216 | 66799.667 | 0 | 264743.101 | 0 | 55734.99 | 43577.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1165910000000 | 1214579.359 | 17-OCT-12:00 | 448566.543 | 423230.021 | 53990.353 | 0 | 193977.949 | 0 | 51237.279 | 43577.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1082900000000 | 1127136.328 | 03-NOV-13:00 | 448566.543 | 423230.021 | 47939.363 | 0 | 113222.372 | 0 | 50600.815 | 43577.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1073510000000 | 1058368.178 | 29-DEC-08:45 | 448566.543 | 473785.475 | 47410.049 | 0 | 36489.651 | 0 | 48663.218 | 3453.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 14460100000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 991461000000 | 1053859.836 |  | 448566.543 | 418415.216 | 47410.049 | 0 | 33880.376 | 0 | 48663.218 | 1505.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1502470000000 | 1317006.039 |  | 448566.543 | 473785.475 | 74839.868 | 0 | 277614.079 | 0 | 56343.803 | 43577.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 298072.78 | 40386.83 | 0 | 338459.6
Cost per Total Building Area ($/m2) | 6.44 | 0.87 | 0 | 7.31
Cost per Net Conditioned Building Area ($/m2) | 6.44 | 0.87 | 0 | 7.31

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 22766.6 | 491.5 | 491.5
Net Site Energy | 22766.6 | 491.5 | 491.5
Total Source Energy | 64874.8 | 1400.57 | 1400.57
Net Source Energy | 64874.8 | 1400.57 | 1400.57
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 6173.79 | 0 | 0 | 0 | 0
Cooling | 2013.4 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.74 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6687.85 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 991.76 | 0 | 0 | 0 | 0 | 0
Pumps | 969.05 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 443.35 | 0 | 0 | 0 | 0 | 9507.83
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 287.32 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 16305.49 | 6461.11 | 0 | 0 | 0 | 11011.78
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.17 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 95.067
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.17 | 6.5404
Conditioned Total | 46320.38 |  | 126016.37 |  | 8024.24 | 4636.15 | 10.76 | 19.33 | 12.5776
Unconditioned Total | 42757.27 |  | 52129.67 |  | 3565.29 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.501 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 115.9 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 1159.04 | 3.18 | 0.501 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 772.69 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 1159.04 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 772.69 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.501 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 115.9 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 1390.85 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 3245.31 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4249822.77 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 5493878.41 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 4018014.26
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_5_COOLC | Coil:Cooling:Water | 118509.27 | - | - | - | -
VAV_1_COOLC | Coil:Cooling:Water | 314547.15 | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water | 3361921.38 | - | - | - | -
VAV_3_COOLC | Coil:Cooling:Water | 454844.97 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_5_HEATC | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_3_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_5_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 6.79 | 15692.46 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 18.53 | 42287.94 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 200.95 | 451782.66 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.61 | 1572.42 | 28.46 | 72847.77 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 31398.83 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 38943.74 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 56708.67 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 523157.6283 | 876.5059 | 2409.8579 | 0 | 0.0074 | 554677.8632 | 219466.1237
February | 446757.7253 | 760.8045 | 2131.6672 | 0 | 0.0065 | 490665.5813 | 188592.1623
March | 470315.1368 | 819.5786 | 2355.9137 | 0 | 0.0072 | 542310.2653 | 200320.3924
April | 406027.3708 | 721.8031 | 2119.3276 | 0 | 0.0064 | 487870.4686 | 174301.2141
May | 488158.0899 | 882.9994 | 2639.0874 | 0 | 0.008 | 607540.1681 | 211011.0535
June | 552873.2746 | 1005.1328 | 3019.3693 | 0 | 0.0091 | 695090.9372 | 239469.9535
July | 559906.3412 | 1018.3671 | 3060.4644 | 0 | 0.0092 | 704552.0523 | 242559.0736
August | 594979.9955 | 1081.8603 | 3250.383 | 0 | 0.0098 | 748272.9921 | 257724.8315
September | 500883.3081 | 908.214 | 2721.0513 | 0 | 0.0082 | 626411.8396 | 216721.6805
October | 447273.1444 | 800.7507 | 2368.3319 | 0 | 0.0072 | 545199.0661 | 192545.1074
November | 425951.2707 | 743.9192 | 2143.5753 | 0 | 0.0065 | 493434.197 | 181582.3172
December | 491926.7239 | 830.9514 | 2306.5826 | 0 | 0.0071 | 530917.3997 | 207011.9781
Annual Sum or Average | 5908210 | 10450.887 | 30525.6115 | 0 | 0.0927 | 7026940 | 2531310
Minimum of Months | 406027.3708 | 721.8031 | 2119.3276 | 0 | 0.0064 | 487870.4686 | 174301.2141
Maximum of Months | 594979.9955 | 1081.8603 | 3250.383 | 0 | 0.0098 | 748272.9921 | 257724.8315
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1287090000000 | 1080410.089 | 24-JAN-08:45 | 448566.543 | 473785.475 | 50157.555 | 0 | 45564.419 | 0 | 58935.083 | 3401.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1138550000000 | 1079427.322 | 13-FEB-08:30 | 448566.543 | 473785.475 | 50157.555 | 0 | 44017.591 | 0 | 58882.742 | 4017.415 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1258390000000 | 1237623.904 | 31-MAR-15:15 | 448566.543 | 418415.216 | 51505.647 | 0 | 205476.694 | 0 | 60923.367 | 52736.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1132070000000 | 1250134.176 | 07-APR-12:00 | 448566.543 | 423230.021 | 56669.875 | 0 | 204045.118 | 0 | 64886.181 | 52736.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1409750000000 | 1463020.998 | 30-MAY-07:00 | 448566.543 | 473785.475 | 57378.642 | 0 | 361968.443 | 0 | 68585.457 | 52736.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1612910000000 | 1515111.584 | 08-JUN-12:00 | 448566.543 | 423230.021 | 73921.335 | 0 | 446927.301 | 0 | 69729.946 | 52736.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1634860000000 | 1513876.642 | 14-JUL-12:00 | 448566.543 | 423230.021 | 74047.555 | 0 | 444178.478 | 0 | 71117.608 | 52736.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 1736310000000 | 1558908.824 | 04-AUG-15:30 | 448566.543 | 418415.216 | 79885.027 | 0 | 488415.435 | 0 | 70890.165 | 52736.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1453540000000 | 1453154.544 | 07-SEP-12:00 | 448566.543 | 423230.021 | 56597.068 | 0 | 402494.52 | 0 | 69529.954 | 52736.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1265090000000 | 1363532.665 | 31-OCT-08:00 | 448566.543 | 473785.475 | 52487.933 | 0 | 270574.085 | 0 | 65382.191 | 52736.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1144980000000 | 1383591.641 | 02-NOV-08:00 | 448566.543 | 473785.475 | 51422.164 | 0 | 291016.188 | 0 | 66064.833 | 52736.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1231950000000 | 1073864.25 | 11-DEC-08:45 | 448566.543 | 473785.475 | 50157.555 | 0 | 41958.126 | 0 | 59039.604 | 356.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 16305500000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1132070000000 | 1073864.25 |  | 448566.543 | 418415.216 | 50157.555 | 0 | 41958.126 | 0 | 58882.742 | 356.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1736310000000 | 1558908.824 |  | 448566.543 | 473785.475 | 79885.027 | 0 | 488415.435 | 0 | 71117.608 | 52736.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 389210.17 | 53744.46 | 0 | 442954.63
Cost per Total Building Area ($/m2) | 8.4 | 1.16 | 0 | 9.56
Cost per Net Conditioned Building Area ($/m2) | 8.4 | 1.16 | 0 | 9.56

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 20066.73 | 433.22 | 433.22
Net Site Energy | 20066.73 | 433.22 | 433.22
Total Source Energy | 56798.65 | 1226.21 | 1226.21
Net Source Energy | 56798.65 | 1226.21 | 1226.21
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4108.62 | 0 | 0 | 0 | 0
Cooling | 1574.08 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.75 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6687.85 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1116.23 | 0 | 0 | 0 | 0 | 0
Pumps | 715.08 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 378.62 | 0 | 0 | 0 | 0 | 10929.48
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 286.14 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 15671.96 | 4394.76 | 0 | 0 | 0 | 12433.42
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.17 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 95.067
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.17 | 6.5404
Conditioned Total | 46320.38 |  | 126016.37 |  | 8024.24 | 4636.15 | 10.76 | 19.33 | 12.5776
Unconditioned Total | 42757.27 |  | 52129.67 |  | 3565.29 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.501 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 115.9 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 1159.04 | 3.18 | 0.501 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 772.69 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 1159.04 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 772.69 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.501 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 115.9 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 1390.85 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 3245.31 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3346106.39 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 5011579.04 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3163591.5
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_5_COOLC | Coil:Cooling:Water | 72864.87 | - | - | - | -
VAV_1_COOLC | Coil:Cooling:Water | 245517.68 | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water | 2646918.83 | - | - | - | -
VAV_3_COOLC | Coil:Cooling:Water | 380805.01 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_5_HEATC | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_3_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_5_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 6.57 | 15188.24 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 20.82 | 47252.44 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 226.17 | 508485.53 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.61 | 1572.42 | 32.56 | 83357.44 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28642.38 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 30662.43 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 44649.68 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 379627.039 | 622.4388 | 1505.4766 | 0 | 0.006 | 1565190 | 158643.4805
February | 323117.4632 | 537.8793 | 1325.187 | 0 | 0.0052 | 1377810 | 135822.4612
March | 362013.6818 | 613.583 | 1544.0034 | 0 | 0.0061 | 1605390 | 153247.0454
April | 324171.1235 | 558.563 | 1431.9653 | 0 | 0.0056 | 1488960 | 138122.1684
May | 359118.1244 | 624.1883 | 1615.6183 | 0 | 0.0063 | 1679960 | 153542.969
June | 385607.796 | 673.763 | 1753.9117 | 0 | 0.0068 | 1823780 | 165215.2914
July | 406812.2036 | 712.5293 | 1859.648 | 0 | 0.0072 | 1933740 | 174468.7586
August | 425129.7414 | 744.3615 | 1942.0246 | 0 | 0.0076 | 2019400 | 182299.959
September | 361178.6564 | 629.9378 | 1636.6229 | 0 | 0.0064 | 1701810 | 154636.6245
October | 348233.9869 | 600.929 | 1543.1542 | 0 | 0.006 | 1604580 | 148463.5473
November | 333064.9894 | 562.0887 | 1407.3909 | 0 | 0.0055 | 1463330 | 140754.3059
December | 364559.2242 | 597.8338 | 1446.2654 | 0 | 0.0057 | 1503630 | 152356.5838
Annual Sum or Average | 4372630 | 7478.0957 | 19011.2682 | 0 | 0.0745 | 19767600 | 1857570
Minimum of Months | 323117.4632 | 537.8793 | 1325.187 | 0 | 0.0052 | 1377810 | 135822.4612
Maximum of Months | 425129.7414 | 744.3615 | 1942.0246 | 0 | 0.0076 | 2019400 | 182299.959
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1240900000000 | 1167681.795 | 24-JAN-13:00 | 448566.543 | 423230.021 | 58671.35 | 0 | 147581.314 | 0 | 48110.428 | 41522.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1092340000000 | 1107566.573 | 07-FEB-13:00 | 448566.543 | 423230.021 | 66277.779 | 0 | 80955.787 | 0 | 47014.304 | 41522.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1272770000000 | 1223670.857 | 30-MAR-15:00 | 448566.543 | 418415.216 | 65905.045 | 0 | 199406.067 | 0 | 49855.848 | 41522.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1180460000000 | 1258190.508 | 26-APR-15:45 | 448566.543 | 418415.216 | 75693.257 | 0 | 223010.18 | 0 | 50983.173 | 41522.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1331890000000 | 1299231.461 | 23-MAY-15:00 | 448566.543 | 418415.216 | 86259.88 | 0 | 252051.013 | 0 | 52416.671 | 41522.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1445910000000 | 1420560.152 | 27-JUN-15:15 | 448566.543 | 418415.216 | 159675.416 | 0 | 288541.217 | 0 | 63839.622 | 41522.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1533090000000 | 1412900.384 | 17-JUL-12:45 | 448566.543 | 423230.021 | 149997.461 | 0 | 285004.908 | 0 | 64579.312 | 41522.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 1601000000000 | 1429277.338 | 30-AUG-15:30 | 448566.543 | 418415.216 | 163401.352 | 0 | 295504.321 | 0 | 61867.768 | 41522.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1349220000000 | 1398803.509 | 01-SEP-15:30 | 448566.543 | 418415.216 | 153886.446 | 0 | 272387.552 | 0 | 64025.614 | 41522.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1272130000000 | 1288349.417 | 05-OCT-15:15 | 448566.543 | 418415.216 | 83091.542 | 0 | 244796.504 | 0 | 51957.474 | 41522.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1160140000000 | 1219211.599 | 10-NOV-13:00 | 448566.543 | 423230.021 | 65818.337 | 0 | 190476.198 | 0 | 49598.362 | 41522.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1192100000000 | 1091794.239 | 06-DEC-08:30 | 448566.543 | 473785.475 | 56327.94 | 0 | 60317.218 | 0 | 47039.736 | 5757.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 15672000000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1092340000000 | 1091794.239 |  | 448566.543 | 418415.216 | 56327.94 | 0 | 60317.218 | 0 | 47014.304 | 5757.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1601000000000 | 1429277.338 |  | 448566.543 | 473785.475 | 163401.352 | 0 | 295504.321 | 0 | 64579.312 | 41522.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 160951.03 | 30370.96 | 0 | 191321.99
Cost per Total Building Area ($/m2) | 3.47 | 0.66 | 0 | 4.13
Cost per Net Conditioned Building Area ($/m2) | 3.47 | 0.66 | 0 | 4.13

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 24816 | 535.75 | 535.75
Net Site Energy | 24816 | 535.75 | 535.75
Total Source Energy | 65204.75 | 1407.69 | 1407.69
Net Source Energy | 65204.75 | 1407.69 | 1407.69
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 8259.4 | 0 | 0 | 0 | 0
Cooling | 1905.39 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.79 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6687.85 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1039.55 | 0 | 0 | 0 | 0 | 0
Pumps | 1003.12 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 413.71 | 0 | 0 | 0 | 0 | 8497.49
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 306.84 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 16249.76 | 8566.24 | 0 | 0 | 0 | 10001.44
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.17 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 95.067
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.17 | 6.5404
Conditioned Total | 46320.38 |  | 126016.37 |  | 8024.24 | 4636.15 | 10.76 | 19.33 | 12.5776
Unconditioned Total | 42757.27 |  | 52129.67 |  | 3565.29 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.501 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 115.9 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 1159.04 | 3.18 | 0.501 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 772.69 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 1159.04 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 772.69 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.501 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 115.9 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 1390.85 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 3245.31 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4162562.2 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 5636831.07 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3935513.35
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_5_COOLC | Coil:Cooling:Water | 113421.05 | - | - | - | -
VAV_1_COOLC | Coil:Cooling:Water | 307562.06 | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water | 3298191 | - | - | - | -
VAV_3_COOLC | Coil:Cooling:Water | 443388.08 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_5_HEATC | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_3_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_5_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 6.72 | 15522.11 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 18.67 | 42608.45 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 202.87 | 456103.4 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.61 | 1572.42 | 28.46 | 72846.64 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 32215.84 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 38144.12 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 55544.28 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 406895.3589 | 631.1031 | 854.2152 | 0 | 0.0065 | 561103.5568 | 165848.1374
February | 335811.0284 | 540.5635 | 769.1753 | 0 | 0.0058 | 505347.4486 | 138758.9496
March | 327076.6507 | 554.8512 | 841.4738 | 0 | 0.0062 | 552984.0018 | 137859.5168
April | 269843.1324 | 474.9504 | 750.2015 | 0 | 0.0055 | 493077.0752 | 115379.2881
May | 317448.0554 | 573.7545 | 931.4402 | 0 | 0.0068 | 612257.443 | 137169.3643
June | 349047.8542 | 635.0773 | 1037.8655 | 0 | 0.0076 | 682229.1611 | 151226.016
July | 354886.9175 | 646.3477 | 1057.3324 | 0 | 0.0077 | 695027.8717 | 153817.5972
August | 380210.514 | 692.0805 | 1131.5152 | 0 | 0.0083 | 743789.8225 | 164756.3927
September | 302698.2202 | 547.584 | 889.752 | 0 | 0.0065 | 584856.6781 | 130842.6354
October | 279125.0381 | 490.7098 | 774.1254 | 0 | 0.0057 | 508798.9587 | 119292.8149
November | 307158.9009 | 515.7879 | 773.0552 | 0 | 0.0057 | 507999.3229 | 128960.1735
December | 378046.024 | 602.2758 | 845.4841 | 0 | 0.0064 | 555452.054 | 155610.9312
Annual Sum or Average | 4008250 | 6905.0856 | 10655.6359 | 0 | 0.0786 | 7002920 | 1699520
Minimum of Months | 269843.1324 | 474.9504 | 750.2015 | 0 | 0.0055 | 493077.0752 | 115379.2881
Maximum of Months | 406895.3589 | 692.0805 | 1131.5152 | 0 | 0.0083 | 743789.8225 | 165848.1374
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1302000000000 | 1073967.568 | 30-JAN-08:15 | 448566.543 | 473785.475 | 50542.362 | 0 | 39623.399 | 0 | 58269.056 | 3180.732 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1172620000000 | 1051126.842 | 28-FEB-08:15 | 448566.543 | 473785.475 | 50542.362 | 0 | 20997.217 | 0 | 57235.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1283160000000 | 1166508.719 | 23-MAR-15:00 | 448566.543 | 418415.216 | 51905.324 | 0 | 137339.287 | 0 | 58628.737 | 51653.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1144150000000 | 1248149.698 | 14-APR-15:45 | 448566.543 | 418415.216 | 57216.953 | 0 | 212168.137 | 0 | 60129.237 | 51653.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1420700000000 | 1364961.662 | 31-MAY-07:00 | 448566.543 | 473785.475 | 58374.421 | 0 | 268409.019 | 0 | 64172.591 | 51653.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1583060000000 | 1483254.726 | 29-JUN-15:15 | 448566.543 | 418415.216 | 84125.918 | 0 | 412085.328 | 0 | 68408.108 | 51653.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1612760000000 | 1502439.818 | 14-JUL-07:30 | 448566.543 | 473785.475 | 56567.297 | 0 | 403403.201 | 0 | 68463.689 | 51653.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 1725910000000 | 1514185.483 | 17-AUG-07:00 | 448566.543 | 473785.475 | 57557.734 | 0 | 413925.534 | 0 | 68696.583 | 51653.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1357120000000 | 1400264.501 | 22-SEP-15:00 | 448566.543 | 418415.216 | 53292.768 | 0 | 361386.663 | 0 | 66949.698 | 51653.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1180630000000 | 1262928.928 | 06-OCT-15:15 | 448566.543 | 418415.216 | 58381.975 | 0 | 221003.933 | 0 | 64907.649 | 51653.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1178770000000 | 1191734.694 | 02-NOV-14:00 | 448566.543 | 396748.592 | 55339.619 | 0 | 180078.619 | 0 | 59347.707 | 51653.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1288880000000 | 1068150.79 | 26-DEC-08:15 | 448566.543 | 473785.475 | 50542.362 | 0 | 35589.363 | 0 | 58479.763 | 1187.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 16249800000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1144150000000 | 1051126.842 |  | 448566.543 | 396748.592 | 50542.362 | 0 | 20997.217 | 0 | 57235.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1725910000000 | 1514185.483 |  | 448566.543 | 473785.475 | 84125.918 | 0 | 413925.534 | 0 | 68696.583 | 51653.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 282633.33 | 67572.48 | 0 | 350205.81
Cost per Total Building Area ($/m2) | 6.1 | 1.46 | 0 | 7.56
Cost per Net Conditioned Building Area ($/m2) | 6.1 | 1.46 | 0 | 7.56

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 23161.85 | 500.04 | 500.04
Net Site Energy | 23161.85 | 500.04 | 500.04
Total Source Energy | 64082.47 | 1383.46 | 1383.46
Net Source Energy | 64082.47 | 1383.46 | 1383.46
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 6580.59 | 0 | 0 | 0 | 0
Cooling | 1436.21 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.71 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6687.85 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1081.15 | 0 | 0 | 0 | 0 | 0
Pumps | 1352.12 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 513.47 | 0 | 0 | 0 | 0 | 11770.58
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 310.39 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 16270.86 | 6890.98 | 0 | 0 | 0 | 13274.52
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.17 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 95.067
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.17 | 6.5404
Conditioned Total | 46320.38 |  | 126016.37 |  | 8024.24 | 4636.15 | 10.76 | 19.33 | 12.5776
Unconditioned Total | 42757.27 |  | 52129.67 |  | 3565.29 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.501 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 115.9 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 1159.04 | 3.18 | 0.501 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 772.69 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 1159.04 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 772.69 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 115.9 | 115.9 | 3.18 | 0.501 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 115.9 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 77.27 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 1390.85 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 3245.31 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 6129093.76 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 5334689.31 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 5794779.55
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_5_COOLC | Coil:Cooling:Water | 68598.1 | - | - | - | -
VAV_1_COOLC | Coil:Cooling:Water | 244630.97 | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water | 4634861.66 | - | - | - | -
VAV_3_COOLC | Coil:Cooling:Water | 661072.49 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_5_HEATC | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_3_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1388.3 | 6.07 | 14241.72 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 19.94 | 45253.36 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 217.41 | 488787.41 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.61 | 1572.42 | 30.93 | 79166.96 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 30489.03 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 56164.66 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 81785.23 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 404958.763 | 643.0917 | 998.2188 | 0 | 0.0071 | 23670400 | 166788.5161
February | 338727.3707 | 549.6643 | 877.4563 | 0 | 0.0062 | 20808900 | 140645.9797
March | 353547.0455 | 596.5609 | 998.4766 | 0 | 0.007 | 23682800 | 149007.9843
April | 288413.8482 | 495.2964 | 845.7708 | 0 | 0.0059 | 20062200 | 122391.6063
May | 321485.1233 | 562.5952 | 980.7436 | 0 | 0.0068 | 23265400 | 137441.228
June | 362091.3693 | 638.7569 | 1123.0685 | 0 | 0.0078 | 26642400 | 155294.3085
July | 392040.73 | 694.5152 | 1226.5392 | 0 | 0.0085 | 29097400 | 168421.8064
August | 394657.5969 | 698.3555 | 1231.8493 | 0 | 0.0085 | 29223300 | 169469.12
September | 330357.3188 | 580.389 | 1016.0106 | 0 | 0.0071 | 24102300 | 141453.4647
October | 309907.0654 | 533.6095 | 913.8718 | 0 | 0.0064 | 21677800 | 131648.068
November | 322515.3779 | 540.9164 | 898.9651 | 0 | 0.0063 | 21322000 | 135611.855
December | 381869.3081 | 611.3111 | 958.9753 | 0 | 0.0068 | 22740700 | 157751.1077
Annual Sum or Average | 4200570 | 7145.0621 | 12069.9459 | 0 | 0.0844 | 286296000 | 1775930
Minimum of Months | 288413.8482 | 495.2964 | 845.7708 | 0 | 0.0059 | 20062200 | 122391.6063
Maximum of Months | 404958.763 | 698.3555 | 1231.8493 | 0 | 0.0085 | 29223300 | 169469.12
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1345250000000 | 1122274.563 | 20-JAN-08:00 | 448566.543 | 473785.475 | 54017.757 | 0 | 56272.232 | 0 | 84299.303 | 5333.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1182620000000 | 1131642.651 | 03-FEB-15:15 | 448566.543 | 396748.592 | 58146.201 | 0 | 68257.556 | 0 | 83867.277 | 76056.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1345950000000 | 1335688.263 | 30-MAR-15:00 | 448566.543 | 418415.216 | 63998.968 | 0 | 241452.719 | 0 | 87198.336 | 76056.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1140180000000 | 1283327.321 | 06-APR-15:00 | 448566.543 | 418415.216 | 57782.165 | 0 | 196380.712 | 0 | 86126.204 | 76056.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1322230000000 | 1379361.195 | 16-MAY-15:00 | 448566.543 | 418415.216 | 68000.585 | 0 | 279455.958 | 0 | 88866.412 | 76056.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1514150000000 | 1492041.261 | 30-JUN-12:00 | 448566.543 | 423230.021 | 91796.846 | 0 | 353630.485 | 0 | 98760.884 | 76056.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1653680000000 | 1574175.614 | 21-JUL-15:45 | 448566.543 | 418415.216 | 160604.988 | 0 | 360800.817 | 0 | 109731.569 | 76056.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 1660830000000 | 1542681.256 | 09-AUG-15:00 | 448566.543 | 418415.216 | 148675.586 | 0 | 342792.924 | 0 | 108174.505 | 76056.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1369790000000 | 1445608.273 | 01-SEP-15:00 | 448566.543 | 418415.216 | 81719.306 | 0 | 316532.767 | 0 | 104317.96 | 76056.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1232000000000 | 1377488.963 | 06-OCT-15:30 | 448566.543 | 418415.216 | 70067.53 | 0 | 275626.149 | 0 | 88757.044 | 76056.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1211780000000 | 1144583.523 | 21-NOV-08:00 | 448566.543 | 473785.475 | 54387.948 | 0 | 9291.692 | 0 | 82495.382 | 76056.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1292410000000 | 1122153.143 | 21-DEC-08:45 | 448566.543 | 473785.475 | 54017.757 | 0 | 57929.648 | 0 | 84224.767 | 3628.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 16270900000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1140180000000 | 1122153.143 |  | 448566.543 | 396748.592 | 54017.757 | 0 | 9291.692 | 0 | 82495.382 | 3628.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1660830000000 | 1574175.614 |  | 448566.543 | 473785.475 | 160604.988 | 0 | 360800.817 | 0 | 109731.569 | 76056.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 361947.28 | 55588.86 | 0 | 417536.14
Cost per Total Building Area ($/m2) | 7.81 | 1.2 | 0 | 9.01
Cost per Net Conditioned Building Area ($/m2) | 7.81 | 1.2 | 0 | 9.01

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 25638.48 | 553.5 | 553.5
Net Site Energy | 25638.48 | 553.5 | 553.5
Total Source Energy | 64277.78 | 1387.68 | 1387.68
Net Source Energy | 64277.78 | 1387.68 | 1387.68
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 9828 | 0 | 0 | 0 | 0
Cooling | 1307.23 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.69 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6687.85 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1083.33 | 0 | 0 | 0 | 0 | 0
Pumps | 915.72 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 277.28 | 0 | 0 | 0 | 0 | 5297.76
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 339.03 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 15471.45 | 10167.02 | 0 | 0 | 0 | 6801.71
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.17 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 95.067
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.17 | 6.5404
Conditioned Total | 46320.38 |  | 126016.37 |  | 8024.24 | 4636.15 | 10.76 | 19.33 | 12.5776
Unconditioned Total | 42757.27 |  | 52129.67 |  | 3565.29 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 115.9 | 115.9 | 3.18 | 0.651 | 0.64 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 77.27 | 77.27 | 3.18 | 0.501 | 0.49 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 115.9 | 115.9 | 3.18 | 0.501 | 0.49 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 77.27 | 77.27 | 3.18 | 0.501 | 0.49 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 115.9 | 1159.04 | 3.18 | 0.651 | 0.64 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 77.27 | 772.69 | 3.18 | 0.501 | 0.49 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 115.9 | 1159.04 | 3.18 | 0.501 | 0.49 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 77.27 | 772.69 | 3.18 | 0.501 | 0.49 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 115.9 | 115.9 | 3.18 | 0.651 | 0.64 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 77.27 | 77.27 | 3.18 | 0.501 | 0.49 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 115.9 | 115.9 | 3.18 | 0.501 | 0.49 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 77.27 | 77.27 | 3.18 | 0.501 | 0.49 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.18 | 0.546 | 0.535
North Total or Average |  |  | 1390.85 | 3.18 | 0.651 | 0.64
Non-North Total or Average |  |  | 3245.31 | 3.18 | 0.501 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3924405.89 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 5708479.31 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3710347.38
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_5_COOLC | Coil:Cooling:Water | 81275.6 | - | - | - | -
VAV_1_COOLC | Coil:Cooling:Water | 290559.14 | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water | 3132162.25 | - | - | - | -
VAV_3_COOLC | Coil:Cooling:Water | 420408.9 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_5_HEATC | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_3_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1388.3 | 5.24 | 12296.8 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 19.19 | 43548.18 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 210 | 472125.91 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.61 | 1572.42 | 28.79 | 73707.58 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 32625.33 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 35961.75 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 52366.38 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 409192.9945 | 636.4084 | 864.7098 | 0 | 0.0066 | 568006.2144 | 166951.1166
February | 348555.5935 | 552.993 | 772.0382 | 0 | 0.0058 | 507189.4107 | 143252.1817
March | 349744.8308 | 584.1885 | 870.1064 | 0 | 0.0065 | 571761.1176 | 146542.4713
April | 271509.644 | 471.2199 | 733.1364 | 0 | 0.0054 | 481834.4349 | 115454.8881
May | 285338.7071 | 507.4035 | 810.1463 | 0 | 0.0059 | 532496.9011 | 122499.9527
June | 313779.2783 | 568.7498 | 925.9707 | 0 | 0.0068 | 608668.3404 | 135739.5309
July | 336727.308 | 611.8347 | 998.5421 | 0 | 0.0073 | 656377.2791 | 145809.157
August | 335465.5109 | 608.155 | 990.2839 | 0 | 0.0072 | 650943.735 | 145130.194
September | 273129.8531 | 486.6658 | 778.6495 | 0 | 0.0057 | 511798.2946 | 117351.4907
October | 276738.2764 | 481.2076 | 750.2283 | 0 | 0.0055 | 493071.3476 | 117765.562
November | 328902.8182 | 542.0118 | 794.2777 | 0 | 0.0059 | 521900.2257 | 137105.838
December | 391959.9123 | 618.6439 | 857.7208 | 0 | 0.0065 | 563462.5258 | 160783.885
Annual Sum or Average | 3921040 | 6669.4819 | 10145.8101 | 0 | 0.0751 | 6667510 | 1654390
Minimum of Months | 271509.644 | 471.2199 | 733.1364 | 0 | 0.0054 | 481834.4349 | 115454.8881
Maximum of Months | 409192.9945 | 636.4084 | 998.5421 | 0 | 0.0073 | 656377.2791 | 166951.1166
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1318020000000 | 1062663.709 | 13-JAN-08:00 | 448566.543 | 473785.475 | 51799.107 | 0 | 33921.457 | 0 | 54591.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1176890000000 | 1079438.99 | 24-FEB-08:00 | 448566.543 | 473785.475 | 51799.107 | 0 | 46898.977 | 0 | 54439.77 | 3949.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1326730000000 | 1083384.67 | 17-MAR-07:00 | 448566.543 | 473785.475 | 51799.107 | 0 | 50401.829 | 0 | 54450.837 | 4380.878 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1118060000000 | 1170756.738 | 04-APR-15:15 | 448566.543 | 418415.216 | 56990.377 | 0 | 142452.687 | 0 | 55633.605 | 48698.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1235620000000 | 1277616.197 | 31-MAY-15:00 | 448566.543 | 418415.216 | 66984.887 | 0 | 236935.148 | 0 | 58016.094 | 48698.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1412370000000 | 1395672.146 | 14-JUN-10:45 | 448566.543 | 411193.008 | 63706.189 | 0 | 358894.333 | 0 | 64613.764 | 48698.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1523070000000 | 1541579.657 | 07-JUL-07:45 | 448566.543 | 473785.475 | 73425.417 | 0 | 429479.132 | 0 | 67624.779 | 48698.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 1510470000000 | 1410173.953 | 11-AUG-15:30 | 448566.543 | 418415.216 | 82165.064 | 0 | 347808.459 | 0 | 64520.362 | 48698.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1187590000000 | 1425437.362 | 08-SEP-12:15 | 448566.543 | 423230.021 | 63869.89 | 0 | 375744.672 | 0 | 65327.926 | 48698.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1144130000000 | 1204319.55 | 27-OCT-12:00 | 448566.543 | 423230.021 | 59585.311 | 0 | 168125.471 | 0 | 56113.895 | 48698.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1211030000000 | 1080293.451 | 17-NOV-08:15 | 448566.543 | 473785.475 | 51799.107 | 0 | 47734.665 | 0 | 54663.846 | 3743.814 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1307470000000 | 1073557.254 | 26-DEC-08:15 | 448566.543 | 473785.475 | 51799.107 | 0 | 40948.942 | 0 | 55544.891 | 2912.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 15471500000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1118060000000 | 1062663.709 |  | 448566.543 | 411193.008 | 51799.107 | 0 | 33921.457 | 0 | 54439.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1523070000000 | 1541579.657 |  | 448566.543 | 473785.475 | 82165.064 | 0 | 429479.132 | 0 | 67624.779 | 48698.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 271026.86 | 80059.01 | 0 | 351085.87
Cost per Total Building Area ($/m2) | 5.85 | 1.73 | 0 | 7.58
Cost per Net Conditioned Building Area ($/m2) | 5.85 | 1.73 | 0 | 7.58

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 32552.44 | 702.77 | 702.77
Net Site Energy | 32552.44 | 702.77 | 702.77
Total Source Energy | 73203.24 | 1580.37 | 1580.37
Net Source Energy | 73203.24 | 1580.37 | 1580.37
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 16990.65 | 0 | 0 | 0 | 0
Cooling | 1108 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.32 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6687.85 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1155.22 | 0 | 0 | 0 | 0 | 0
Pumps | 827.28 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 205.84 | 0 | 0 | 0 | 0 | 4135.01
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 377.93 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 15183.86 | 17368.58 | 0 | 0 | 0 | 5638.95
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.17 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.59 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.59 | 95.067
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.59 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | No | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 3563.11 | No | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.17 | 6.5404
Conditioned Total | 46320.38 |  | 126016.37 |  | 8024.24 | 4636.15 | 10.76 | 19.33 | 12.5776
Unconditioned Total | 42757.27 |  | 52129.67 |  | 3565.29 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 2.254 | 3.4 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 115.9 | 115.9 | 2.58 | 0.654 | 0.64 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 77.27 | 77.27 | 2.58 | 0.504 | 0.49 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 115.9 | 115.9 | 2.58 | 0.504 | 0.49 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 77.27 | 77.27 | 2.58 | 0.504 | 0.49 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 115.9 | 1159.04 | 2.58 | 0.654 | 0.64 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 77.27 | 772.69 | 2.58 | 0.504 | 0.49 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 115.9 | 1159.04 | 2.58 | 0.504 | 0.49 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 77.27 | 772.69 | 2.58 | 0.504 | 0.49 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 115.9 | 115.9 | 2.58 | 0.654 | 0.64 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 77.27 | 77.27 | 2.58 | 0.504 | 0.49 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 115.9 | 115.9 | 2.58 | 0.504 | 0.49 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 77.27 | 77.27 | 2.58 | 0.504 | 0.49 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 2.58 | 0.549 | 0.535
North Total or Average |  |  | 1390.85 | 2.58 | 0.654 | 0.64
Non-North Total or Average |  |  | 3245.31 | 2.58 | 0.504 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3695451.67 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 6391925.14 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3493881.58
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_5_COOLC | Coil:Cooling:Water | 51549.67 | - | - | - | -
VAV_1_COOLC | Coil:Cooling:Water | 266782.29 | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water | 3004310.85 | - | - | - | -
VAV_3_COOLC | Coil:Cooling:Water | 372808.86 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_5_HEATC | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_3_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1388.3 | 4.17 | 9788.81 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 19.33 | 43866.05 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 217.12 | 488151.57 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.61 | 1572.42 | 27.83 | 71237.24 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 36531.39 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 33863.7 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 49311.26 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 451171.9056 | 495.7583 | 1804.7376 | 0 | 0.0065 | 362015.917 | 169416.2263
February | 380039.0986 | 424.2931 | 1660.3122 | 0 | 0.0059 | 333081.5313 | 143736.287
March | 362672.3165 | 420.7349 | 1915.6394 | 0 | 0.0067 | 384382.0113 | 139604.0738
April | 263537.7705 | 317.2164 | 1632.3315 | 0 | 0.0056 | 327581.9561 | 103211.7462
May | 247785.0178 | 306.616 | 1709.6811 | 0 | 0.0058 | 343133.9182 | 98328.9904
June | 275272.3251 | 343.4201 | 1957.7209 | 0 | 0.0066 | 392924.3844 | 109666.2573
July | 273492.4416 | 341.4268 | 1949.8154 | 0 | 0.0066 | 391338.4087 | 108992.1269
August | 273057.136 | 339.2214 | 1911.9436 | 0 | 0.0065 | 383732.2831 | 108562.9077
September | 238456.3172 | 290.5262 | 1550.2026 | 0 | 0.0053 | 311112.2582 | 93927.4642
October | 307633.236 | 363.1948 | 1756.9445 | 0 | 0.0061 | 352564.9534 | 119388.8835
November | 383732.4241 | 434.9996 | 1814.1725 | 0 | 0.0064 | 363980.5928 | 146146.2001
December | 421052.7607 | 468.727 | 1811.1308 | 0 | 0.0065 | 363331.1162 | 159039.6321
Annual Sum or Average | 3877900 | 4546.1346 | 21474.6321 | 0 | 0.0745 | 4309180 | 1500020
Minimum of Months | 238456.3172 | 290.5262 | 1550.2026 | 0 | 0.0053 | 311112.2582 | 93927.4642
Maximum of Months | 451171.9056 | 495.7583 | 1957.7209 | 0 | 0.0067 | 392924.3844 | 169416.2263
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1275600000000 | 1087431.814 | 18-JAN-08:15 | 448566.543 | 473785.475 | 52843.32 | 0 | 51845.195 | 3997.501 | 52588.924 | 3804.857 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1173650000000 | 1074420.442 | 27-FEB-08:00 | 448566.543 | 473785.475 | 52843.32 | 0 | 46950.564 | 0 | 52274.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1354410000000 | 1065401.755 | 31-MAR-07:15 | 448566.543 | 473785.475 | 52843.32 | 0 | 38066.588 | 0 | 51251.77 | 888.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1154270000000 | 1103985.11 | 28-APR-07:45 | 448566.543 | 473785.475 | 52843.32 | 0 | 69950.203 | 0 | 51602.386 | 7237.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1209070000000 | 1227346.261 | 24-MAY-15:15 | 448566.543 | 418415.216 | 68801.724 | 0 | 191727.705 | 0 | 53977.877 | 45857.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1384510000000 | 1333828.719 | 20-JUN-15:00 | 448566.543 | 418415.216 | 82303.587 | 0 | 276292.328 | 0 | 62393.85 | 45857.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1378920000000 | 1329292.652 | 12-JUL-15:30 | 448566.543 | 418415.216 | 87735.837 | 0 | 272448.173 | 0 | 56269.688 | 45857.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 1352120000000 | 1296359.533 | 15-AUG-15:15 | 448566.543 | 418415.216 | 69948.354 | 0 | 254539.889 | 0 | 59032.335 | 45857.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1096240000000 | 1145472.876 | 07-SEP-15:00 | 448566.543 | 418415.216 | 57115.05 | 0 | 123208.334 | 0 | 52310.537 | 45857.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1242300000000 | 1096630.831 | 05-OCT-07:45 | 448566.543 | 473785.475 | 52843.32 | 0 | 62102.968 | 0 | 51707.711 | 7624.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1282520000000 | 1097963.753 | 14-NOV-08:45 | 448566.543 | 473785.475 | 52843.32 | 0 | 59297.514 | 3997.501 | 52244.211 | 7229.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1280240000000 | 1049369.384 | 19-DEC-08:15 | 448566.543 | 473785.475 | 52843.32 | 0 | 18785.912 | 3997.501 | 51390.633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 15183900000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1096240000000 | 1049369.384 |  | 448566.543 | 418415.216 | 52843.32 | 0 | 18785.912 | 0 | 51251.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1384510000000 | 1333828.719 |  | 448566.543 | 473785.475 | 87735.837 | 0 | 276292.328 | 3997.501 | 62393.85 | 45857.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 427269.87 | 71428.39 | 0 | 498698.26
Cost per Total Building Area ($/m2) | 9.22 | 1.54 | 0 | 10.77
Cost per Net Conditioned Building Area ($/m2) | 9.22 | 1.54 | 0 | 10.77

## Picture
DOE Commercial Building Benchmark - Large Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | 10.5 | 56.5 | 2946.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 2.8
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 14.1 | 86.15 | 4492.11
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.45
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 9.1 | 47.4 | 2471.57
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | 5.35 | 28.26 | 1473.56
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8 | 76 | 3962.86
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 12
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 122 | 6361.43
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 18
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 30.55 | 1592.96
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Sun, Hol, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 450 | 3058.2 | 159463.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624 | 4488 | 234017.14
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 648
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Core_bottom Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_bottom Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_bottom Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_bottom Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Core_mid Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_mid Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_mid Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_mid Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Core_top Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_top Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_top Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_top Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720