## BuildingSummary
Building Summary Medium Office new construction version 1.1_3.1
|  | Value | Data Source
Program
| Building Name | Benchmark Medium Office
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 4982.2 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 3
Window Fraction (Window to Wall Ratio)
| South | 0.33
| East | 0.33
| North | 0.33
| West | 0.33
| Total | 0.33
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor
| Floor to Ceiling Height (m) | 2.74
| Floor to Floor Height (m) | 3.96
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1977.67
| Net Dimensions - Total Area (m2) | 1324.84
| Wall to Skin Ratio | 0.544
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1661
| Net Dimensions - Total Area (m2) | 1661
| Roof to Skin Ratio | 0.456
Window Dimensions (m2)
| South | 195.85
| East | 130.57
| North | 195.85
| West | 130.57
| Total Area (m2) | 652.84
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1661
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 1423.65
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 9964.31
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.29 | See Benchmark Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | PACU | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 174.77

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Perimeter_bot_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0702 | 0 | 0 | 10 | 0 | 111.5894 | 0 | 0.262
Perimeter_bot_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.28 | 43.52 | 18.5806 | 7.0643 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 70.6435 | 0 | 0.2759
Perimeter_bot_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 111.5894 | 0 | 0.262
Perimeter_bot_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.28 | 43.52 | 18.5806 | 7.0638 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 70.6381 | 0 | 0.27592
Core_bottom | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 10.76 | 8.07 | 0 | 37.4755 | 10 | 0 | 529.3363 | 0 | 0
Perimeter_mid_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0702 | 0 | 0 | 10 | 0 | 111.5894 | 0 | 0.262
Perimeter_mid_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.28 | 43.52 | 18.5806 | 7.0643 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 70.6435 | 0 | 0.2759
Perimeter_mid_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 111.5894 | 0 | 0.262
Perimeter_mid_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.28 | 43.52 | 18.5806 | 7.0638 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 70.6381 | 0 | 0.27592
Core_mid | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 10.76 | 8.07 | 0 | 37.4755 | 10 | 0 | 529.3363 | 0 | 0
Perimeter_top_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0702 | 0 | 0 | 10 | 0 | 111.5894 | 0 | 0.65876
Perimeter_top_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.28 | 43.52 | 18.5806 | 7.0643 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 70.6435 | 0 | 0.67264
Perimeter_top_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 111.5894 | 0 | 0.65876
Perimeter_top_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.28 | 43.52 | 18.5806 | 7.0638 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 70.6381 | 0 | 0.67267
Core_top | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 10.76 | 8.07 | 0 | 37.4755 | 10 | 0 | 529.3363 | 0 | 0.39675
Firstfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.84 | 0 | [10 empty] | 0.10903
Midfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.84 | 0 | [10 empty] | 0.10903
Topfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.84 | 0 | [10 empty] | 1.0017
Total Conditioned Zones |  |  | 4982.19 | 19741.41 |  | 1977.72 | 652.8 |  | 268.139
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 42.2 | 369 | 83.3 | 414.1 | 472 | 52.6 | 21.6 | 938.7 | 23.5 | 118 | 832.4 | 187.6 | 236.8 | 28.1 | 32.3 | 1.67
Fabric
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7473 | 2.7473
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.49 | 6.49 | 6.49 | 3.18 | 3.18 | 3.18 | 6.49 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 2.58
| SHGC | 0.25 | 0.25 | 0.25 | 0.262 | 0.262 | 0.262 | 0.34 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.501 | 0.504
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.34 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| VAV_1_COOLC DXCOIL | 130.04 | 131.4295 | 125.3051 | 125.2013 | 104.9883 | 116.3533 | 93.541 | 133.6831 | 137.2774 | 109.2532 | 130.1057 | 131.6235 | 127.4467 | 125.3183 | 118.7181 | 113.4607
| VAV_2_COOLC DXCOIL | 150.3016 | 150.8444 | 158.3629 | 147.3676 | 128.303 | 152.7786 | 124.7998 | 158.409 | 168.4234 | 139.0772 | 156.4333 | 164.0052 | 154.3581 | 157.9309 | 152.1626 | 157.3825
| VAV_3_COOLC DXCOIL | 169.4404 | 170.0815 | 176.1879 | 162.0901 | 127.383 | 171.4682 | 118.4958 | 171.883 | 177.7943 | 137.1828 | 168.9133 | 165.4195 | 164.8379 | 157.8282 | 151.4138 | 154.0659
Heating (kW)
| HEATSYS1 BOILER | 425.5944 | 447.1792 | 496.3748 | 433.8105 | 409.9121 | 459.7038 | 384.0482 | 482.3936 | 453.6205 | 433.4836 | 466.3679 | 431.7628 | 467.5971 | 436.2481 | 457.4602 | 483.2661
HVAC Efficiency
Air Conditioning (COP)
| VAV_1_COOLC DXCOIL | 4.71 | 4.84 | 5.38 | 5.06 | 5.58 | 5.59 | 5.58 | 5.08 | 5.58 | 5.58 | 5.12 | 5.58 | 5.27 | 5.58 | 5.58 | 5.58
| VAV_2_COOLC DXCOIL | 4.73 | 4.93 | 5.42 | 5.07 | 5.58 | 5.54 | 5.58 | 5.08 | 4.86 | 5.54 | 5.13 | 4.86 | 5.27 | 4.86 | 5.54 | 4.86
| VAV_3_COOLC DXCOIL | 4.5 | 4.68 | 4.86 | 4.92 | 5.59 | 4.75 | 5.59 | 4.97 | 4.86 | 5.59 | 4.93 | 4.86 | 5.1 | 4.86 | 5.5 | 5.54
| Heating Efficiency (%) | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
HVAC Control - Economizer
| VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| VAV_1_FAN | 6.65 | 6.94 | 7.34 | 6.92 | 6.34 | 7.03 | 5.65 | 7.43 | 8.29 | 6.6 | 7.28 | 7.95 | 7.33 | 7.57 | 7.17 | 6.85
| VAV_2_FAN | 7.72 | 8.13 | 9.39 | 8.17 | 7.75 | 9.23 | 7.54 | 8.86 | 10.17 | 8.4 | 8.83 | 9.91 | 8.94 | 9.54 | 9.19 | 9.51
| VAV_3_FAN | 8.17 | 8.7 | 10.64 | 8.76 | 7.7 | 10.09 | 7.16 | 9.39 | 10.74 | 8.29 | 9.16 | 9.99 | 9.25 | 9.53 | 9.1 | 9.31
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.088875 | 0.12037 | 0.10286 | 0.099665 | 0.13174 | 0.10094 | 0.15056 | 0.077952 | 0.03732 | 0.077941 | 0.088142 | 0.037337 | 0.063001 | 0.079626 | 0.063267 | 0.10275
| Total Cost ($/m2) | 10.44 | 13.43 | 11.24 | 10.32 | 12.52 | 10.36 | 13.27 | 8.1 | 3.67 | 6.92 | 8.55 | 3.53 | 6.05 | 7.32 | 5.8 | 9.32
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011404 | 0.0080537 | 0.0081978 | 0.0095917 | 0.0086194 | 0.0076701 | 0.0085576 | 0.009691 | 0.0068932 | 0.0084161 | 0.0083429 | 0.0069199 | 0.0078622 | 0.008119 | 0.007862 | 0.0041242
| Total Cost ($/m2) | 0.16 | 0.75 | 0.73 | 1.23 | 0.46 | 0.71 | 1.18 | 1.96 | 0.96 | 1.69 | 2.12 | 1.32 | 2.55 | 2.3 | 2.97 | 2.51
Total Utility Costs
| Cost Intensity ($/m2) | 10.6 | 14.18 | 11.96 | 11.56 | 12.98 | 11.07 | 14.45 | 10.06 | 4.63 | 8.61 | 10.67 | 4.85 | 8.61 | 9.62 | 8.77 | 11.83
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 166227.7778 | 136855.5556 | 119952.7778 | 97891.6667 | 59872.2222 | 88591.6667 | 26516.6667 | 96450 | 66758.3333 | 25466.6667 | 62022.2222 | 49386.1111 | 55852.7778 | 37452.7778 | 33255.5556 | 26941.6667
| Interior Lighting | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667
| Exterior Lighting | 11933.3333 | 11911.1111 | 11908.3333 | 11927.7778 | 11925 | 11913.8889 | 11902.7778 | 11913.8889 | 11911.1111 | 11894.4444 | 11897.2222 | 11900 | 11908.3333 | 11891.6667 | 11888.8889 | 11819.4444
| Interior Equipment | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 29744.4444 | 29505.5556 | 34886.1111 | 28569.4444 | 24150 | 33197.2222 | 22875 | 31597.2222 | 34061.1111 | 27141.6667 | 31469.4444 | 31586.1111 | 32794.4444 | 30702.7778 | 33169.4444 | 34022.2222
| Pumps | 86.1111 | 244.4444 | 213.8889 | 313.8889 | 150 | 227.7778 | 333.3333 | 475 | 338.8889 | 450 | 622.2222 | 494.4444 | 886.1111 | 766.6667 | 1061.1111 | 1888.8889
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 585383.3333 | 555905.5556 | 544352.7778 | 516097.2222 | 473488.8889 | 511322.2222 | 439019.4444 | 517825 | 490461.1111 | 442341.6667 | 483402.7778 | 470755.5556 | 478830.5556 | 458202.7778 | 456763.8889 | 452061.1111
Gas (MJ)
| Heating | 42150 | 432530 | 411760 | 604070 | 229910 | 431980 | 651310 | 967620 | 654580 | 961770 | 1223800 | 909560 | 1575020 | 1365750 | 1833440 | 2979390
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 27750 | 31690 | 29420 | 35500 | 34770 | 32150 | 38020 | 38480 | 37920 | 40050 | 41110 | 40980 | 43380 | 43790 | 47120 | 51640
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 69900 | 464220 | 441170 | 639570 | 264680 | 464120 | 689340 | 1006100 | 692500 | 1001820 | 1264910 | 950540 | 1618390 | 1409550 | 1880560 | 3031040
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 2177280 | 2465480 | 2400840 | 2497520 | 1969240 | 2304880 | 2269800 | 2870270 | 2458160 | 2594250 | 3005160 | 2645260 | 3342190 | 3059080 | 3524910 | 4658450
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 120.1118 | 98.8882 | 86.6747 | 70.734 | 43.2621 | 64.014 | 19.1602 | 69.6922 | 48.2378 | 18.4015 | 44.8156 | 35.6851 | 40.3578 | 27.0624 | 24.0296 | 19.4673
| Interior Lighting (elec) | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091
| Exterior Lighting (elec) | 8.6227 | 8.6067 | 8.6046 | 8.6187 | 8.6167 | 8.6087 | 8.6006 | 8.6087 | 8.6067 | 8.5946 | 8.5966 | 8.5986 | 8.6046 | 8.5926 | 8.5906 | 8.5404
| Interior Equipment (elec) | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 21.4926 | 21.3199 | 25.2078 | 20.6435 | 17.4502 | 23.9874 | 16.5289 | 22.8313 | 24.6117 | 19.6119 | 22.739 | 22.8233 | 23.6964 | 22.185 | 23.9674 | 24.5836
| Pumps (elec) | 0.062222 | 0.17663 | 0.15455 | 0.22681 | 0.10839 | 0.16459 | 0.24086 | 0.34322 | 0.24487 | 0.32516 | 0.4496 | 0.35727 | 0.64028 | 0.55397 | 0.76673 | 1.3649
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 422.9827 | 401.6828 | 393.3351 | 372.9183 | 342.1307 | 369.468 | 317.224 | 374.1668 | 354.3944 | 319.6245 | 349.2942 | 340.1556 | 345.9904 | 331.0853 | 330.0456 | 326.6475
Gas (MJ/m2)
| Heating (gas) | 8.4601 | 86.8152 | 82.6464 | 121.2459 | 46.1464 | 86.7048 | 130.7277 | 194.2158 | 131.384 | 193.0416 | 245.635 | 182.5623 | 316.1301 | 274.1264 | 367.9988 | 598.0081
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 5.5698 | 6.3607 | 5.905 | 7.1254 | 6.9789 | 6.453 | 7.6312 | 7.7235 | 7.6111 | 8.0386 | 8.2514 | 8.2253 | 8.707 | 8.7893 | 9.4577 | 10.3649
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 14.03 | 93.1759 | 88.5494 | 128.3713 | 53.1252 | 93.1558 | 138.3608 | 201.9393 | 138.9951 | 201.0802 | 253.8863 | 190.7876 | 324.8351 | 282.9178 | 377.4565 | 608.375
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 437.0126 | 494.8587 | 481.8845 | 501.2896 | 395.2559 | 462.6239 | 455.5828 | 576.1061 | 493.3895 | 520.7048 | 603.1805 | 530.9432 | 670.8275 | 614.0031 | 707.5021 | 935.0205
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 148.1071 | 142.0889 | 126.8482 | 129.4992 | 124.6074 | 120.5975 | 111.8464 | 130.6963 | 120.893 | 115.4973 | 118.1794 | 119.8175 | 117.8478 | 119.2113 | 116.0452 | 120.2435
| Feb | 154.8841 | 136.765 | 128.9318 | 131.4365 | 124.1757 | 122.9771 | 120.9628 | 125.8541 | 125.0011 | 115.5226 | 118.1246 | 119.359 | 115.4856 | 119.15 | 117.4481 | 118.0298
| Mar | 155.8909 | 142.3969 | 139.6854 | 131.792 | 123.8872 | 126.7588 | 117.2505 | 134.2171 | 127.641 | 119.5662 | 125.0606 | 125.1074 | 118.3088 | 122.5304 | 117.7023 | 116.1505
| Apr | 162.8806 | 145.44 | 143.8575 | 138.0238 | 127.6126 | 140.5721 | 120.1186 | 135.5257 | 135.542 | 116.5301 | 131.6627 | 130.3048 | 124.2739 | 119.4802 | 117.6757 | 118.2094
| May | 168.5446 | 169.2561 | 168.9772 | 154.5853 | 140.2607 | 156.4816 | 124.2837 | 144.6497 | 146.555 | 130.2739 | 150.7699 | 140.8789 | 143.3705 | 129.4565 | 127.1511 | 123.1358
| Jun | 177.6938 | 172.6884 | 202.5783 | 164.2081 | 135.4858 | 189.5382 | 127.1395 | 170.7518 | 163.4689 | 135.4707 | 163.0577 | 150.0839 | 163.279 | 158.1727 | 144.4347 | 141.188
| Jul | 175.1267 | 182.6199 | 202.6326 | 180.4844 | 142.2194 | 185.7321 | 139.1163 | 176.6962 | 171.7518 | 144.5144 | 171.3741 | 163.2301 | 163.2627 | 156.7935 | 163.2698 | 141.6212
| Aug | 183.8159 | 180.7538 | 201.7891 | 165.5815 | 152.1735 | 179.7544 | 130.1349 | 176.6765 | 169.588 | 143.8199 | 166.4579 | 158.4118 | 160.116 | 149.2991 | 150.5723 | 136.6079
| Sep | 176.0049 | 165.7002 | 184.0515 | 158.7739 | 144.9036 | 171.8424 | 142.7274 | 153.3314 | 157.1552 | 137.2139 | 149.5879 | 143.5531 | 143.5152 | 140.529 | 145.5936 | 117.6607
| Oct | 167.2776 | 153.4892 | 148.9124 | 140.6713 | 133.9312 | 143.8158 | 127.9276 | 141.8551 | 138.3406 | 123.5591 | 139.3821 | 135.33 | 127.695 | 128.3523 | 120.5331 | 120.7348
| Nov | 155.4839 | 146.6268 | 136.343 | 131.8381 | 127.4148 | 124.9759 | 116.9621 | 136.7926 | 123.9928 | 120.0147 | 142.0807 | 125.3816 | 120.4851 | 118.4773 | 117.4261 | 121.1471
| Dec | 146.1079 | 140.0167 | 129.9406 | 133.7631 | 125.9445 | 124.5 | 111.5098 | 124.7317 | 121.0142 | 116.0383 | 117.66 | 119.6312 | 117.2058 | 119.1861 | 116.9848 | 117.5456
Time of Peak Electrical Demand
| Jan | 23-JAN-16:15 | 03-JAN-08:00 | 27-JAN-13:00 | 24-JAN-08:00 | 26-JAN-13:15 | 18-JAN-13:00 | 02-JAN-08:15 | 09-JAN-08:00 | 17-JAN-08:45 | 31-JAN-08:00 | 24-JAN-08:45 | 11-JAN-08:45 | 30-JAN-08:00 | 20-JAN-08:00 | 13-JAN-08:00 | 18-JAN-08:15
| Feb | 21-FEB-13:00 | 21-FEB-08:00 | 28-FEB-13:00 | 22-FEB-08:15 | 13-FEB-12:30 | 08-FEB-13:00 | 15-FEB-16:15 | 13-FEB-08:00 | 14-FEB-16:15 | 21-FEB-13:00 | 13-FEB-08:30 | 06-FEB-08:30 | 27-FEB-08:00 | 03-FEB-08:15 | 24-FEB-08:00 | 27-FEB-08:15
| Mar | 27-MAR-15:30 | 29-MAR-07:45 | 17-MAR-15:00 | 30-MAR-07:00 | 03-MAR-13:00 | 31-MAR-12:00 | 01-MAR-13:15 | 10-MAR-08:00 | 02-MAR-13:00 | 29-MAR-12:00 | 31-MAR-15:15 | 30-MAR-12:00 | 14-MAR-07:45 | 30-MAR-15:30 | 17-MAR-07:00 | 31-MAR-07:15
| Apr | 03-APR-15:15 | 24-APR-07:00 | 17-APR-15:45 | 20-APR-15:00 | 13-APR-12:00 | 21-APR-15:30 | 28-APR-12:15 | 04-APR-07:00 | 21-APR-15:30 | 18-APR-15:00 | 10-APR-07:00 | 25-APR-12:00 | 14-APR-15:00 | 06-APR-15:00 | 18-APR-07:15 | 28-APR-07:45
| May | 15-MAY-15:00 | 18-MAY-15:30 | 30-MAY-15:30 | 15-MAY-15:15 | 30-MAY-07:00 | 31-MAY-15:00 | 26-MAY-12:00 | 16-MAY-07:45 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-12:45 | 24-MAY-15:30 | 31-MAY-12:30 | 16-MAY-15:00 | 31-MAY-15:00 | 30-MAY-12:30
| Jun | 26-JUN-15:30 | 12-JUN-15:30 | 28-JUN-15:00 | 19-JUN-15:15 | 29-JUN-07:00 | 27-JUN-15:00 | 16-JUN-15:00 | 26-JUN-15:30 | 29-JUN-15:30 | 28-JUN-15:15 | 08-JUN-12:00 | 27-JUN-15:15 | 30-JUN-15:15 | 26-JUN-15:15 | 14-JUN-11:45 | 21-JUN-15:15
| Jul | 05-JUL-07:00 | 05-JUL-15:00 | 11-JUL-15:00 | 03-JUL-15:45 | 11-JUL-07:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-15:30 | 03-JUL-15:30 | 24-JUL-15:15 | 03-JUL-15:15 | 17-JUL-15:15 | 18-JUL-07:00 | 21-JUL-15:45 | 07-JUL-07:00 | 11-JUL-15:00
| Aug | 21-AUG-15:15 | 28-AUG-15:30 | 01-AUG-15:00 | 14-AUG-15:30 | 08-AUG-15:00 | 04-AUG-15:15 | 15-AUG-12:15 | 04-AUG-15:15 | 01-AUG-15:15 | 07-AUG-15:15 | 04-AUG-15:30 | 30-AUG-12:00 | 28-AUG-15:30 | 08-AUG-15:45 | 14-AUG-07:00 | 15-AUG-12:00
| Sep | 11-SEP-15:15 | 15-SEP-15:15 | 11-SEP-15:45 | 05-SEP-15:00 | 25-SEP-15:15 | 01-SEP-15:15 | 28-SEP-15:30 | 08-SEP-15:30 | 05-SEP-12:00 | 01-SEP-15:45 | 07-SEP-12:00 | 01-SEP-15:30 | 14-SEP-15:15 | 12-SEP-12:45 | 07-SEP-15:15 | 25-SEP-07:00
| Oct | 10-OCT-15:30 | 30-OCT-08:00 | 02-OCT-15:15 | 02-OCT-12:00 | 19-OCT-12:00 | 06-OCT-12:00 | 31-OCT-13:15 | 03-OCT-07:00 | 11-OCT-15:00 | 17-OCT-12:00 | 31-OCT-08:00 | 05-OCT-15:15 | 06-OCT-15:15 | 06-OCT-15:30 | 27-OCT-12:45 | 05-OCT-07:15
| Nov | 01-NOV-08:00 | 27-NOV-08:00 | 13-NOV-13:00 | 22-NOV-08:00 | 09-NOV-13:15 | 10-NOV-13:30 | 16-NOV-16:00 | 03-NOV-13:00 | 01-NOV-13:00 | 03-NOV-08:00 | 02-NOV-08:00 | 10-NOV-13:00 | 02-NOV-13:00 | 13-NOV-08:00 | 17-NOV-08:30 | 14-NOV-08:45
| Dec | 19-DEC-13:00 | 20-DEC-08:00 | 13-DEC-13:15 | 26-DEC-08:00 | 19-DEC-13:15 | 05-DEC-13:00 | 26-DEC-08:15 | 08-DEC-08:00 | 04-DEC-08:30 | 29-DEC-08:45 | 11-DEC-08:45 | 06-DEC-08:30 | 26-DEC-08:00 | 21-DEC-08:45 | 26-DEC-08:00 | 19-DEC-08:15
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77
| Total Building | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77
Emissions
| Carbon Equivalent (kg) | 161801.7508 | 193799.6728 | 172281.9618 | 170509.746 | 60107.5487 | 180825.359 | 63736.8054 | 157880.6978 | 212840.2534 | 50283.1732 | 280534.9434 | 209443.6267 | 193084.6807 | 192862.7508 | 190258.6109 | 181861.9248
| CO2 (kg) | 375383.7067 | 489479.1789 | 409431.2712 | 394134.813 | 161523.9998 | 432644.8523 | 172893.3211 | 365785.0177 | 502920.2257 | 128727.1952 | 660543.7561 | 497607.3189 | 462173.8179 | 462892.1852 | 458418.5334 | 476565.4618
| NOX (kg) | 658.9124 | 633.5431 | 674.0242 | 726.9815 | 138.9465 | 691.8046 | 149.8287 | 674.1363 | 851.8459 | 170.3539 | 1142.611 | 831.1417 | 766.0673 | 757.991 | 746.6903 | 542.5737
| SO2 (kg) | 2505.6946 | 2651.7959 | 2189.0652 | 1811.669 | 1377.868 | 2812.8017 | 1277.6751 | 1890.5384 | 2141.9341 | 342.1642 | 3258.0784 | 2055.9519 | 1130.5525 | 1223.8367 | 1078.5397 | 2301.9815
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0114 | 0.0075 | 0.006 | 0.0067 | 0.0006 | 0.0053 | 0.0006 | 0.0077 | 0.0084 | 0.0014 | 0.01 | 0.0081 | 0.0084 | 0.0086 | 0.0081 | 0.0081
| Water for Electricity (m3) | 310.1116 | 904.5242 | 16169.6 | 3222.3 | 8313.41 | 14027.6 | 7708.18 | 117.5658 | 2227.09 | 4519.33 | 749.9685 | 2137.61 | 742.8783 | 29024.5 | 708.6418 | 461.8613

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2177.28 | 437.01 | 437.01
Net Site Energy | 2177.28 | 437.01 | 437.01
Total Source Energy | 7066.51 | 1418.36 | 1418.36
Net Source Energy | 7066.51 | 1418.36 | 1418.36
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 42.15 | 0 | 0 | 0 | 0
Cooling | 598.42 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.96 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 107.08 | 0 | 0 | 0 | 0 | 0
Pumps | 0.31 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 27.75 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2107.38 | 69.9 | 0 | 0 | 0 | 174.77
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 40.7174
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.17 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 10.76 | 18.59 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 65.28 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 65.28 | 65.28 | 6.49 | 0.441 | 0.44 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 65.28 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 65.28 | 65.28 | 6.49 | 0.441 | 0.44 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 65.28 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 65.28 | 65.28 | 6.49 | 0.441 | 0.44 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 6.49 | 0.307 | 0.307
North Total or Average |  |  | 195.85 | 6.49 | 0.441 | 0.44
Non-North Total or Average |  |  | 456.98 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 425594.37 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 130040 | 96546.58 | 33493.42 | 0.74 | 4.71
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 150301.62 | 111744.12 | 38557.5 | 0.74 | 4.73
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 169440.4 | 122753.23 | 46687.17 | 0.72 | 4.5
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Gas | 16770.45 | 0.99
VAV_2_HEATC | Coil:Heating:Gas | 2009.64 | 0.99
VAV_3_HEATC | Coil:Heating:Gas | 1303.33 | 0.99
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 6.65 | 17422 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 7.72 | 20203.02 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 8.17 | 21390.45 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2503.91 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 29558.4123 | 51.2717 | 192.4838 | 0 | 0.0009 | 23821.8656 | 12679.2185
February | 26882.381 | 46.9252 | 177.3823 | 0 | 0.0008 | 21953.1212 | 11560.9181
March | 31273.663 | 54.7418 | 207.5482 | 0 | 0.0009 | 25686.615 | 13464.5655
April | 29400.0394 | 51.7268 | 197.1964 | 0 | 0.0009 | 24405.6553 | 12684.4079
May | 33008.8865 | 58.1071 | 221.645 | 0 | 0.001 | 27431.5168 | 14244.5068
June | 33817.8139 | 59.5448 | 227.1851 | 0 | 0.001 | 28117.1931 | 14594.9681
July | 33533.8897 | 59.0476 | 225.2987 | 0 | 0.001 | 27883.7202 | 14472.6994
August | 36050.6109 | 63.4794 | 242.2101 | 0 | 0.0011 | 29976.7419 | 15558.9122
September | 32297.4809 | 56.8639 | 216.9402 | 0 | 0.001 | 26849.2432 | 13938.4278
October | 31619.1893 | 55.6419 | 212.1653 | 0 | 0.001 | 26258.2593 | 13642.9148
November | 29476.491 | 51.8463 | 197.5915 | 0 | 0.0009 | 24454.5437 | 12715.8941
December | 28464.8488 | 49.716 | 188.048 | 0 | 0.0009 | 23273.1538 | 12244.3176
Annual Sum or Average | 375383.7067 | 658.9124 | 2505.6946 | 0 | 0.0114 | 310111.6291 | 161801.7508
Minimum of Months | 26882.381 | 46.9252 | 177.3823 | 0 | 0.0008 | 21953.1212 | 11560.9181
Maximum of Months | 36050.6109 | 63.4794 | 242.2101 | 0 | 0.0011 | 29976.7419 | 15558.9122
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 161883000000 | 148107.109 | 23-JAN-16:15 | 48247.488 | 50956.165 | 7552.763 | 0 | 41342.243 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 149184000000 | 154884.102 | 21-FEB-13:00 | 48247.488 | 51598.363 | 8918.379 | 0 | 46111.423 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 174555000000 | 155890.85 | 27-MAR-15:30 | 48247.488 | 50956.165 | 9443.495 | 0 | 47235.252 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 165850000000 | 162880.616 | 03-APR-15:15 | 48247.488 | 50956.165 | 11362.378 | 0 | 52306.135 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 186412000000 | 168544.554 | 15-MAY-15:00 | 48247.488 | 50956.165 | 11558.562 | 0 | 57773.889 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 191072000000 | 177693.77 | 26-JUN-15:30 | 48247.488 | 50956.165 | 12277.954 | 0 | 66203.714 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 189485000000 | 175126.718 | 05-JUL-07:00 | 48247.488 | 58341.44 | 11032.278 | 0 | 57497.063 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 203709000000 | 183815.925 | 21-AUG-15:15 | 48247.488 | 50956.165 | 14420.756 | 0 | 70183.066 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 182456000000 | 176004.89 | 11-SEP-15:15 | 48247.488 | 50956.165 | 13713.468 | 0 | 63079.319 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 178439000000 | 167277.627 | 10-OCT-15:30 | 48247.488 | 50956.165 | 13292.439 | 0 | 54773.085 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 166182000000 | 155483.944 | 01-NOV-08:00 | 48247.488 | 58341.44 | 6473.347 | 0 | 42413.22 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 158154000000 | 146107.921 | 19-DEC-13:00 | 48247.488 | 51598.363 | 7171.139 | 0 | 39082.482 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2107380000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 149184000000 | 146107.921 |  | 48247.488 | 50956.165 | 6473.347 | 0 | 39082.482 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 203709000000 | 183815.925 |  | 48247.488 | 58341.44 | 14420.756 | 0 | 70183.066 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 52025.66 | 797.17 | 0 | 52822.83
Cost per Total Building Area ($/m2) | 10.44 | 0.16 | 0 | 10.6
Cost per Net Conditioned Building Area ($/m2) | 10.44 | 0.16 | 0 | 10.6

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2465.48 | 494.86 | 494.86
Net Site Energy | 2465.48 | 494.86 | 494.86
Total Source Energy | 506.93 | 101.75 | 101.75
Net Source Energy | 506.93 | 101.75 | 101.75
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 432.53 | 0 | 0 | 0 | 0
Cooling | 492.68 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.88 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 106.22 | 0 | 0 | 0 | 0 | 0
Pumps | 0.88 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 31.69 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2001.26 | 464.22 | 0 | 0 | 0 | 174.77
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 40.7174
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.17 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 10.76 | 18.59 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 65.28 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 65.28 | 65.28 | 6.49 | 0.61 | 0.61 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 65.28 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 65.28 | 65.28 | 6.49 | 0.61 | 0.61 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 65.28 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 65.28 | 65.28 | 6.49 | 0.61 | 0.61 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 6.49 | 0.358 | 0.358
North Total or Average |  |  | 195.85 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 456.98 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 447179.24 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 131429.52 | 98890.58 | 32538.94 | 0.75 | 4.84
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 150844.41 | 114480.81 | 36363.6 | 0.76 | 4.93
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 170081.46 | 126270.41 | 43811.06 | 0.74 | 4.68
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Gas | 14411.05 | 0.99
VAV_2_HEATC | Coil:Heating:Gas | 12566.49 | 0.99
VAV_3_HEATC | Coil:Heating:Gas | 11678.98 | 0.99
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 6.94 | 18172.72 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 8.13 | 21279.66 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 8.7 | 22637.61 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2630.91 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 40639.3999 | 50.9834 | 197.5197 | 0 | 0.0006 | 67366.3735 | 15881.9357
February | 36328.9557 | 45.5432 | 176.113 | 0 | 0.0005 | 60065.1961 | 14193.2049
March | 40680.2599 | 52.3513 | 216.1585 | 0 | 0.0006 | 73730.0188 | 16067.6169
April | 37129.3906 | 48.4521 | 206.6809 | 0 | 0.0006 | 70500.3769 | 14751.5409
May | 41733.0718 | 54.7583 | 236.4888 | 0 | 0.0007 | 80669.3962 | 16619.0718
June | 44172.5542 | 58.0098 | 251.022 | 0 | 0.0007 | 85627.091 | 17597.0591
July | 44598.8865 | 58.5738 | 253.5023 | 0 | 0.0007 | 86473.1739 | 17767.4271
August | 47046.1199 | 61.7832 | 267.3468 | 0 | 0.0008 | 91195.686 | 18741.7576
September | 40246.0728 | 52.8419 | 228.548 | 0 | 0.0006 | 77960.8443 | 16031.3837
October | 39261.6151 | 51.352 | 220.1938 | 0 | 0.0006 | 75110.2557 | 15613.8051
November | 37578.1091 | 48.6364 | 203.5581 | 0 | 0.0006 | 69433.4025 | 14878.0887
December | 40064.7433 | 50.258 | 194.6639 | 0 | 0.0006 | 66392.3564 | 15656.7814
Annual Sum or Average | 489479.1789 | 633.5431 | 2651.7959 | 0 | 0.0075 | 904524.1715 | 193799.6728
Minimum of Months | 36328.9557 | 45.5432 | 176.113 | 0 | 0.0005 | 60065.1961 | 14193.2049
Maximum of Months | 47046.1199 | 61.7832 | 267.3468 | 0 | 0.0008 | 91195.686 | 18741.7576
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 149048000000 | 142088.943 | 03-JAN-08:00 | 48247.488 | 58341.44 | 5345.389 | 0 | 30124.916 | 0 | 29.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 132894000000 | 136765.033 | 21-FEB-08:00 | 48247.488 | 58341.44 | 5345.389 | 0 | 24812.521 | 0 | 18.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 163128000000 | 142396.878 | 29-MAR-07:45 | 48247.488 | 58341.44 | 5690.548 | 0 | 30108.012 | 0 | 9.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 155982000000 | 145440 | 24-APR-07:00 | 48247.488 | 58341.44 | 5812.7 | 0 | 33029.922 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 178481000000 | 169256.144 | 18-MAY-15:30 | 48247.488 | 50956.165 | 10946.72 | 0 | 59097.322 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 189450000000 | 172688.449 | 12-JUN-15:30 | 48247.488 | 50956.165 | 12853.432 | 0 | 60622.915 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 191322000000 | 182619.878 | 05-JUL-15:00 | 48247.488 | 50956.165 | 14399.806 | 0 | 69007.969 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 201771000000 | 180753.839 | 28-AUG-15:30 | 48247.488 | 50956.165 | 14665.713 | 0 | 66876.022 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 172489000000 | 165700.236 | 15-SEP-15:15 | 48247.488 | 50956.165 | 8732.95 | 0 | 57755.184 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 166182000000 | 153489.179 | 30-OCT-08:00 | 48247.488 | 58341.44 | 6039.053 | 0 | 40852.748 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 153622000000 | 146626.765 | 27-NOV-08:00 | 48247.488 | 58341.44 | 5674.567 | 0 | 34354.82 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 146893000000 | 140016.683 | 20-DEC-08:00 | 48247.488 | 58341.44 | 5345.389 | 0 | 28065.417 | 0 | 16.948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2001260000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 132894000000 | 136765.033 |  | 48247.488 | 50956.165 | 5345.389 | 0 | 24812.521 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 201771000000 | 182619.878 |  | 48247.488 | 58341.44 | 14665.713 | 0 | 69007.969 | 0 | 29.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 66912.66 | 3738.7 | 0 | 70651.36
Cost per Total Building Area ($/m2) | 13.43 | 0.75 | 0 | 14.18
Cost per Net Conditioned Building Area ($/m2) | 13.43 | 0.75 | 0 | 14.18

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2400.84 | 481.88 | 481.88
Net Site Energy | 2400.84 | 481.88 | 481.88
Total Source Energy | 6680.18 | 1340.81 | 1340.81
Net Source Energy | 6680.18 | 1340.81 | 1340.81
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 411.76 | 0 | 0 | 0 | 0
Cooling | 431.83 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.87 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 125.59 | 0 | 0 | 0 | 0 | 0
Pumps | 0.77 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 29.42 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1959.67 | 441.17 | 0 | 0 | 0 | 174.77
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 40.7174
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.17 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 10.76 | 18.59 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 65.28 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 65.28 | 65.28 | 6.49 | 0.61 | 0.61 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 65.28 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 65.28 | 65.28 | 6.49 | 0.61 | 0.61 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 65.28 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 65.28 | 65.28 | 6.49 | 0.61 | 0.61 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 43.52 | 6.49 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 6.49 | 0.358 | 0.358
North Total or Average |  |  | 195.85 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 456.98 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 496374.84 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 125305.08 | 98660.46 | 26644.62 | 0.79 | 5.38
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 158362.88 | 125375.68 | 32987.19 | 0.79 | 5.42
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 176187.92 | 140713.41 | 35474.51 | 0.8 | 4.86
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Gas | 7796.99 | 0.99
VAV_2_HEATC | Coil:Heating:Gas | 4726.21 | 0.99
VAV_3_HEATC | Coil:Heating:Gas | 2845.6 | 0.99
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 7.34 | 19209.24 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 9.39 | 24413.9 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 10.64 | 24444.05 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2920.34 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 32208.9855 | 50.0184 | 150.4668 | 0 | 0.0004 | 1111280 | 13249.0923
February | 28865.7804 | 45.2799 | 138.1277 | 0 | 0.0004 | 1020170 | 11919.7083
March | 32867.5449 | 53.847 | 173.8414 | 0 | 0.0005 | 1284070 | 13803.7291
April | 30130.4669 | 50.3183 | 166.2764 | 0 | 0.0005 | 1228250 | 12750.8271
May | 33999.4016 | 57.2738 | 191.2036 | 0 | 0.0005 | 1412400 | 14438.1021
June | 39133.1847 | 66.0483 | 220.9883 | 0 | 0.0006 | 1632420 | 16630.9746
July | 40103.9052 | 67.704 | 226.5956 | 0 | 0.0006 | 1673850 | 17045.2696
August | 41455.2853 | 69.9823 | 234.2087 | 0 | 0.0006 | 1730080 | 17619.3299
September | 35593.5078 | 60.0573 | 200.8783 | 0 | 0.0005 | 1483870 | 15124.9746
October | 32091.55 | 53.7165 | 177.9898 | 0 | 0.0005 | 1314780 | 13593.1892
November | 30500.3506 | 49.7964 | 160.0735 | 0 | 0.0004 | 1182370 | 12792.1156
December | 32481.3083 | 49.9818 | 148.4151 | 0 | 0.0004 | 1096100 | 13314.6494
Annual Sum or Average | 409431.2712 | 674.0242 | 2189.0652 | 0 | 0.006 | 16169600 | 172281.9618
Minimum of Months | 28865.7804 | 45.2799 | 138.1277 | 0 | 0.0004 | 1020170 | 11919.7083
Maximum of Months | 41455.2853 | 69.9823 | 234.2087 | 0 | 0.0006 | 1730080 | 17619.3299
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 134680000000 | 126848.164 | 27-JAN-13:00 | 48247.488 | 51598.363 | 5935.861 | 0 | 21058.003 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 123639000000 | 128931.847 | 28-FEB-13:00 | 48247.488 | 51598.363 | 6113.773 | 0 | 22963.773 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 155622000000 | 139685.352 | 17-MAR-15:00 | 48247.488 | 50956.165 | 7393.888 | 0 | 33079.361 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 148856000000 | 143857.546 | 17-APR-15:45 | 48247.488 | 50956.165 | 8859.282 | 0 | 35786.161 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 171175000000 | 168977.195 | 30-MAY-15:30 | 48247.488 | 50956.165 | 14006.234 | 0 | 55758.858 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 197840000000 | 202578.343 | 28-JUN-15:00 | 48247.488 | 50956.165 | 19061.917 | 0 | 84304.324 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 202860000000 | 202632.587 | 11-JUL-15:00 | 48247.488 | 50956.165 | 18307.517 | 0 | 85112.967 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 209676000000 | 201789.079 | 01-AUG-15:00 | 48247.488 | 50956.165 | 18875.431 | 0 | 83701.545 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 179837000000 | 184051.467 | 11-SEP-15:45 | 48247.488 | 50956.165 | 16859.035 | 0 | 67980.329 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 159343000000 | 148912.442 | 02-OCT-15:15 | 48247.488 | 50956.165 | 9717.953 | 0 | 39982.386 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 143296000000 | 136343.049 | 13-NOV-13:00 | 48247.488 | 51598.363 | 7075.653 | 0 | 29413.095 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 132840000000 | 129940.615 | 13-DEC-13:15 | 48247.488 | 51598.363 | 5955.267 | 0 | 24122.383 | 0 | 17.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1959670000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 123639000000 | 126848.164 |  | 48247.488 | 50956.165 | 5935.861 | 0 | 21058.003 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 209676000000 | 202632.587 |  | 48247.488 | 51598.363 | 19061.917 | 0 | 85112.967 | 0 | 17.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 55992.39 | 3616.62 | 0 | 59609.01
Cost per Total Building Area ($/m2) | 11.24 | 0.73 | 0 | 11.96
Cost per Net Conditioned Building Area ($/m2) | 11.24 | 0.73 | 0 | 11.96

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2497.52 | 501.29 | 501.29
Net Site Energy | 2497.52 | 501.29 | 501.29
Total Source Energy | 6948.54 | 1394.68 | 1394.68
Net Source Energy | 6948.54 | 1394.68 | 1394.68
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 604.07 | 0 | 0 | 0 | 0
Cooling | 352.41 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.94 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 102.85 | 0 | 0 | 0 | 0 | 0
Pumps | 1.13 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 35.5 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1857.95 | 639.57 | 0 | 0 | 0 | 174.77
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 40.7174
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.17 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 10.76 | 18.59 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 65.28 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.402 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 65.28 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.402 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 65.28 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.402 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.18 | 0.304 | 0.409
North Total or Average |  |  | 195.85 | 3.18 | 0.402 | 0.622
Non-North Total or Average |  |  | 456.98 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 433810.49 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 125201.31 | 96063.6 | 29137.71 | 0.77 | 5.06
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 147367.58 | 113222.85 | 34144.73 | 0.77 | 5.07
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 162090.12 | 123193.99 | 38896.13 | 0.76 | 4.92
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Gas | 19074.25 | 0.99
VAV_2_HEATC | Coil:Heating:Gas | 17196.09 | 0.99
VAV_3_HEATC | Coil:Heating:Gas | 16307.81 | 0.99
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 6.92 | 18111.36 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 8.17 | 21383.14 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 8.76 | 22794.83 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2552.25 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 35933.4801 | 60.3538 | 136.1237 | 0 | 0.0005 | 242056.5201 | 14998.2298
February | 30521.3905 | 52.7175 | 122.7484 | 0 | 0.0005 | 218289.6399 | 12873.5511
March | 33462.477 | 61.0096 | 150.3227 | 0 | 0.0006 | 267362.2089 | 14410.7142
April | 30201.2136 | 56.6381 | 143.3908 | 0 | 0.0005 | 255049.0105 | 13151.6571
May | 32299.7125 | 61.9731 | 160.2149 | 0 | 0.0006 | 284987.1929 | 14194.7386
June | 33799.4943 | 65.1177 | 168.9627 | 0 | 0.0006 | 300550.0938 | 14878.4992
July | 33910.8803 | 65.3392 | 169.5537 | 0 | 0.0006 | 301601.389 | 14928.1748
August | 36135.3578 | 69.6291 | 180.6946 | 0 | 0.0007 | 321418.7594 | 15907.7786
September | 31913.5872 | 61.4302 | 159.2699 | 0 | 0.0006 | 283308.0638 | 14043.3283
October | 30955.8055 | 58.4038 | 148.6919 | 0 | 0.0005 | 264481.3042 | 13512.6308
November | 31335.4511 | 56.5381 | 137.8585 | 0 | 0.0005 | 245187.6794 | 13439.9007
December | 33665.9629 | 57.8311 | 133.8371 | 0 | 0.0005 | 238005.5875 | 14170.5427
Annual Sum or Average | 394134.813 | 726.9815 | 1811.669 | 0 | 0.0067 | 3222300 | 170509.746
Minimum of Months | 30201.2136 | 52.7175 | 122.7484 | 0 | 0.0005 | 218289.6399 | 12873.5511
Maximum of Months | 36135.3578 | 69.6291 | 180.6946 | 0 | 0.0007 | 321418.7594 | 15907.7786
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 139567000000 | 129499.216 | 24-JAN-08:00 | 48247.488 | 58341.44 | 5362.552 | 0 | 17482.561 | 0 | 65.174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 125864000000 | 131436.523 | 22-FEB-08:15 | 48247.488 | 58341.44 | 5362.552 | 0 | 19431.103 | 0 | 53.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 154159000000 | 131791.991 | 30-MAR-07:00 | 48247.488 | 58341.44 | 5362.552 | 0 | 19810.403 | 0 | 30.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 147059000000 | 138023.828 | 20-APR-15:00 | 48247.488 | 50956.165 | 6637.656 | 0 | 32174.07 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 164321000000 | 154585.286 | 15-MAY-15:15 | 48247.488 | 50956.165 | 10376.709 | 0 | 44996.474 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 173294000000 | 164208.071 | 19-JUN-15:15 | 48247.488 | 50956.165 | 12095.896 | 0 | 52900.072 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 173901000000 | 180484.402 | 03-JUL-15:45 | 48247.488 | 50956.165 | 15490.991 | 0 | 65781.308 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 185327000000 | 165581.531 | 14-AUG-15:30 | 48247.488 | 50956.165 | 12069.061 | 0 | 54300.368 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 163353000000 | 158773.914 | 05-SEP-15:00 | 48247.488 | 50956.165 | 11463.379 | 0 | 48098.432 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 152497000000 | 140671.325 | 02-OCT-12:00 | 48247.488 | 51598.363 | 7070.276 | 0 | 33746.748 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 141373000000 | 131838.076 | 22-NOV-08:00 | 48247.488 | 58341.44 | 5362.552 | 0 | 19844.861 | 0 | 41.734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 137232000000 | 133763.077 | 26-DEC-08:00 | 48247.488 | 58341.44 | 5362.552 | 0 | 21707.902 | 0 | 103.695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1857950000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 125864000000 | 129499.216 |  | 48247.488 | 50956.165 | 5362.552 | 0 | 17482.561 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 185327000000 | 180484.402 |  | 48247.488 | 58341.44 | 15490.991 | 0 | 65781.308 | 0 | 103.695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 51436.64 | 6134.54 | 0 | 57571.18
Cost per Total Building Area ($/m2) | 10.32 | 1.23 | 0 | 11.56
Cost per Net Conditioned Building Area ($/m2) | 10.32 | 1.23 | 0 | 11.56

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1969.24 | 395.26 | 395.26
Net Site Energy | 1969.24 | 395.26 | 395.26
Total Source Energy | 5564.64 | 1116.91 | 1116.91
Net Source Energy | 5564.64 | 1116.91 | 1116.91
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 229.91 | 0 | 0 | 0 | 0
Cooling | 215.54 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.93 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 86.94 | 0 | 0 | 0 | 0 | 0
Pumps | 0.54 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 34.77 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1704.56 | 264.68 | 0 | 0 | 0 | 174.77
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 40.7174
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.17 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 10.76 | 18.59 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 65.28 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.402 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 65.28 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.402 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 65.28 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.402 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.18 | 0.304 | 0.409
North Total or Average |  |  | 195.85 | 3.18 | 0.402 | 0.622
Non-North Total or Average |  |  | 456.98 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 409912.13 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 104988.28 | 83849.44 | 21138.84 | 0.8 | 5.58
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 128303.01 | 102469.88 | 25833.14 | 0.8 | 5.58
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 127382.99 | 101735.09 | 25647.89 | 0.8 | 5.59
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Gas | 5647.88 | 0.99
VAV_2_HEATC | Coil:Heating:Gas | 3457.74 | 0.99
VAV_3_HEATC | Coil:Heating:Gas | 3546.22 | 0.99
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 6.34 | 16604.73 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 7.75 | 20292.14 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 7.7 | 20146.63 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2411.65 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 14211.0078 | 12.3052 | 106.8111 | 0 | 0.0001 | 644395.6297 | 5244.3301
February | 12396.5532 | 10.7165 | 96.3193 | 0 | 0 | 581111.1948 | 4584.3342
March | 14240.1275 | 12.2859 | 114.9888 | 0 | 0.0001 | 693765.0336 | 5279.3584
April | 12633.6543 | 10.8703 | 107.3191 | 0 | 0.0001 | 647511.7578 | 4699.9554
May | 13455.1294 | 11.5535 | 118.5126 | 0 | 0.0001 | 715063.2821 | 5018.4202
June | 13321.9829 | 11.4225 | 120.3307 | 0 | 0.0001 | 726043.4395 | 4977.8849
July | 13227.7691 | 11.3293 | 121.6934 | 0 | 0.0001 | 734273.5192 | 4949.435
August | 14760.0856 | 12.6417 | 135.7942 | 0 | 0.0001 | 819354.4433 | 5522.7931
September | 13142.8472 | 11.26 | 120.3103 | 0 | 0.0001 | 725925.6896 | 4915.8234
October | 13235.0956 | 11.353 | 118.6462 | 0 | 0.0001 | 715876.7519 | 4942.6738
November | 13157.1644 | 11.327 | 110.6444 | 0 | 0.0001 | 667570.7429 | 4891.2884
December | 13742.5827 | 11.8817 | 106.4979 | 0 | 0.0001 | 642519.3139 | 5081.2518
Annual Sum or Average | 161523.9998 | 138.9465 | 1377.868 | 0 | 0.0006 | 8313410 | 60107.5487
Minimum of Months | 12396.5532 | 10.7165 | 96.3193 | 0 | 0 | 581111.1948 | 4584.3342
Maximum of Months | 14760.0856 | 12.6417 | 135.7942 | 0 | 0.0001 | 819354.4433 | 5522.7931
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 132125000000 | 124607.37 | 26-JAN-13:15 | 48247.488 | 51598.363 | 5379.643 | 0 | 19373.426 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 119150000000 | 124175.729 | 13-FEB-12:30 | 48247.488 | 50788.728 | 5548.304 | 0 | 19582.759 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 142248000000 | 123887.159 | 03-MAR-13:00 | 48247.488 | 51598.363 | 5323.778 | 0 | 18709.081 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 132764000000 | 127612.593 | 13-APR-12:00 | 48247.488 | 51598.363 | 5561.632 | 0 | 22196.66 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 146615000000 | 140260.661 | 30-MAY-07:00 | 48247.488 | 58341.44 | 5580.784 | 0 | 28082.499 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 148866000000 | 135485.848 | 29-JUN-07:00 | 48247.488 | 58341.44 | 5230.425 | 0 | 23658.046 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 150554000000 | 142219.374 | 11-JUL-07:00 | 48247.488 | 58341.44 | 6084.117 | 0 | 29537.879 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 167998000000 | 152173.541 | 08-AUG-15:00 | 48247.488 | 50956.165 | 7509.932 | 0 | 45451.506 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 148842000000 | 144903.644 | 25-SEP-15:15 | 48247.488 | 50956.165 | 10208.822 | 0 | 35482.719 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 146782000000 | 133931.2 | 19-OCT-12:00 | 48247.488 | 51598.363 | 6150.187 | 0 | 27926.712 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 136877000000 | 127414.828 | 09-NOV-13:15 | 48247.488 | 51598.363 | 5824.34 | 0 | 21736.187 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 131741000000 | 125944.534 | 19-DEC-13:15 | 48247.488 | 51598.363 | 5797.792 | 0 | 20292.442 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1704560000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 119150000000 | 123887.159 |  | 48247.488 | 50788.728 | 5230.425 | 0 | 18709.081 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 167998000000 | 152173.541 |  | 48247.488 | 58341.44 | 10208.822 | 0 | 45451.506 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 62378.77 | 2281.39 | 0 | 64660.16
Cost per Total Building Area ($/m2) | 12.52 | 0.46 | 0 | 12.98
Cost per Net Conditioned Building Area ($/m2) | 12.52 | 0.46 | 0 | 12.98

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2304.88 | 462.62 | 462.62
Net Site Energy | 2304.88 | 462.62 | 462.62
Total Source Energy | 7091.21 | 1423.31 | 1423.31
Net Source Energy | 7091.21 | 1423.31 | 1423.31
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 431.98 | 0 | 0 | 0 | 0
Cooling | 318.93 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.89 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 119.51 | 0 | 0 | 0 | 0 | 0
Pumps | 0.82 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 32.15 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1840.76 | 464.12 | 0 | 0 | 0 | 174.77
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 40.7174
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.17 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 10.76 | 18.59 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 65.28 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.402 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 65.28 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.402 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 65.28 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.402 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 43.52 | 3.18 | 0.262 | 0.318 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.18 | 0.304 | 0.409
North Total or Average |  |  | 195.85 | 3.18 | 0.402 | 0.622
Non-North Total or Average |  |  | 456.98 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 459703.82 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 116353.34 | 92926.21 | 23427.13 | 0.8 | 5.59
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 152778.56 | 122017.4 | 30761.16 | 0.8 | 5.54
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 171468.22 | 135332.48 | 36135.74 | 0.79 | 4.75
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Gas | 12538.41 | 0.99
VAV_2_HEATC | Coil:Heating:Gas | 9366.27 | 0.99
VAV_3_HEATC | Coil:Heating:Gas | 8126.59 | 0.99
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 7.03 | 18402.2 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 9.23 | 24007.25 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 10.09 | 23181.13 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2704.59 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 35289.3635 | 53.0411 | 197.5951 | 0 | 0.0004 | 985291.8832 | 14397.2692
February | 29962.0766 | 46.6604 | 183.053 | 0 | 0.0003 | 912848.649 | 12392.8978
March | 34802.7633 | 54.5974 | 216.3727 | 0 | 0.0004 | 1079020 | 14436.5195
April | 32271.2355 | 52.3741 | 217.0646 | 0 | 0.0004 | 1082540 | 13568.1083
May | 35981.0762 | 58.7806 | 245.643 | 0 | 0.0005 | 1225080 | 15167.958
June | 40987.2501 | 67.1246 | 281.3773 | 0 | 0.0005 | 1403300 | 17295.549
July | 42093.266 | 68.9507 | 289.109 | 0 | 0.0005 | 1441860 | 17763.7948
August | 44133.5032 | 72.2892 | 303.0885 | 0 | 0.0006 | 1511580 | 18624.4263
September | 36935.5858 | 60.475 | 253.4285 | 0 | 0.0005 | 1263910 | 15584.3692
October | 34128.7117 | 55.4407 | 230.048 | 0 | 0.0004 | 1147290 | 14354.4781
November | 32236.3322 | 50.6809 | 201.4473 | 0 | 0.0004 | 1004600 | 13383.3324
December | 33823.6882 | 51.3899 | 194.5747 | 0 | 0.0004 | 970254.4369 | 13856.6566
Annual Sum or Average | 432644.8523 | 691.8046 | 2812.8017 | 0 | 0.0053 | 14027600 | 180825.359
Minimum of Months | 29962.0766 | 46.6604 | 183.053 | 0 | 0.0003 | 912848.649 | 12392.8978
Maximum of Months | 44133.5032 | 72.2892 | 303.0885 | 0 | 0.0006 | 1511580 | 18624.4263
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 129294000000 | 120597.488 | 18-JAN-13:00 | 48247.488 | 51598.363 | 5729.223 | 0 | 14998.375 | 0 | 24.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 119788000000 | 122977.079 | 08-FEB-13:00 | 48247.488 | 51598.363 | 5903.902 | 0 | 17215.949 | 0 | 11.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 141594000000 | 126758.83 | 31-MAR-12:00 | 48247.488 | 51598.363 | 5953.147 | 0 | 20951.382 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 142055000000 | 140572.137 | 21-APR-15:30 | 48247.488 | 50956.165 | 7802.077 | 0 | 33557.957 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 160760000000 | 156481.581 | 31-MAY-15:00 | 48247.488 | 50956.165 | 11082.8 | 0 | 46186.678 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 184147000000 | 189538.23 | 27-JUN-15:00 | 48247.488 | 50956.165 | 17651.997 | 0 | 72674.13 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 189207000000 | 185732.15 | 24-JUL-15:00 | 48247.488 | 50956.165 | 17248.252 | 0 | 69271.795 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 198356000000 | 179754.363 | 04-AUG-15:15 | 48247.488 | 50956.165 | 14866.986 | 0 | 65675.275 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 165856000000 | 171842.429 | 01-SEP-15:15 | 48247.488 | 50956.165 | 14664.134 | 0 | 57966.192 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 150553000000 | 143815.838 | 06-OCT-12:00 | 48247.488 | 51598.363 | 8120.962 | 0 | 35840.575 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 131827000000 | 124975.861 | 10-NOV-13:30 | 48247.488 | 51598.363 | 6196.162 | 0 | 18925.398 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 127321000000 | 124500.029 | 05-DEC-13:00 | 48247.488 | 51598.363 | 5831.673 | 0 | 18803.018 | 0 | 19.486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1840760000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 119788000000 | 120597.488 |  | 48247.488 | 50956.165 | 5729.223 | 0 | 14998.375 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 198356000000 | 189538.23 |  | 48247.488 | 51598.363 | 17651.997 | 0 | 72674.13 | 0 | 24.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 51610.87 | 3559.87 | 0 | 55170.74
Cost per Total Building Area ($/m2) | 10.36 | 0.71 | 0 | 11.07
Cost per Net Conditioned Building Area ($/m2) | 10.36 | 0.71 | 0 | 11.07

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2269.8 | 455.58 | 455.58
Net Site Energy | 2269.8 | 455.58 | 455.58
Total Source Energy | 5644.3 | 1132.9 | 1132.9
Net Source Energy | 5644.3 | 1132.9 | 1132.9
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 651.31 | 0 | 0 | 0 | 0
Cooling | 95.46 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.85 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 82.35 | 0 | 0 | 0 | 0 | 0
Pumps | 1.2 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 38.02 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1580.47 | 689.34 | 0 | 0 | 0 | 174.77
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 40.7174
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.17 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 10.76 | 18.59 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 65.28 | 65.28 | 6.49 | 0.34 | 0.34 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 43.52 | 43.52 | 6.49 | 0.34 | 0.34 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 65.28 | 65.28 | 6.49 | 0.61 | 0.61 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 43.52 | 43.52 | 6.49 | 0.34 | 0.34 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 65.28 | 65.28 | 6.49 | 0.34 | 0.34 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 43.52 | 43.52 | 6.49 | 0.34 | 0.34 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 65.28 | 65.28 | 6.49 | 0.61 | 0.61 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 43.52 | 43.52 | 6.49 | 0.34 | 0.34 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 65.28 | 65.28 | 6.49 | 0.34 | 0.34 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 43.52 | 43.52 | 6.49 | 0.34 | 0.34 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 65.28 | 65.28 | 6.49 | 0.61 | 0.61 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 43.52 | 43.52 | 6.49 | 0.34 | 0.34 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 6.49 | 0.421 | 0.421
North Total or Average |  |  | 195.85 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 456.98 | 6.49 | 0.34 | 0.34
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 384048.16 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 93540.99 | 74707 | 18833.99 | 0.8 | 5.58
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 124799.77 | 99671.99 | 25127.78 | 0.8 | 5.58
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 118495.84 | 94637.32 | 23858.51 | 0.8 | 5.59
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Gas | 10419.43 | 0.99
VAV_2_HEATC | Coil:Heating:Gas | 7474.01 | 0.99
VAV_3_HEATC | Coil:Heating:Gas | 8070.93 | 0.99
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 5.65 | 14794.25 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 7.54 | 19738.07 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 7.16 | 18741.06 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2259.48 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 17527.9781 | 15.3433 | 102.0453 | 0 | 0.0001 | 615520.8994 | 6377.799
February | 13626.0654 | 11.8458 | 93.9933 | 0 | 0 | 567030.4487 | 5002.7739
March | 15934.237 | 13.8609 | 108.3918 | 0 | 0.0001 | 653885.2503 | 5845.5654
April | 13742.2759 | 11.9126 | 100.9027 | 0 | 0.0001 | 608740.2396 | 5064.0749
May | 13938.4736 | 12.0362 | 110.6696 | 0 | 0.0001 | 667698.5449 | 5161.7777
June | 13468.0673 | 11.6092 | 110.6512 | 0 | 0.0001 | 667601.9668 | 4998.9131
July | 12795.4761 | 11.0083 | 108.9152 | 0 | 0.0001 | 657142.538 | 4760.8318
August | 14088.0966 | 12.1259 | 118.9256 | 0 | 0.0001 | 717536.8309 | 5238.7512
September | 12961.5792 | 11.151 | 110.3687 | 0 | 0.0001 | 665912.1578 | 4822.7548
October | 13649.2303 | 11.7767 | 110.1153 | 0 | 0.0001 | 664361.2491 | 5059.979
November | 14474.3798 | 12.5648 | 103.1402 | 0 | 0.0001 | 622225.7131 | 5324.2839
December | 16687.4618 | 14.5941 | 99.5562 | 0 | 0.0001 | 600519.9405 | 6079.3008
Annual Sum or Average | 172893.3211 | 149.8287 | 1277.6751 | 0 | 0.0006 | 7708180 | 63736.8054
Minimum of Months | 12795.4761 | 11.0083 | 93.9933 | 0 | 0 | 567030.4487 | 4760.8318
Maximum of Months | 17527.9781 | 15.3433 | 118.9256 | 0 | 0.0001 | 717536.8309 | 6377.799
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 126205000000 | 111846.428 | 02-JAN-08:15 | 48247.488 | 58341.44 | 4586.359 | 0 | 0 | 0 | 671.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 116263000000 | 120962.768 | 15-FEB-16:15 | 48247.488 | 50956.165 | 4805.571 | 0 | 16945.094 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 134071000000 | 117250.524 | 01-MAR-13:15 | 48247.488 | 51598.363 | 4839.679 | 0 | 12552.774 | 0 | 12.221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 124815000000 | 120118.581 | 28-APR-12:15 | 48247.488 | 51598.363 | 4713.049 | 0 | 15550.217 | 0 | 9.464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 136903000000 | 124283.732 | 26-MAY-12:00 | 48247.488 | 51598.363 | 4821.319 | 0 | 19608.112 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 136883000000 | 127139.469 | 16-JUN-15:00 | 48247.488 | 50956.165 | 6014.764 | 0 | 21912.602 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 134739000000 | 139116.319 | 03-JUL-12:00 | 48247.488 | 51598.363 | 8161.073 | 0 | 31100.946 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 147122000000 | 130134.85 | 15-AUG-12:15 | 48247.488 | 51598.363 | 5603.098 | 0 | 24677.451 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 136537000000 | 142727.363 | 28-SEP-15:30 | 48247.488 | 50956.165 | 9330.027 | 0 | 34185.233 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 136219000000 | 127927.56 | 31-OCT-13:15 | 48247.488 | 51598.363 | 5570.915 | 0 | 22502.345 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 127580000000 | 116962.116 | 16-NOV-16:00 | 48247.488 | 50956.165 | 4655.298 | 0 | 10343.435 | 2729.127 | 30.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 123129000000 | 111509.759 | 26-DEC-08:15 | 48247.488 | 58341.44 | 4586.359 | 0 | 0 | 0 | 334.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1580470000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 116263000000 | 111509.759 |  | 48247.488 | 50956.165 | 4586.359 | 0 | 0 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 147122000000 | 142727.363 |  | 48247.488 | 58341.44 | 9330.027 | 0 | 34185.233 | 2729.127 | 671.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 66098.24 | 5899.1 | 0 | 71997.34
Cost per Total Building Area ($/m2) | 13.27 | 1.18 | 0 | 14.45
Cost per Net Conditioned Building Area ($/m2) | 13.27 | 1.18 | 0 | 14.45

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2870.27 | 576.11 | 576.11
Net Site Energy | 2870.27 | 576.11 | 576.11
Total Source Energy | 7764.94 | 1558.54 | 1558.54
Net Source Energy | 7764.94 | 1558.54 | 1558.54
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 967.62 | 0 | 0 | 0 | 0
Cooling | 347.22 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.89 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 113.75 | 0 | 0 | 0 | 0 | 0
Pumps | 1.71 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 38.48 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1864.17 | 1006.1 | 0 | 0 | 0 | 174.77
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 40.7174
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.17 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 10.76 | 18.59 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 195.85 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 456.98 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 482393.6 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 133683.1 | 102863.54 | 30819.56 | 0.77 | 5.08
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 158408.95 | 122203.86 | 36205.09 | 0.77 | 5.08
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 171883.04 | 131234.94 | 40648.1 | 0.76 | 4.97
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Gas | 22869.9 | 0.99
VAV_2_HEATC | Coil:Heating:Gas | 20656.23 | 0.99
VAV_3_HEATC | Coil:Heating:Gas | 19843.52 | 0.99
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 7.43 | 19463.98 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 8.86 | 23049.76 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 9.39 | 24427.61 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2838.08 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 36249.7881 | 58.9845 | 144.1582 | 0 | 0.0006 | 8962.0049 | 14930.8533
February | 30727.9146 | 51.5565 | 130.7959 | 0 | 0.0005 | 8131.9879 | 12798.8266
March | 31880.407 | 56.9555 | 154.8353 | 0 | 0.0006 | 9628.0347 | 13595.7192
April | 27653.6046 | 51.3984 | 145.3179 | 0 | 0.0006 | 9036.9453 | 11975.5013
May | 28337.9316 | 55.1291 | 162.4902 | 0 | 0.0007 | 10105.6734 | 12496.6736
June | 29600.974 | 58.9109 | 177.0468 | 0 | 0.0007 | 11011.3926 | 13174.7839
July | 29695.899 | 59.1924 | 178.1257 | 0 | 0.0007 | 11078.5242 | 13225.4982
August | 32136.8499 | 64.0243 | 192.5819 | 0 | 0.0008 | 11977.613 | 14309.5393
September | 27336.1277 | 53.8946 | 160.6906 | 0 | 0.0006 | 9993.9718 | 12120.2157
October | 28405.775 | 53.9847 | 155.8319 | 0 | 0.0006 | 9691.1832 | 12409.8881
November | 29782.9682 | 53.6516 | 147.096 | 0 | 0.0006 | 9146.9474 | 12741.775
December | 33976.778 | 56.4539 | 141.5679 | 0 | 0.0006 | 8801.4916 | 14101.4235
Annual Sum or Average | 365785.0177 | 674.1363 | 1890.5384 | 0 | 0.0077 | 117565.7701 | 157880.6978
Minimum of Months | 27336.1277 | 51.3984 | 130.7959 | 0 | 0.0005 | 8131.9879 | 11975.5013
Maximum of Months | 36249.7881 | 64.0243 | 192.5819 | 0 | 0.0008 | 11977.613 | 14930.8533
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 142105000000 | 130696.34 | 09-JAN-08:00 | 48247.488 | 58341.44 | 5763.048 | 0 | 18237.421 | 0 | 106.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 128944000000 | 125854.15 | 13-FEB-08:00 | 48247.488 | 58341.44 | 5763.048 | 0 | 13339.59 | 0 | 162.583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 152666000000 | 134217.133 | 10-MAR-08:00 | 48247.488 | 58341.44 | 5763.048 | 0 | 21840.382 | 0 | 24.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 143293000000 | 135525.721 | 04-APR-07:00 | 48247.488 | 58341.44 | 5763.048 | 0 | 23131.428 | 0 | 42.316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 160240000000 | 144649.725 | 16-MAY-07:45 | 48247.488 | 58341.44 | 6110.665 | 0 | 31940.875 | 0 | 9.256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 174601000000 | 170751.807 | 26-JUN-15:30 | 48247.488 | 50956.165 | 12932.911 | 0 | 58606.793 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 175666000000 | 176696.154 | 25-JUL-15:30 | 48247.488 | 50956.165 | 12773.585 | 0 | 64710.467 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 189922000000 | 176676.508 | 04-AUG-15:15 | 48247.488 | 50956.165 | 14030.925 | 0 | 63433.48 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 158468000000 | 153331.374 | 08-SEP-15:30 | 48247.488 | 50956.165 | 9341.117 | 0 | 44778.154 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 153667000000 | 141855.144 | 03-OCT-07:00 | 48247.488 | 58341.44 | 5791.785 | 0 | 29461.077 | 0 | 13.354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 145038000000 | 136792.638 | 03-NOV-13:00 | 48247.488 | 51598.363 | 6381.495 | 0 | 30556.711 | 0 | 8.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 139560000000 | 124731.7 | 08-DEC-08:00 | 48247.488 | 58341.44 | 5763.048 | 0 | 12282.374 | 0 | 97.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1864170000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 128944000000 | 124731.7 |  | 48247.488 | 50956.165 | 5763.048 | 0 | 12282.374 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 189922000000 | 176696.154 |  | 48247.488 | 58341.44 | 14030.925 | 0 | 64710.467 | 0 | 162.583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 40365.55 | 9750.11 | 0 | 50115.66
Cost per Total Building Area ($/m2) | 8.1 | 1.96 | 0 | 10.06
Cost per Net Conditioned Building Area ($/m2) | 8.1 | 1.96 | 0 | 10.06

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2458.16 | 493.39 | 493.39
Net Site Energy | 2458.16 | 493.39 | 493.39
Total Source Energy | 6614.67 | 1327.67 | 1327.67
Net Source Energy | 6614.67 | 1327.67 | 1327.67
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 654.58 | 0 | 0 | 0 | 0
Cooling | 240.33 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.88 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 122.62 | 0 | 0 | 0 | 0 | 0
Pumps | 1.22 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 37.92 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1765.66 | 692.5 | 0 | 0 | 0 | 174.77
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 40.7174
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.17 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 10.76 | 18.59 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 195.85 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 456.98 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 453620.48 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 137277.41 | 109637.32 | 27640.08 | 0.8 | 5.58
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 168423.4 | 134512.23 | 33911.16 | 0.8 | 4.86
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 177794.29 | 141996.34 | 35797.94 | 0.8 | 4.86
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Gas | 16032.52 | 0.99
VAV_2_HEATC | Coil:Heating:Gas | 13618.12 | 0.99
VAV_3_HEATC | Coil:Heating:Gas | 12899.1 | 0.99
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 8.29 | 21711.51 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 10.17 | 23366.82 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 10.74 | 24666.92 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2668.8 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 43289.0981 | 69.2115 | 162.1142 | 0 | 0.0006 | 168531.1948 | 17917.0266
February | 36991.4001 | 60.342 | 145.0215 | 0 | 0.0006 | 150771.2182 | 15428.1049
March | 41654.6714 | 69.203 | 170.0911 | 0 | 0.0007 | 176844.0321 | 17496.0392
April | 36825.5111 | 62.8357 | 159.3328 | 0 | 0.0006 | 165670.3009 | 15630.0622
May | 41812.9181 | 72.8937 | 189.2901 | 0 | 0.0007 | 196829.5354 | 17898.7337
June | 44901.7752 | 78.5951 | 204.9871 | 0 | 0.0008 | 213153.7679 | 19252.0253
July | 46310.2454 | 81.1181 | 211.7289 | 0 | 0.0008 | 220164.5773 | 19861.5708
August | 48888.9622 | 85.6087 | 223.3762 | 0 | 0.0009 | 232275.7075 | 20964.9491
September | 41692.8354 | 72.852 | 189.6539 | 0 | 0.0007 | 197208.8966 | 17863.7752
October | 38977.8023 | 66.6896 | 169.6271 | 0 | 0.0007 | 176375.305 | 16561.3683
November | 39102.4566 | 64.5675 | 157.5298 | 0 | 0.0006 | 163781.2027 | 16385.2658
December | 42472.55 | 67.9291 | 159.1815 | 0 | 0.0006 | 165482.5619 | 17581.3322
Annual Sum or Average | 502920.2257 | 851.8459 | 2141.9341 | 0 | 0.0084 | 2227090 | 212840.2534
Minimum of Months | 36825.5111 | 60.342 | 145.0215 | 0 | 0.0006 | 150771.2182 | 15428.1049
Maximum of Months | 48888.9622 | 85.6087 | 223.3762 | 0 | 0.0009 | 232275.7075 | 20964.9491
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 133614000000 | 120893.001 | 17-JAN-08:45 | 48247.488 | 58341.44 | 6004.438 | 0 | 8123.38 | 0 | 176.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 119533000000 | 125001.053 | 14-FEB-16:15 | 48247.488 | 50956.165 | 6883.575 | 0 | 18905.17 | 0 | 8.655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 140204000000 | 127640.961 | 02-MAR-13:00 | 48247.488 | 51598.363 | 7423.557 | 0 | 20362.726 | 0 | 8.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 131345000000 | 135542.033 | 21-APR-15:30 | 48247.488 | 50956.165 | 8170.463 | 0 | 28159.466 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 156049000000 | 146554.965 | 31-MAY-15:00 | 48247.488 | 50956.165 | 10378.695 | 0 | 36964.167 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 168991000000 | 163468.922 | 29-JUN-15:30 | 48247.488 | 50956.165 | 14876.789 | 0 | 49380.03 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 174549000000 | 171751.777 | 03-JUL-15:30 | 48247.488 | 50956.165 | 17148.759 | 0 | 55390.915 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 184151000000 | 169588.048 | 01-AUG-15:15 | 48247.488 | 50956.165 | 15364.777 | 0 | 55011.169 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 156350000000 | 157155.24 | 05-SEP-12:00 | 48247.488 | 51598.363 | 9794.291 | 0 | 47506.648 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 139832000000 | 138340.614 | 11-OCT-15:00 | 48247.488 | 50956.165 | 8150.044 | 0 | 30978.467 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 129848000000 | 123992.797 | 01-NOV-13:00 | 48247.488 | 51598.363 | 7216.044 | 0 | 16919.375 | 0 | 11.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 131197000000 | 121014.162 | 04-DEC-08:30 | 48247.488 | 58341.44 | 6004.438 | 0 | 8286.73 | 0 | 134.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1765660000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 119533000000 | 120893.001 |  | 48247.488 | 50956.165 | 6004.438 | 0 | 8123.38 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 184151000000 | 171751.777 |  | 48247.488 | 58341.44 | 17148.759 | 0 | 55390.915 | 0 | 176.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 18304.25 | 4773.52 | 0 | 23077.77
Cost per Total Building Area ($/m2) | 3.67 | 0.96 | 0 | 4.63
Cost per Net Conditioned Building Area ($/m2) | 3.67 | 0.96 | 0 | 4.63

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2594.25 | 520.71 | 520.71
Net Site Energy | 2594.25 | 520.71 | 520.71
Total Source Energy | 3868.01 | 776.37 | 776.37
Net Source Energy | 3868.01 | 776.37 | 776.37
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 961.77 | 0 | 0 | 0 | 0
Cooling | 91.68 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.82 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 97.71 | 0 | 0 | 0 | 0 | 0
Pumps | 1.62 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 40.05 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1592.43 | 1001.82 | 0 | 0 | 0 | 174.77
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 40.7174
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.17 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 10.76 | 18.59 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 195.85 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 456.98 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 433483.6 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 109253.19 | 87255.63 | 21997.55 | 0.8 | 5.58
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 139077.22 | 111074.76 | 28002.47 | 0.8 | 5.54
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 137182.81 | 109561.77 | 27621.04 | 0.8 | 5.59
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Gas | 17022.47 | 0.99
VAV_2_HEATC | Coil:Heating:Gas | 14251.55 | 0.99
VAV_3_HEATC | Coil:Heating:Gas | 14433.73 | 0.99
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 6.6 | 17279.26 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 8.4 | 21854.25 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 8.29 | 21696.55 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2550.33 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 15566.2491 | 18.4452 | 27.6186 | 0 | 0.0001 | 364435.5666 | 5849.6879
February | 11881.8641 | 14.6614 | 24.7975 | 0 | 0.0001 | 327352.9265 | 4527.4543
March | 12697.4414 | 16.0519 | 28.9523 | 0 | 0.0001 | 382281.5493 | 4879.3643
April | 10070.6892 | 13.2677 | 26.3883 | 0 | 0.0001 | 348528.3848 | 3927.416
May | 8521.2453 | 12.3143 | 29.2746 | 0 | 0.0001 | 386830.7947 | 3439.6766
June | 7845.0923 | 11.8348 | 30.1286 | 0 | 0.0001 | 398177.9188 | 3220.0313
July | 7432.6664 | 11.5545 | 30.7274 | 0 | 0.0001 | 406130.8155 | 3087.3641
August | 8079.1917 | 12.5702 | 33.4684 | 0 | 0.0001 | 442359.8806 | 3357.0598
September | 8287.0417 | 12.058 | 28.9943 | 0 | 0.0001 | 383136.9419 | 3353.9325
October | 10217.6677 | 13.6238 | 27.8103 | 0 | 0.0001 | 367337.2109 | 4002.1289
November | 12890.0514 | 15.9218 | 27.0063 | 0 | 0.0001 | 356514.967 | 4913.3697
December | 15237.9949 | 18.0502 | 26.9977 | 0 | 0.0001 | 356242.1451 | 5725.6879
Annual Sum or Average | 128727.1952 | 170.3539 | 342.1642 | 0 | 0.0014 | 4519330 | 50283.1732
Minimum of Months | 7432.6664 | 11.5545 | 24.7975 | 0 | 0.0001 | 327352.9265 | 3087.3641
Maximum of Months | 15566.2491 | 18.4452 | 33.4684 | 0 | 0.0001 | 442359.8806 | 5849.6879
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 128413000000 | 115497.251 | 31-JAN-08:00 | 48247.488 | 58341.44 | 5236.921 | 0 | 3496.681 | 0 | 174.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 115346000000 | 115522.631 | 21-FEB-13:00 | 48247.488 | 51598.363 | 5236.921 | 0 | 10404.5 | 0 | 35.359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 134701000000 | 119566.229 | 29-MAR-12:00 | 48247.488 | 51598.363 | 5827.39 | 0 | 13884.169 | 0 | 8.819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 122808000000 | 116530.099 | 18-APR-15:00 | 48247.488 | 50956.165 | 5642.155 | 0 | 11675.841 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 136304000000 | 130273.933 | 05-MAY-15:00 | 48247.488 | 50956.165 | 5571.931 | 0 | 25489.9 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 140302000000 | 135470.691 | 28-JUN-15:15 | 48247.488 | 50956.165 | 7840.546 | 0 | 28418.042 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 143105000000 | 144514.446 | 24-JUL-15:15 | 48247.488 | 50956.165 | 9720.811 | 0 | 35581.532 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 155870000000 | 143819.856 | 07-AUG-15:15 | 48247.488 | 50956.165 | 10238.356 | 0 | 34369.397 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 135002000000 | 137213.869 | 01-SEP-15:45 | 48247.488 | 50956.165 | 7290.341 | 0 | 30711.424 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 129435000000 | 123559.121 | 17-OCT-12:00 | 48247.488 | 51598.363 | 5891.439 | 0 | 17812.415 | 0 | 9.415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 125622000000 | 120014.746 | 03-NOV-08:00 | 48247.488 | 58341.44 | 5236.921 | 0 | 8123 | 0 | 65.896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 125526000000 | 116038.282 | 29-DEC-08:45 | 48247.488 | 58341.44 | 5236.921 | 0 | 4064.768 | 0 | 147.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1592430000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 115346000000 | 115497.251 |  | 48247.488 | 50956.165 | 5236.921 | 0 | 3496.681 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 155870000000 | 144514.446 |  | 48247.488 | 58341.44 | 10238.356 | 0 | 35581.532 | 0 | 174.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 34476.54 | 8431.39 | 0 | 42907.94
Cost per Total Building Area ($/m2) | 6.92 | 1.69 | 0 | 8.61
Cost per Net Conditioned Building Area ($/m2) | 6.92 | 1.69 | 0 | 8.61

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3005.16 | 603.18 | 603.18
Net Site Energy | 3005.16 | 603.18 | 603.18
Total Source Energy | 7552.19 | 1515.84 | 1515.84
Net Source Energy | 7552.19 | 1515.84 | 1515.84
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1223.8 | 0 | 0 | 0 | 0
Cooling | 223.28 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.83 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 113.29 | 0 | 0 | 0 | 0 | 0
Pumps | 2.24 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 41.11 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1740.25 | 1264.91 | 0 | 0 | 0 | 174.77
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 40.7174
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.17 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 10.76 | 18.59 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 195.85 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 456.98 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 466367.93 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 130105.7 | 100356.29 | 29749.41 | 0.77 | 5.12
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 156433.26 | 121135.12 | 35298.14 | 0.77 | 5.13
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 168913.27 | 128535.37 | 40377.9 | 0.76 | 4.93
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Gas | 32875.5 | 0.99
VAV_2_HEATC | Coil:Heating:Gas | 30511.91 | 0.99
VAV_3_HEATC | Coil:Heating:Gas | 30015.12 | 0.99
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 7.28 | 19048.69 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 8.83 | 22956.92 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 9.16 | 23820.86 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2743.8 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 61624.8975 | 98.5901 | 255.949 | 0 | 0.0008 | 58904.6984 | 25406.5525
February | 52488.4322 | 85.7474 | 228.638 | 0 | 0.0007 | 52622.314 | 21809.4261
March | 56205.896 | 94.4377 | 260.5207 | 0 | 0.0008 | 59964.5484 | 23604.2997
April | 47306.5189 | 82.2009 | 235.5533 | 0 | 0.0007 | 54221.9365 | 20126.5942
May | 52068.8105 | 93.2783 | 276.0653 | 0 | 0.0008 | 63551.3614 | 22420.6447
June | 57600.0579 | 104.64 | 314.1006 | 0 | 0.0009 | 72309.21 | 24941.2824
July | 58760.1367 | 106.8268 | 320.902 | 0 | 0.001 | 73875.0504 | 25451.1858
August | 61935.0951 | 112.5492 | 337.9431 | 0 | 0.001 | 77798.0277 | 26821.624
September | 52354.2975 | 94.5224 | 281.9707 | 0 | 0.0009 | 64911.8096 | 22613.6205
October | 50364.8598 | 88.5897 | 257.2233 | 0 | 0.0008 | 59211.6721 | 21530.505
November | 51538.303 | 87.0107 | 241.3771 | 0 | 0.0007 | 55558.8655 | 21683.8241
December | 58296.4508 | 94.2177 | 247.8352 | 0 | 0.0008 | 57039.0023 | 24125.3846
Annual Sum or Average | 660543.7561 | 1142.611 | 3258.0784 | 0 | 0.01 | 749968.4963 | 280534.9434
Minimum of Months | 47306.5189 | 82.2009 | 228.638 | 0 | 0.0007 | 52622.314 | 20126.5942
Maximum of Months | 61935.0951 | 112.5492 | 337.9431 | 0 | 0.001 | 77798.0277 | 26821.624
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 136684000000 | 118179.389 | 24-JAN-08:45 | 48247.488 | 58341.44 | 5667.067 | 0 | 5745.56 | 0 | 177.833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 122106000000 | 118124.567 | 13-FEB-08:30 | 48247.488 | 58341.44 | 5667.067 | 0 | 5691.966 | 0 | 176.606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 139143000000 | 125060.563 | 31-MAR-15:15 | 48247.488 | 50956.165 | 5667.067 | 0 | 20179.588 | 0 | 10.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 125818000000 | 131662.729 | 10-APR-07:00 | 48247.488 | 58341.44 | 5667.067 | 0 | 19348.837 | 0 | 57.896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 147466000000 | 150769.867 | 30-MAY-12:45 | 48247.488 | 51598.363 | 6495.213 | 0 | 44420.354 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 167788000000 | 163057.734 | 08-JUN-12:00 | 48247.488 | 51598.363 | 8840.329 | 0 | 54363.104 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 171421000000 | 171374.096 | 03-JUL-15:15 | 48247.488 | 50956.165 | 13184.317 | 0 | 58977.676 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 180524000000 | 166457.864 | 04-AUG-15:30 | 48247.488 | 50956.165 | 10407.063 | 0 | 56838.697 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 150623000000 | 149587.902 | 07-SEP-12:00 | 48247.488 | 51598.363 | 6260.794 | 0 | 43472.807 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 137396000000 | 139382.084 | 31-OCT-08:00 | 48247.488 | 58341.44 | 5667.067 | 0 | 27108.063 | 0 | 18.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 128920000000 | 142080.709 | 02-NOV-08:00 | 48247.488 | 58341.44 | 5667.067 | 0 | 29791.98 | 0 | 32.734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 132355000000 | 117660.001 | 11-DEC-08:45 | 48247.488 | 58341.44 | 5667.067 | 0 | 5202.01 | 0 | 201.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1740250000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 122106000000 | 117660.001 |  | 48247.488 | 50956.165 | 5667.067 | 0 | 5202.01 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 180524000000 | 171374.096 |  | 48247.488 | 58341.44 | 13184.317 | 0 | 58977.676 | 0 | 201.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 42607.99 | 10553.01 | 0 | 53161
Cost per Total Building Area ($/m2) | 8.55 | 2.12 | 0 | 10.67
Cost per Net Conditioned Building Area ($/m2) | 8.55 | 2.12 | 0 | 10.67

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2645.26 | 530.94 | 530.94
Net Site Energy | 2645.26 | 530.94 | 530.94
Total Source Energy | 6661.07 | 1336.98 | 1336.98
Net Source Energy | 6661.07 | 1336.98 | 1336.98
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 909.56 | 0 | 0 | 0 | 0
Cooling | 177.79 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.84 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 113.71 | 0 | 0 | 0 | 0 | 0
Pumps | 1.78 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 40.98 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1694.72 | 950.54 | 0 | 0 | 0 | 174.77
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 40.7174
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.17 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 10.76 | 18.59 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 195.85 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 456.98 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 431762.83 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 131623.55 | 105121.84 | 26501.71 | 0.8 | 5.58
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 164005.24 | 130983.64 | 33021.59 | 0.8 | 4.86
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 165419.53 | 132113.18 | 33306.35 | 0.8 | 4.86
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Gas | 24961.99 | 0.99
VAV_2_HEATC | Coil:Heating:Gas | 22456.8 | 0.99
VAV_3_HEATC | Coil:Heating:Gas | 22355.51 | 0.99
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 7.95 | 20817.31 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 9.91 | 22753.85 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 9.99 | 22950.06 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2540.21 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 45998.0517 | 72.0435 | 164.1451 | 0 | 0.0007 | 170630.9112 | 18891.196
February | 39183.899 | 62.4944 | 145.9089 | 0 | 0.0006 | 151683.2836 | 16202.8448
March | 42860.0409 | 70.2205 | 169.6817 | 0 | 0.0007 | 176411.3923 | 17905.7068
April | 37030.8521 | 62.3979 | 155.9554 | 0 | 0.0006 | 162153.3128 | 15639.9079
May | 39374.1645 | 67.5737 | 172.467 | 0 | 0.0007 | 179329.5347 | 16749.9856
June | 41149.4607 | 71.6048 | 185.5707 | 0 | 0.0007 | 192961.1327 | 17601.7555
July | 43690.0515 | 76.4748 | 199.4588 | 0 | 0.0008 | 207405.2564 | 18732.5523
August | 45765.3193 | 80.0652 | 208.7048 | 0 | 0.0008 | 217019.3386 | 19618.2077
September | 38569.206 | 66.8317 | 172.4022 | 0 | 0.0007 | 179266.3664 | 16470.2758
October | 38927.5357 | 65.8832 | 165.5097 | 0 | 0.0007 | 172089.2992 | 16469.3562
November | 40406.0414 | 65.6297 | 156.88 | 0 | 0.0006 | 163097.7855 | 16824.5617
December | 44652.696 | 69.9222 | 159.2676 | 0 | 0.0006 | 165560.5435 | 18337.2762
Annual Sum or Average | 497607.3189 | 831.1417 | 2055.9519 | 0 | 0.0081 | 2137610 | 209443.6267
Minimum of Months | 37030.8521 | 62.3979 | 145.9089 | 0 | 0.0006 | 151683.2836 | 15639.9079
Maximum of Months | 45998.0517 | 80.0652 | 208.7048 | 0 | 0.0008 | 217019.3386 | 19618.2077
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 135278000000 | 119817.47 | 11-JAN-08:45 | 48247.488 | 58341.44 | 5726.879 | 0 | 7382.993 | 0 | 118.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 120256000000 | 119358.959 | 06-FEB-08:30 | 48247.488 | 58341.44 | 5726.879 | 0 | 6855.077 | 0 | 188.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 139861000000 | 125107.402 | 30-MAR-12:00 | 48247.488 | 51598.363 | 6454.533 | 0 | 18798.569 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 128557000000 | 130304.767 | 25-APR-12:00 | 48247.488 | 51598.363 | 6640.782 | 0 | 23809.684 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 142175000000 | 140878.863 | 24-MAY-15:30 | 48247.488 | 50956.165 | 8195.683 | 0 | 33471.077 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 152982000000 | 150083.936 | 27-JUN-15:15 | 48247.488 | 50956.165 | 11065.582 | 0 | 39806.251 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 164433000000 | 163230.132 | 17-JUL-15:15 | 48247.488 | 50956.165 | 15527.827 | 0 | 48490.201 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 172056000000 | 158411.788 | 30-AUG-12:00 | 48247.488 | 51598.363 | 12403.893 | 0 | 46153.595 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 142125000000 | 143553.121 | 01-SEP-15:30 | 48247.488 | 50956.165 | 9729.214 | 0 | 34611.804 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 136434000000 | 135330.037 | 05-OCT-15:15 | 48247.488 | 50956.165 | 8145.941 | 0 | 27971.993 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 129306000000 | 125381.623 | 10-NOV-13:00 | 48247.488 | 51598.363 | 6442.5 | 0 | 19077.587 | 0 | 15.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 131258000000 | 119631.151 | 06-DEC-08:30 | 48247.488 | 58341.44 | 5726.879 | 0 | 7160.226 | 0 | 155.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1694720000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 120256000000 | 119358.959 |  | 48247.488 | 50956.165 | 5726.879 | 0 | 6855.077 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 172056000000 | 163230.132 |  | 48247.488 | 58341.44 | 15527.827 | 0 | 48490.201 | 0 | 188.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 17576.56 | 6577.68 | 0 | 24154.23
Cost per Total Building Area ($/m2) | 3.53 | 1.32 | 0 | 4.85
Cost per Net Conditioned Building Area ($/m2) | 3.53 | 1.32 | 0 | 4.85

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3342.19 | 670.83 | 670.83
Net Site Energy | 3342.19 | 670.83 | 670.83
Total Source Energy | 7691.96 | 1543.89 | 1543.89
Net Source Energy | 7691.96 | 1543.89 | 1543.89
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1575.02 | 0 | 0 | 0 | 0
Cooling | 201.07 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.87 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 118.06 | 0 | 0 | 0 | 0 | 0
Pumps | 3.19 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 43.38 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1723.79 | 1618.39 | 0 | 0 | 0 | 174.77
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 40.7174
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.17 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 10.76 | 18.59 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 195.85 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 456.98 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 467597.05 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 127446.66 | 99535.77 | 27910.89 | 0.78 | 5.27
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 154358.14 | 120935.76 | 33422.38 | 0.78 | 5.27
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 164837.88 | 127361.92 | 37475.96 | 0.77 | 5.1
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Gas | 38205.61 | 0.99
VAV_2_HEATC | Coil:Heating:Gas | 35768.49 | 0.99
VAV_3_HEATC | Coil:Heating:Gas | 35303.86 | 0.99
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 7.33 | 19188.72 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 8.94 | 23253.97 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 9.25 | 24070.06 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2751.03 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 50796.5862 | 73.8657 | 90.6166 | 0 | 0.0007 | 59496.9957 | 20234.0195
February | 41390.2153 | 62.4387 | 81.1671 | 0 | 0.0006 | 53306.5206 | 16702.3332
March | 40309.1283 | 64.7396 | 91.8492 | 0 | 0.0007 | 60344.129 | 16641.8941
April | 32130.0386 | 54.5942 | 82.951 | 0 | 0.0006 | 54512.5449 | 13550.9909
May | 34106.3209 | 60.7723 | 97.2357 | 0 | 0.0007 | 63912.0586 | 14654.0566
June | 36232.4117 | 65.792 | 107.3068 | 0 | 0.0008 | 70536.41 | 15685.2541
July | 36662.9808 | 66.7229 | 109.0672 | 0 | 0.0008 | 71694.1585 | 15885.8952
August | 39525.0398 | 71.8759 | 117.4002 | 0 | 0.0009 | 77171.5533 | 17120.6915
September | 32310.7745 | 57.7527 | 92.7022 | 0 | 0.0007 | 60932.9198 | 13899.7737
October | 33650.2268 | 56.9422 | 86.1102 | 0 | 0.0006 | 56587.6911 | 14169.6666
November | 38433.5719 | 61.042 | 85.3441 | 0 | 0.0006 | 56067.0279 | 15802.0538
December | 46626.5231 | 69.5292 | 88.8021 | 0 | 0.0007 | 58316.3009 | 18738.0515
Annual Sum or Average | 462173.8179 | 766.0673 | 1130.5525 | 0 | 0.0084 | 742878.3103 | 193084.6807
Minimum of Months | 32130.0386 | 54.5942 | 81.1671 | 0 | 0.0006 | 53306.5206 | 13550.9909
Maximum of Months | 50796.5862 | 73.8657 | 117.4002 | 0 | 0.0009 | 77171.5533 | 20234.0195
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 138058000000 | 117847.837 | 30-JAN-08:00 | 48247.488 | 58341.44 | 5726.15 | 0 | 5300.552 | 0 | 232.206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 123694000000 | 115485.602 | 27-FEB-08:00 | 48247.488 | 58341.44 | 5726.15 | 0 | 2931.85 | 0 | 238.674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 140024000000 | 118308.753 | 14-MAR-07:45 | 48247.488 | 58341.44 | 5726.15 | 0 | 5834.761 | 0 | 158.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 126492000000 | 124273.877 | 14-APR-15:00 | 48247.488 | 50956.165 | 5761.448 | 0 | 19300.326 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 148303000000 | 143370.467 | 31-MAY-12:30 | 48247.488 | 51598.363 | 7463.169 | 0 | 36052.997 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 163674000000 | 163278.989 | 30-JUN-15:15 | 48247.488 | 50956.165 | 12098.062 | 0 | 51968.824 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 166361000000 | 163262.702 | 18-JUL-07:00 | 48247.488 | 58341.44 | 7351.522 | 0 | 49313.802 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 179071000000 | 160115.95 | 28-AUG-15:30 | 48247.488 | 50956.165 | 10631.137 | 0 | 50272.71 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 141390000000 | 143515.195 | 14-SEP-15:15 | 48247.488 | 50956.165 | 7805.878 | 0 | 36497.214 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 131307000000 | 127694.98 | 06-OCT-15:15 | 48247.488 | 50956.165 | 6099.044 | 0 | 22383.528 | 0 | 8.755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 130099000000 | 120485.119 | 02-NOV-13:00 | 48247.488 | 51598.363 | 6175.847 | 0 | 14441.891 | 0 | 21.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 135319000000 | 117205.821 | 26-DEC-08:00 | 48247.488 | 58341.44 | 5726.15 | 0 | 4629.123 | 0 | 261.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1723790000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 123694000000 | 115485.602 |  | 48247.488 | 50956.165 | 5726.15 | 0 | 2931.85 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 179071000000 | 163278.989 |  | 48247.488 | 58341.44 | 12098.062 | 0 | 51968.824 | 0 | 261.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 30166.7 | 12724.14 | 0 | 42890.84
Cost per Total Building Area ($/m2) | 6.05 | 2.55 | 0 | 8.61
Cost per Net Conditioned Building Area ($/m2) | 6.05 | 2.55 | 0 | 8.61

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3059.08 | 614 | 614
Net Site Energy | 3059.08 | 614 | 614
Total Source Energy | 7273 | 1459.8 | 1459.8
Net Source Energy | 7273 | 1459.8 | 1459.8
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1365.75 | 0 | 0 | 0 | 0
Cooling | 134.83 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 110.53 | 0 | 0 | 0 | 0 | 0
Pumps | 2.76 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 43.79 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1649.53 | 1409.55 | 0 | 0 | 0 | 174.77
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 40.7174
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.17 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 10.76 | 18.59 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 65.28 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 65.28 | 65.28 | 3.18 | 0.501 | 0.622 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 43.52 | 3.18 | 0.402 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 195.85 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 456.98 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 436248.08 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 125318.32 | 100086.14 | 25232.19 | 0.8 | 5.58
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 157930.92 | 126132.36 | 31798.56 | 0.8 | 4.86
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 157828.17 | 126050.3 | 31777.87 | 0.8 | 4.86
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Gas | 35034.39 | 0.99
VAV_2_HEATC | Coil:Heating:Gas | 32369.84 | 0.99
VAV_3_HEATC | Coil:Heating:Gas | 32387.25 | 0.99
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 7.57 | 19820.09 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 9.54 | 21911.1 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 9.53 | 21896.85 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2566.59 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 48213.2372 | 71.705 | 101.2701 | 0 | 0.0007 | 2400510 | 19387.6112
February | 40332.0548 | 61.5833 | 90.5008 | 0 | 0.0007 | 2145570 | 16373.0335
March | 40641.1489 | 65.5074 | 103.6789 | 0 | 0.0007 | 2458680 | 16832.2049
April | 34042.6917 | 56.2122 | 91.6937 | 0 | 0.0006 | 2174690 | 14228.9252
May | 34685.77 | 59.415 | 101.1685 | 0 | 0.0007 | 2399750 | 14704.6659
June | 36330.0491 | 63.4016 | 110.196 | 0 | 0.0008 | 2614060 | 15514.8444
July | 36883.4305 | 65.2549 | 115.0845 | 0 | 0.0008 | 2730160 | 15836.9652
August | 38253.6549 | 67.4641 | 118.5822 | 0 | 0.0008 | 2813100 | 16404.5226
September | 33687.1893 | 58.292 | 100.3807 | 0 | 0.0007 | 2381150 | 14338.1181
October | 35472.9656 | 58.996 | 97.0726 | 0 | 0.0007 | 2302330 | 14867.5418
November | 38866.7538 | 61.7261 | 95.8207 | 0 | 0.0007 | 2272160 | 16008.2618
December | 45483.2392 | 68.4335 | 98.3881 | 0 | 0.0007 | 2332360 | 18366.0562
Annual Sum or Average | 462892.1852 | 757.991 | 1223.8367 | 0 | 0.0086 | 29024500 | 192862.7508
Minimum of Months | 33687.1893 | 56.2122 | 90.5008 | 0 | 0.0006 | 2145570 | 14228.9252
Maximum of Months | 48213.2372 | 71.705 | 118.5822 | 0 | 0.0008 | 2813100 | 19387.6112
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 136427000000 | 119211.29 | 20-JAN-08:00 | 48247.488 | 58341.44 | 5477.802 | 0 | 6979.872 | 0 | 164.688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 121938000000 | 119150.047 | 03-FEB-08:15 | 48247.488 | 58341.44 | 5477.802 | 0 | 6955.763 | 0 | 127.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 139732000000 | 122530.437 | 30-MAR-15:30 | 48247.488 | 50956.165 | 5903.199 | 0 | 17415.135 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 123593000000 | 119480.239 | 06-APR-15:00 | 48247.488 | 50956.165 | 5489.696 | 0 | 14778.44 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 136384000000 | 129456.471 | 16-MAY-15:00 | 48247.488 | 50956.165 | 6287.057 | 0 | 23957.311 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 148564000000 | 158172.735 | 26-JUN-15:15 | 48247.488 | 50956.165 | 12524.246 | 0 | 46436.385 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 155161000000 | 156793.453 | 21-JUL-15:45 | 48247.488 | 50956.165 | 12647.206 | 0 | 44934.144 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 159875000000 | 149299.095 | 08-AUG-15:45 | 48247.488 | 50956.165 | 10627.33 | 0 | 39459.662 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 135327000000 | 140528.963 | 12-SEP-12:45 | 48247.488 | 51598.363 | 7067.332 | 0 | 33607.33 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 130847000000 | 128352.34 | 06-OCT-15:30 | 48247.488 | 50956.165 | 6564.67 | 0 | 22575.568 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 129133000000 | 118477.349 | 13-NOV-08:00 | 48247.488 | 58341.44 | 5477.802 | 0 | 6208.572 | 0 | 202.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 132554000000 | 119186.09 | 21-DEC-08:45 | 48247.488 | 58341.44 | 5477.802 | 0 | 6979.772 | 0 | 139.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1649530000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 121938000000 | 118477.349 |  | 48247.488 | 50956.165 | 5477.802 | 0 | 6208.572 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 159875000000 | 158172.735 |  | 48247.488 | 58341.44 | 12647.206 | 0 | 46436.385 | 0 | 202.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 36484.96 | 11444.18 | 0 | 47929.13
Cost per Total Building Area ($/m2) | 7.32 | 2.3 | 0 | 9.62
Cost per Net Conditioned Building Area ($/m2) | 7.32 | 2.3 | 0 | 9.62

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3524.91 | 707.5 | 707.5
Net Site Energy | 3524.91 | 707.5 | 707.5
Total Source Energy | 7705.2 | 1546.55 | 1546.55
Net Source Energy | 7705.2 | 1546.55 | 1546.55
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1833.44 | 0 | 0 | 0 | 0
Cooling | 119.72 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.8 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 119.41 | 0 | 0 | 0 | 0 | 0
Pumps | 3.82 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 47.12 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1644.35 | 1880.56 | 0 | 0 | 0 | 174.77
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 40.7174
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.17 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 10.76 | 18.59 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 65.28 | 65.28 | 3.18 | 0.501 | 0.49 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 43.52 | 43.52 | 3.18 | 0.501 | 0.49 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 65.28 | 65.28 | 3.18 | 0.651 | 0.64 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 43.52 | 43.52 | 3.18 | 0.501 | 0.49 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 65.28 | 65.28 | 3.18 | 0.501 | 0.49 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 43.52 | 43.52 | 3.18 | 0.501 | 0.49 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 65.28 | 65.28 | 3.18 | 0.651 | 0.64 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 43.52 | 43.52 | 3.18 | 0.501 | 0.49 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 65.28 | 65.28 | 3.18 | 0.501 | 0.49 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 43.52 | 43.52 | 3.18 | 0.501 | 0.49 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 65.28 | 65.28 | 3.18 | 0.651 | 0.64 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 43.52 | 43.52 | 3.18 | 0.501 | 0.49 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.18 | 0.546 | 0.535
North Total or Average |  |  | 195.85 | 3.18 | 0.651 | 0.64
Non-North Total or Average |  |  | 456.98 | 3.18 | 0.501 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 457460.22 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 118718.15 | 94814.88 | 23903.28 | 0.8 | 5.58
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 152162.59 | 121525.46 | 30637.14 | 0.8 | 5.54
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 151413.84 | 120636.93 | 30776.9 | 0.8 | 5.5
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Gas | 40720.65 | 0.99
VAV_2_HEATC | Coil:Heating:Gas | 37727.19 | 0.99
VAV_3_HEATC | Coil:Heating:Gas | 37874.68 | 0.99
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 7.17 | 18776.22 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 9.19 | 23910.46 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 9.1 | 23668.63 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2691.39 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 50569.1507 | 73.6718 | 90.6564 | 0 | 0.0007 | 59523.9271 | 20156.5007
February | 42958.352 | 63.9246 | 81.3776 | 0 | 0.0006 | 53439.8099 | 17251.0347
March | 42521.0722 | 66.9799 | 92.6168 | 0 | 0.0007 | 60842.0581 | 17429.6845
April | 33328.0691 | 55.3162 | 81.7665 | 0 | 0.0006 | 53728.541 | 13930.6983
May | 32812.7853 | 56.6972 | 87.7838 | 0 | 0.0006 | 57692.5505 | 13929.0693
June | 32610.38 | 58.7078 | 94.928 | 0 | 0.0007 | 62397.5508 | 14068.7672
July | 34522.9279 | 62.5536 | 101.8068 | 0 | 0.0007 | 66920.5687 | 14932.3741
August | 35345.2672 | 63.6124 | 102.8274 | 0 | 0.0008 | 67589.8612 | 15246.8377
September | 31122.9215 | 54.207 | 84.6623 | 0 | 0.0006 | 55642.8048 | 13252.7983
October | 34188.595 | 57.088 | 84.9964 | 0 | 0.0006 | 55852.4486 | 14323.2273
November | 40477.0409 | 63.1071 | 86.0382 | 0 | 0.0007 | 56517.1418 | 16529.4005
December | 47961.9716 | 70.8247 | 89.0796 | 0 | 0.0007 | 58494.5084 | 19208.2182
Annual Sum or Average | 458418.5334 | 746.6903 | 1078.5397 | 0 | 0.0081 | 708641.7707 | 190258.6109
Minimum of Months | 31122.9215 | 54.207 | 81.3776 | 0 | 0.0006 | 53439.8099 | 13252.7983
Maximum of Months | 50569.1507 | 73.6718 | 102.8274 | 0 | 0.0008 | 67589.8612 | 20156.5007
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 138121000000 | 116045.222 | 13-JAN-08:00 | 48247.488 | 58341.44 | 5721.944 | 0 | 3512.748 | 0 | 221.602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 124003000000 | 117448.051 | 24-FEB-08:00 | 48247.488 | 58341.44 | 5721.944 | 0 | 5003.724 | 0 | 133.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 141179000000 | 117702.307 | 17-MAR-07:00 | 48247.488 | 58341.44 | 5721.944 | 0 | 5258.276 | 0 | 133.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 124673000000 | 117675.688 | 18-APR-07:15 | 48247.488 | 58341.44 | 5721.944 | 0 | 5225.865 | 0 | 138.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 133871000000 | 127151.086 | 31-MAY-15:00 | 48247.488 | 50956.165 | 6866.106 | 0 | 21072.877 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 144789000000 | 144434.736 | 14-JUN-11:45 | 48247.488 | 50788.728 | 6682.641 | 0 | 38707.43 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 155284000000 | 163269.808 | 07-JUL-07:00 | 48247.488 | 58341.44 | 8508.417 | 0 | 48164.014 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 156837000000 | 150572.347 | 14-AUG-07:00 | 48247.488 | 58341.44 | 7147.913 | 0 | 36827.056 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 129115000000 | 145593.599 | 07-SEP-15:15 | 48247.488 | 50956.165 | 7355.775 | 0 | 39025.721 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 129601000000 | 120533.108 | 27-OCT-12:45 | 48247.488 | 51598.363 | 6350.588 | 0 | 14315.248 | 0 | 21.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 131144000000 | 117426.136 | 17-NOV-08:30 | 48247.488 | 58341.44 | 5721.944 | 0 | 4957.715 | 0 | 157.548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 135732000000 | 116984.802 | 26-DEC-08:00 | 48247.488 | 58341.44 | 5721.944 | 0 | 4394.681 | 0 | 279.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1644350000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 124003000000 | 116045.222 |  | 48247.488 | 50788.728 | 5721.944 | 0 | 3512.748 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 156837000000 | 163269.808 |  | 48247.488 | 58341.44 | 8508.417 | 0 | 48164.014 | 0 | 279.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 28898.04 | 14785.02 | 0 | 43683.06
Cost per Total Building Area ($/m2) | 5.8 | 2.97 | 0 | 8.77
Cost per Net Conditioned Building Area ($/m2) | 5.8 | 2.97 | 0 | 8.77

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4658.45 | 935.02 | 935.02
Net Site Energy | 4658.45 | 935.02 | 935.02
Total Source Energy | 9123.03 | 1831.13 | 1831.13
Net Source Energy | 9123.03 | 1831.13 | 1831.13
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2979.39 | 0 | 0 | 0 | 0
Cooling | 96.99 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.55 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 122.48 | 0 | 0 | 0 | 0 | 0
Pumps | 6.8 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 51.64 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1627.42 | 3031.04 | 0 | 0 | 0 | 174.77
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 40.7174
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.59 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.59 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.17 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 10.76 | 18.59 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 65.28 | 65.28 | 2.58 | 0.504 | 0.49 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 43.52 | 43.52 | 2.58 | 0.504 | 0.49 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 65.28 | 65.28 | 2.58 | 0.654 | 0.64 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 43.52 | 43.52 | 2.58 | 0.504 | 0.49 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 65.28 | 65.28 | 2.58 | 0.504 | 0.49 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 43.52 | 43.52 | 2.58 | 0.504 | 0.49 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 65.28 | 65.28 | 2.58 | 0.654 | 0.64 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 43.52 | 43.52 | 2.58 | 0.504 | 0.49 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 65.28 | 65.28 | 2.58 | 0.504 | 0.49 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 43.52 | 43.52 | 2.58 | 0.504 | 0.49 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 65.28 | 65.28 | 2.58 | 0.654 | 0.64 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 43.52 | 43.52 | 2.58 | 0.504 | 0.49 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 2.58 | 0.549 | 0.535
North Total or Average |  |  | 195.85 | 2.58 | 0.654 | 0.64
Non-North Total or Average |  |  | 456.98 | 2.58 | 0.504 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 483266.1 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 113460.71 | 90615.99 | 22844.72 | 0.8 | 5.58
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 157382.46 | 125694.33 | 31688.13 | 0.8 | 4.86
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 154065.92 | 123045.56 | 31020.36 | 0.8 | 5.54
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Gas | 57022.1 | 0.99
VAV_2_HEATC | Coil:Heating:Gas | 52950.67 | 0.99
VAV_3_HEATC | Coil:Heating:Gas | 53269.49 | 0.99
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 6.85 | 17944.71 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 9.51 | 21835.01 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1572.42 | 9.31 | 24209.54 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2843.22 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 58856.2743 | 62.8392 | 197.0734 | 0 | 0.0007 | 39521.441 | 21818.5382
February | 49670.7028 | 53.6114 | 178.439 | 0 | 0.0007 | 35788.2022 | 18502.5332
March | 46118.4883 | 51.5923 | 203.6482 | 0 | 0.0007 | 40855.1566 | 17458.6125
April | 32859.0092 | 38.3462 | 178.3026 | 0 | 0.0006 | 35778.1815 | 12683.3468
May | 28626.1218 | 34.8601 | 185.7454 | 0 | 0.0006 | 37277.4478 | 11273.1772
June | 28713.233 | 35.6586 | 200.7957 | 0 | 0.0007 | 40300.2117 | 11414.0279
July | 28449.6976 | 35.3963 | 200.3123 | 0 | 0.0007 | 40203.3951 | 11319.2681
August | 30143.3066 | 37.0618 | 202.9982 | 0 | 0.0007 | 40741.1044 | 11925.1477
September | 29491.7532 | 35.109 | 174.5156 | 0 | 0.0006 | 35021.041 | 11490.1529
October | 38953.0541 | 44.4623 | 190.5402 | 0 | 0.0007 | 38229.8019 | 14882.3852
November | 49556.2269 | 54.2533 | 194.0418 | 0 | 0.0007 | 38922.149 | 18577.6828
December | 55127.5941 | 59.383 | 195.569 | 0 | 0.0007 | 39223.1266 | 20517.0523
Annual Sum or Average | 476565.4618 | 542.5737 | 2301.9815 | 0 | 0.0081 | 461861.2589 | 181861.9248
Minimum of Months | 28449.6976 | 34.8601 | 174.5156 | 0 | 0.0006 | 35021.041 | 11273.1772
Maximum of Months | 58856.2743 | 62.8392 | 203.6482 | 0 | 0.0007 | 40855.1566 | 21818.5382
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 139258000000 | 120243.515 | 18-JAN-08:15 | 48247.488 | 58341.44 | 5591.545 | 0 | 5002.415 | 2729.127 | 331.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 126104000000 | 118029.755 | 27-FEB-08:15 | 48247.488 | 58341.44 | 5591.545 | 0 | 2712.177 | 2729.127 | 407.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 143958000000 | 116150.51 | 31-MAR-07:15 | 48247.488 | 58341.44 | 5591.545 | 0 | 3814.468 | 0 | 155.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 126068000000 | 118209.398 | 28-APR-07:45 | 48247.488 | 58341.44 | 5591.545 | 0 | 5951.035 | 0 | 77.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 131351000000 | 123135.788 | 30-MAY-12:30 | 48247.488 | 51598.363 | 6717.628 | 0 | 16563.859 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 142002000000 | 141187.963 | 21-JUN-15:15 | 48247.488 | 50956.165 | 7838.179 | 0 | 34137.681 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 141661000000 | 141621.194 | 11-JUL-15:00 | 48247.488 | 50956.165 | 8682.839 | 0 | 33726.252 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 143556000000 | 136607.868 | 15-AUG-12:00 | 48247.488 | 51598.363 | 7432.869 | 0 | 29320.698 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 123400000000 | 117660.73 | 25-SEP-07:00 | 48247.488 | 58341.44 | 5591.545 | 0 | 5309.201 | 0 | 171.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 134707000000 | 120734.83 | 05-OCT-07:15 | 48247.488 | 58341.44 | 5591.545 | 0 | 5682.355 | 2729.127 | 142.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 137146000000 | 121147.14 | 14-NOV-08:45 | 48247.488 | 58341.44 | 5591.545 | 0 | 6040.574 | 2729.127 | 196.965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 138207000000 | 117545.609 | 19-DEC-08:15 | 48247.488 | 58341.44 | 5591.545 | 0 | 2386.98 | 2729.127 | 249.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1627420000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 123400000000 | 116150.51 |  | 48247.488 | 50956.165 | 5591.545 | 0 | 2386.98 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 143958000000 | 141621.194 |  | 48247.488 | 58341.44 | 8682.839 | 0 | 34137.681 | 2729.127 | 407.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 46448.39 | 12500.64 | 0 | 58949.04
Cost per Total Building Area ($/m2) | 9.32 | 2.51 | 0 | 11.83
Cost per Net Conditioned Building Area ($/m2) | 9.32 | 2.51 | 0 | 11.83

## Picture
DOE Commercial Building Benchmark - Medium Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | 10.5 | 56.5 | 2946.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 2.8
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 14.1 | 86.15 | 4492.11
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.45
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 9.1 | 47.4 | 2471.57
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | 5.35 | 28.26 | 1473.56
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8 | 76 | 3962.86
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 12
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 122 | 6361.43
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 18
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 30.55 | 1592.96
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Sun, Hol, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 450 | 3058.2 | 159463.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624 | 4488 | 234017.14
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 648
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Core_bottom Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_bottom Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_bottom Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_bottom Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Core_mid Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_mid Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_mid Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_mid Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Core_top Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_top Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_top Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_top Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720