## Instructions
Title Block
Test Report Template Name: | Electric Motors
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | Instructions
File Name: | Electric Motors - v1.0.xlsx
Test Start Date: | [MM/DD/YYYY]
Test Completion Date: | [MM/DD/YYYY]
Reference Test Procedures
10 CFR 431 Subpart B Appendix B: Uniform Test Method for Measuring the Efficiency of Electric Motors
Table of Contents
Tab | Contents
Instructions | Instructions and table of contents
General Info & Test Results | Lab information, product information and test results
Determination of Test Method | Determination of industry test methods that can be applied to the detailed product
Setup & Instrumentation | Space for instrumentation information and sensor placement descriptions
NEMA MG 1-2016 | Detailed method of testing and calculations relating to industry standard NEMA MG 1-2016
CSA C390-10 | Efficiency calculations for motors tested in accordance with CSA C390-10
IEC 60034-2-1 Method 2-1-1A | Efficiency calculations for motors tested in accordance with IEC 60034-2-1 Method 2-1-1A
IEC 60034-2-1 Method 2-1-1B | Efficiency calculations for motors tested in accordance with IEC 60034-2-1 Method 2-1-1B
IEEE 112-2017 Method A | Efficiency calculations for motors tested in accordance with IEEE 112-2017 Method A
IEEE 112-2017 Method B | Efficiency calculations for motors tested in accordance with IEEE 112-2017 Method B
IEEE 114-2010 | Efficiency calculations for motors tested in accordance with IEEE 114-2010
CSA C747-09 | Efficiency calculations for motors tested in accordance with CSA C747-09
IEC 61800-9-2 | Efficiency calculations for motors tested in accordance with IEC 61800-9-2
Photos | Inputs for photographs
Comments | Inputs for report template user to provide comments
Report Sign-off Block | Report approval and revision history
Drop-downs | Drop-downs used
Version Control | Revision history
LEGEND
Tabs | Tabs with input cells
Tabs with space to paste raw data
Cells | Input data
Auto-populated cell
Provided data
NOT USED
Instructions for Completing this Template
Follow the steps below, filling in all input cells (shaded light blue) in each tab you are instructed to complete. Using TAB to "hop" from input cell to input cell is useful, but does not ensure that all input cells are reached. To guarantee that you enter all required information, you must visually scan for light blue cells in the entire area bounded by yellow-shaded cells.
Important: Start with a clean (unused) template copy for each new report. Enter only data and information that are unique to the unit tested and the current test of that unit. All abbreviations and variable names should be consistent with the reference test procedure.
STEP: | FILL IN INPUT CELLS IN THIS TAB:
Step 1 | General Info & Test Results
Step 2 | Determination of Test Method
Step 3 | Setup & Instrumentation
Step 4a (dependent on step 3) | NEMA MG 1-2016
Step 4b (dependent on step 3) | CSA C390-10
Step 4c (dependent on step 3) | IEC 60034-2-1 Method 2-1-1A
Step 4d (dependent on step 3) | IEC 60034-2-1 Method 2-1-1B
Step 4e (dependent on step 3) | IEEE 112-2017 Method A
Step 4f (dependent on step 3) | IEEE 112-2017 Method B
Step 4g (dependent on step 3) | IEEE 114-2010
Step 4h (dependent on step 3) | CSA C747-09
Step 4i (dependent on step 3) | IEC 61800-9-2
Step 5 | Photos
Step 6 | Comments
Step 7 | Report Sign-off Block

## General Info & Test Results
Title Block |  | Back to Instructions tab
Test Report Template Name: | Electric Motors
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | General Info & Test Results
File Name: | Electric Motors - v1.0.xlsx
Test Start Date: | [MM/DD/YYYY]
Test Completion Date: | [MM/DD/YYYY]
Lab Information |  | Test Results
Lab Name: |  | Industry load method used
Lab Location:
|  | Percentage of Rated Load (%) | Efficiency (%)
Test Information
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
Product Information
Manufacturer:
Brand:
Manufacturer Model Number:
Serial Number:
Date Manufactured: | [MM/DD/YYYY]
Date Product Received: | [MM/DD/YYYY] | NOTE: Copy only; sign off is done in the Report Sign-Off Block tab
Condition as Received: |  | Test Report Sign-Off Block
We certify that the information and data in this report: (1) were obtained from the specific test unit under test; (2) were obtained during the specific test being reported; (3) were not copied from any other source, except where instructed to do so; and (4) were not altered or modified in any way.
Product Characteristics
Product Design |  | Role |  | Date | Entity
EM Variety (if applicable) |  | Test Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Speed Configuration |  | Template Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Rotor Type |  | Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Duty Type |  | Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Frame size
Performance requirement met
Inverter Capabilities
Capacitor Configuration
Conductor Material
Additional Design Options
Is there a single or double shaft extension?
Is there a non-standard endshield or flange?
Are there non-standard bases, feet, or mounting?
Is there a separately powered blower?
Is this a vertical EM or have bearings incapable of horizontal operation?
Electrical info
Rated Load (hp)
Rated Voltage (V)
Rated Frequency (Hz)
Nameplate speed (rpm)
Phase Configuration
Pole Configuration (number of poles)
Power Supply Type
Current Waveform
Synchronous Speed (rpm)
Inverter info (if applicable)
Is this inverter listed as recommended in manufacturer catalog?
Inverter Efficiency (%)
Switching Frequency (Hz)
Max Frequency (Hz)
Operating Phase
Max Output Voltage (V)
Motor Control Method
Load Profile Setting
Saving Energy Mode (if used)
Manufacturer
Brand
Model Number

## Determination of Test Method
Title Block |  |  | Back to Instructions tab
Test Report Template Name: | Electric Motors
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | Determination of Test Method
File Name: | Electric Motors - v1.0.xlsx
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
Determination of Industry Test Procedure Used
Please complete product information reporting in the "General Info & Test Results" tab of this document before referring below. 10 CFR Part 431 Subpart B appoints applicable industry standards that may be utilized during testing to Electric Motors with various characteristics. The purpose of this portion of the template is to indicate which industry procedures may be used based on the given product information specified. Note that if multiple procedures are indicated, only one of the tests needs to be completed. After identifying the industry test procedure being used, please refer to the sheet in this document matching the industry title, and note any applicable set-up instructions below.
Additional Determinations
Is this a polyphase EM? | No
Does performance design meet criteria in 431.25(g)? | No
Does frame size meet criteria in 431.25(g)? | No
Do electric requirements meet criteria in 431.25(g)? | No
Does frame size meet ESEM definition? | No
Is this an ESEM? | No | NOTE: The term "ESEM" refers to equipment formally named "SNEM" in 10 CFR Part 431
Does this EM meet the criteria in 431.25(g)? | No
Applicable test case (internal) | N/A
Permissible industry test procedures | More product information needed for determination
Additional setup information (if applicable) | N/A
Test Procedure being Used

## Setup & Instrumentation
Title Block
Test Report Template Name: | Electric Motors
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | Setup & Instrumentation
File Name: | Electric Motors - v1.0.xlsx
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
Test Setup 1. This table must include all instrumentation, sensors, and equipment used during testing. 2. Entries may be added or deleted as needed depending on the industry test method used. 3. Refer to each industry document for more details on instrument requirements.
Instrument Type | Brand | Model # | Sensor Location | Accuracy | Date of Last Calibration | Deadline for Next Calibration
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[5 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]

## NEMA MG 1-2016
Title Block |  |  | Back to Instructions tab
Test Report Template Name: | Electric Motors
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | NEMA MG 1-2016
File Name: | Electric Motors - v1.0.xlsx
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
Test Procedure Description
NEMA MG 1-2016 incorporates multiple industry standards by reference to provide further inform testing. Refer below and test according to one of the applicable test procedures. When testing air-over electric motors, further temperature testing is needed before referring to applicable test standards for load testing.
Determination of Test Procedure
Motor Characteristic | Value
EM Variety | 0
Motor Phase | 0
Rotor Type | 0
Rated Load (hp) | 0
Conductor Material | 0
k constant value | Winding material needed
Capacitor Configuration | 0
Is this a vertical motor? | 0
Applicable Test Procedure | Motor information needed
Determination of Target Temperature
Indication of Motor Temperature Rise
Description | Value
Temperature Rise (˚C)
Ambient Temperature (˚C)
Insulation Class
Target Temperature (˚C) | Fill in above
Temperature Testing
Location of temperature detectors
Motor at ambient temperature (25˚C)
Description | Value
Detector Reading (˚C)
Motor Winding Resistance (Ω)
Motor at rated load with air flow provided by an external blower
Description | Value | Reading within tolerance?
Highest Detector Reading (˚C) |  | #VALUE!
Immediately after shutting down motor and blower
Description | Value
Motor Winding Resistance (Ω)
Detector Reading (˚C)
Average Winding Temperature (˚C) | #DIV/0!
Is average winding temperature within 10˚C of target? | #VALUE!
Ratio (Average winding temp/highest detector reading) | #DIV/0!
Perform temperature tests above first
Description | Value
Highest Detector Reading (˚C)
Is tolerance met? | #VALUE!
Load Test
Perform the load test to any of the following test standards with the external blower configured exactly as it was at the conclusion of the temperature test:
IEEE 112 Method B
IEEE 114
CSA C390
CSA C747
IEC 60034-2-1 Method 2-1-1B
The average winding temperature must be within 10 ˚C of the target temperature determined in cell C34.
Load Test Used

## CSA C390-10
Title Block |  |  |  |  | Back to Instructions tab
Test Report Template Name: | Electric Motors
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | CSA C390-10
File Name: | Electric Motors - v1.0.xlsx
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
Instrumentation Requirements
Before proceeding, please ensure the information regarding test equipment has been reported in the "Setup & Instrumentation" tab of this document. Verify the following: Instruments shall be accompanied by a calibration record performed within 12 months of testing, and limiting error shall be within ±0.2% of full scale when testing for efficiency. Errors relating to instrument transformers shall be within ±0.3% of full scale. Instruments used for power measurement shall be selected at a power factor of 1.0, and shall be calibrated over the range of intended use, including measurements from 0.1 to 1.0 power factor. If a dynamometer is used, the coupling, friction, and windage load shall not be greater than 15% of the rated output of the motor. The errors of the instrumentation used to measure torque shall be within ±0.2% of full scale. Power shall have a maximum uncertainty of ±1.0%. Voltage and current shall have a maximum uncertainty of ±0.5%. Torque shall have a maximum uncertainty of ±0.7%. Temperature shall have a maximum uncertainty of ±1.5 °C. Winding resistance shall have a maximum uncertainty of ±1%. A four-wire measuring circuit shall be used to eliminate errors from test lead resistance. Motor speed shall have a maximum uncertainty of ±1 rpm.
Has instrumentation data been reported and does it meet conditions above?
Test Procedure Description
The test procedure in CSA C390-10 utilizes an input-output efficiency calculation approach with indirect measurement of the stray-load loss and direct measurement of the stator winding, rotor winding, core, and windage-friction losses.
Relevant Motor Characteristics
Description | Value
Rated Load (hp) | 0
Rated Frequency (Hz) | 0
Rated Voltage (V) | 0
Number of poles | 0
Winding Material Used | 0
k value | Winding material needed
Cold Temperature Test
When the motor winding, stator core, or frame temperature is within 3°C of ambient temperature, record the following:
Description | Value
Cold winding temperature (°C)
Cold motor stator winding resistance (Ω)
Heat-run test
Establish thermal equilibrium at rated voltage, frequency, and no less than full-load, then disconnect power and allow the motor to stop and record the following within the maximum allowable time delay:
Description | Value
Maximum allowed time delay (sec) | Provide rated hp
Actual time delay (sec)
Stator Winding Resistance (Ω)
Stator Winding Temperature (°C)
Ambient Temperature (°C)
Winding temp after equilibrium (°C)
Temperature rise by resistance (°C)
Corrected Winding Resistance Ambient (Ω)
Load test - Apply rated voltage and frequency
Load Point Index | Percentage of Rated Load (%) | Targeted Load Range (%)
1 |  | 125-115
2 |  | 114-100
3 |  | 99-85
4 |  | 84-50
5 |  | 49-35
6 |  | 34-20
Load Point Index
Description | 1 | 2 | 3 | 4 | 5 | 6
Torque (N*m)
Power input (kW)
Line a Current (A)
Line b Current (A)
Line c Current (A)
Speed (rpm)
Winding Temperature (°C)
Ambient temperature (°C)
Line a-b Voltage (V)
Line b-c Voltage (V)
Line c-a Voltage (V)
Frequency (Hz)
Total Harmonic Distortion (%)
Average Line Curent (A) | 0 | 0 | 0 | 0 | 0 | 0
Average Line Voltage (V) | 0 | 0 | 0 | 0 | 0 | 0
Voltage Unbalance (%)
Frequency Variation (%)
Corrected Torque (N*m) | 0 | 0 | 0 | 0 | 0 | 0
Torque2 (N2*m2) | 0 | 0 | 0 | 0 | 0 | 0
Corrected Voltage (V)
Corrected winding temperature (°C)
Corrected winding resistance (Ω)
cos φ
sin φ
Core and winding friction correction (kW)
Permissibility of Power Supply: | Data is permissible - may proceed with testing
Calculations
Load Point Index
Description | 1 | 2 | 3 | 4 | 5 | 6
Stator Winding Loss (kW)
Synchronous Speed
Slip
Core Loss (kW)
Rotor Winding Loss (kW)
Outlet Power (kW) | 0 | 0 | 0 | 0 | 0 | 0
Residual Power (kW)
Stray Load Loss (kW)
Corrected Stator Winding Loss (kW)
Slip Corrected to Ambient
Corrected Rotor Winding Loss (kW)
Corrected power Output (kW)
Efficiency (%)
Linear Regression Data (Residual Power vs. Torque2)
Slope
Intercept
Correlation Coefficient
Satisfactory? | Yes
Load Point index deleted (if applicable)
No-load test - Establish power stabilization and apply rated frequency at no-load
No-Load Index | Percentage of Nominal Voltage (%) | Targeted Voltage Range (%)
1 |  | 125-115
2 |  | 114-100
3 |  | 99-85
4 |  | 84-50
5 |  | 49-35
6 |  | 34-20
No-Load Index
Description | 1 | 2 | 3 | 4 | 5 | 6
Line a-b Voltage (V)
Line b-c Voltage (V)
Line c-a Voltage (V)
Line a Current (A)
Line b Current (A)
Line c Current (A)
Frequency, (Hz)
Power input, (kW)
Winding temperature, (°C)
Total Harmonic Distortion (%)
Average Voltage (V) | 0 | 0 | 0 | 0 | 0 | 0
Average Current (A) | 0 | 0 | 0 | 0 | 0 | 0
Voltage Unbalance (%)
Frequency Variation (%)
Permissibility of Power Supply: | Data is permissible - may proceed with testing
Stator core and windage-friction losses
Description | Value
Slope - temp device vs resistance
Intercept - temp device vs resistance
Slope - resistance temp vs resistance
Intercept - resistance temp vs resistance
No-Load Index
Description | 1 | 2 | 3 | 4 | 5 | 6
Corrected winding temp (°C)
Corrected winding resistance (Ω)
Stator Winding loss (kW)
Core and winding friction correction (kW)
Average Voltage2 (V2) | 0 | 0 | 0 | 0 | 0 | 0
Core Losses (kW)
Linear Regression Data (Core and winding loss vs. Voltage2)
Windage-Friction Loss (kW)
Correlation Coefficient
Correlation passed? | Yes
Dynamometer Correction
Is the dynamometer correction necessary?
Test Index | Test Condition Details
A | Operate the motor coupled to the dynamometer, with the dynamometer not loaded.
B | Run the motor uncoupled from the dynamometer.
Test Index
Data Observed | A | B
Power input (kW)
Line a Current (A)
Line b Current (A)
Line c Current (A)
Winding Temperature (°C)
Ambient Temperature (°C)
Line a-b Voltage (V)
Line b-c Voltage (V)
Line c-a Voltage (V)
Total Harmonic Distortion (%)
Frequency (Hz)
Rotational speed (rpm)
Torque Output (N*m)
Average Voltage (V) | 0 | 0
Average Current (A) | 0 | 0
Voltage Unbalance (%)
Frequency Variation (%)
Permissibility of Power Supply: | Data is permissible - may proceed with testing
Calculations
Description | Value
Synchronous Speed (rpm)
Speed (p.u.)
Corrected Winding Temperature Test A
Corrected Winding Resistance Test A
Stator Loss Test A (kW)
Corrected Winding Temperature Test B
Corrected Winding Resistance Test B
Stator Loss Test B (kW)
Core Loss at Rated V (kW)
Dynamometer Correction Factor (N*m) | 0

## IEC 60034-2-1 Method 2-1-1A
Title Block |  |  | Back to Instructions tab
Test Report Template Name: | Electric Motors
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | IEC 60034-2-1 Method 2-1-1A
File Name: | Electric Motors - v1.0.xlsx
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
Instrumentation Requirements
Before proceeding, please ensure the information regarding test equipment has been reported in the "Setup & Instrumentation" tab of this document. Verify the following: For analog instruments the observed values should be in the upper third of the instrument range. The measuring instruments shall have the equivalent of an accuracy class of 0.2 in case of a direct test and 0.5 in case of an indirect test. The measuring equipment shall reach an overall uncertainty of 0.2 % of reading at power factor 1.0 and shall include all errors of instrument transformers or transducers, if used The instrumentation used to measure the torque shall have a minimum class of 0.2. The minimum torque measured shall be at least 10% of the torque meter’s nominal torque. The instrumentation used to measure supply frequency shall have an accuracy of ±0.1 % of full scale. The speed measurement should be accurate within 0.1 rpm. The instrumentation used to measure temperatures shall have an accuracy of ±1 K.
Has instrumentation data been reported and does it meet conditions above?
Test Procedure Description
Method 2-1-1A of IEC 60034-2-1 utilizes direct measurements of input and output to determine efficiency. The mechanical power of a machine as well as the electrical power of the stator are determined in the same test by measuring the shaft torque and speed at thermal equilibrium.
Relevant Motor Characteristics
Description | Value
Rated Load (W) | 0
Test Procedure Measurements - couple the machine to a load machine and operate at rated load until thermal equilibrium (< = 1 K / 30min) is achieved
Description | Value
Average Terminal Voltage (V)
Average Line Current (A)
Input Power (W)
Operating Speed (1/s)
Torque (N*m) |  | Use in-line, shaft-coupled, rotating torque transducer or stationary stator reaction torque transducer
Primary coolant inlet temperature (˚C)
Efficiency (%)
40% | 30%
???? | ????
40% | 30%
#VALUE! | #VALUE!
#VALUE! | #VALUE!

## IEC 60034-2-1 Method 2-1-1B
Title Block |  |  |  |  | Back to Instructions tab
Test Report Template Name: | Electric Motors
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | IEC 60034-2-1 Method 2-1-1B
File Name: | Electric Motors - v1.0.xlsx
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
Instrumentation Requirements
Before proceeding, please ensure the information regarding test equipment has been reported in the "Setup & Instrumentation" tab of this document. Verify the following: For analog instruments the observed values should be in the upper third of the instrument range. The measuring instruments shall have the equivalent of an accuracy class of 0.2 in case of a direct test and 0.5 in case of an indirect test. The measuring equipment shall reach an overall uncertainty of 0.2 % of reading at power factor 1.0 and shall include all errors of instrument transformers or transducers, if used The instrumentation used to measure the torque shall have a minimum class of 0.2. The minimum torque measured shall be at least 10% of the torque meter’s nominal torque. The instrumentation used to measure supply frequency shall have an accuracy of ±0.1 % of full scale. The speed measurement should be accurate within 0.1 rpm. The instrumentation used to measure temperatures shall have an accuracy of ±1 K.
Has instrumentation data been reported and does it meet conditions above?
Test Procedure Description
Method 2-1-1B of IEC 60034-2-1 utilizes a summation of losses approach to determine efficiency. Separate loss components due to windage and friction, stator and rotor copper, as well as iron, and additional losses are determined to calculate the total losses through varying loads.
Relevant Motor Characteristics
Description | Value
Rated Load (hp) | 0
Number of Poles | 0
Ambient Temperature Measurements
Description | Value
Ambient Temperature (˚C)
Ambient Winding Resistance (Ω)
Rated Load Test
Description | Value
Input Power (W)
Torque (N*m)
Current (A)
Voltage (V)
Operating Speed (1/s)
Frequency (Hz)
Primary Coolant Inlet Temp (˚C)
Winding temperature (˚C)
Test Resistance (Ω)
Uncorrected stator-winding losses (W) | 0
Temperature correction factor | 1.1064
Corrected stator-winding losses (W) | 0
Slip (sec)
Corrected Slip (sec)
Uncorrected rotor winding losses (W)
Corrected rotor winding losses (W)
Corrected input power (W)
Load curve test
Load Point Index | Percentage of Rated Load (%) | Targeted Rated Load (%)
1 |  | 125%
2 |  | 115%
3 |  | 100%
4 |  | 75%
5 |  | 50%
6 |  | 25%
Load Point Index
Description | 1 | 2 | 3 | 4 | 5 | 6
Average Terminal Voltage (V)
Average Line Current (A)
Input Power (W)
Operating Speed (rpm)
Supply Frequency (Hz)
Machine Torque (N*m)
Winding Resistance (Ω)
Uncorrected stator-winding losses (W) | 0 | 0 | 0 | 0 | 0 | 0
Slip (sec)
Uncorrected rotor-winding losses (W)
Iron Losses (W)
Frequency Variation (%)
Permissibility of Power Supply: | Data is permissible - may proceed with testing
No-load test
Description | Value
Resistance immediately before test (Ω)
No-Load Index | Percentage of Rated Voltage? (%) | Targeted Rated Voltage? (%)
1 |  | 110%
2 |  | 100%
3 |  | 95%
4 |  | 90%
5 |  | 60% |  | Referenced in Interpolation (Internal)
6 |  | 50% |  | Input Power (W) | Winding Resistance (Ω)
7 |  | 40% |  | 0 | 0
8 |  | 30% |  | 0 | 0
No-Load Index
Description | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Input power at no-load (W)
Terminal Voltage (V)
Voltage Squared (V2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interpolated Winding Resistance (Ω)
Stator-winding losses at no load (W)
Constant losses (W)
Iron Losses over no-load (W)
Description | Value
Resistance immediately after test (Ω)
Friction and windage losses (W)
Full Load Losses
Description | Value
cos(ϕ)
sin(ϕ)
Inner voltage (V)
Full Load Iron Losses (W)
Additional Load Losses
Load Point Index
Description | 1 | 2 | 3 | 4 | 5 | 6
Output Power (W) | 0 | 0 | 0 | 0 | 0 | 0
Corrected Friction and Windage Losses (W)
Residual losses (W)
Smoothing of the residual loss data
Load Point Index
Description | 1 | 2 | 3 | 4 | 5 | 6
Torque2 (N*m2) | 0 | 0 | 0 | 0 | 0 | 0
Additional Load Losses (W)
Description | Value
Slope
Intercept
Is intercept considerably small?
Correlation coefficient
Correlation coefficient sufficient? | Yes
Load point index deleted (if applicable)
Efficiency determination
Load Point Index
Description | 1 | 2 | 3 | 4 | 5 | 6
Total Losses (W)
Efficiency (%)

## IEEE 112-2017 Method A
Title Block |  |  |  |  | Back to Instructions tab
Test Report Template Name: | Electric Motors
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | IEEE 112-2017 Method A
File Name: | Electric Motors - v1.0.xlsx
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
Instrumentation Requirements
Before proceeding, please ensure the information regarding test equipment has been reported in the "Setup & Instrumentation" tab of this document. Verify the following: Instruments indication of limits of error shall be within ±0.2% of full scale. The total error for current measurements shall not exceed ±0.5% of the full-load reading, including all errors from the ammeter and CTs. The total error for power measurements shall not exceed ±1.0% of the full-load reading, including all errors from the wattmeter, CTs, and VTs. The errors of the transformers used shall not be greater than ±0.5%. The instrument used to measure frequency shall have an accuracy of ±0.05%. The instruments shall bear record of calibration, within 12 months of the test, indicating limits of the error no greater than ±0.2% of full scale. If used, the dynamometer should be sensitive to a change of torque of 0.25% of the rated torque. Total error for torque measurements shall not exceed ±0.7%, which shall include all errors from all sources. For measurements for which the speed is less than or equal to 1800 rpm, the total error of the instrumentation used for speed or slip measurements shall not exceed ±1.0 rpm. For measurements for which the speed is greater than 1800 rpm, the total error for speed measurements shall not exceed ±(0.1 rpm + 0.05% of the reading). Slip measurements shall not exceed a value equivalent to ±(0.1 rpm + 0.05% of [synchronous rpm – slip rpm]).
Has instrumentation data been reported and does it meet conditions above?
Test Procedure Description
Method A of IEEE 112-2017 calculates electric motor efficiency as a ratio of measured output power to measured input power, after applying temperature and dynamometer corrections as needed.
Relevant Motor Characteristics
Description | Value
Rated Voltage (V) | 0
Synchronous speed (rpm) | 0
Rated Frequency (Hz) | 0
Rated Load (W) | 0
Conductor Material | 0
k value | Winding material needed
Ambient ("cold") Temperature Data
Description | Value
Ambient Temperature (˚C)
Stator winding resistance, Rc (Ω)
Rated ("hot") Load Temperature Test - not required if previously performed on a duplicate machine
Is duplicate data being used?
Description | Value
Stator winding resistance, Rh (Ω)
Ambient Temperature (˚C)
Rated Load Temperature (˚C)
Temperature Rise by Resistance (˚C)
Specified Temperature, ts (˚C) | 0
Specified Temperature from duplicate, ts (˚C)
Load Testing - Test from highest to lowest load
Load Point Index | Percentage of Rated Load (%) | Targeted Load Range (%)
1 |  | 100-150
2 |  | 100-150
3 |  | 25-100
4 |  | 25-100
5 |  | 25-100
6 |  | 25-100
Load Point Index
Description | 1 | 2 | 3 | 4 | 5 | 6
Stator winding temp, tt (˚C)
Ambient Temperature (˚C)
Average Terminal Voltage (V)
Frequency (Hz)
Torque (N*m)
Average Line Current (A)
Stator power (W)
Observed Speed (rpm)
Total Harmonic Distortion (%)
Voltage Unbalance (%)
Variation from Average Frequency (%)
Observed Slip (rpm) | 0 | 0 | 0 | 0 | 0 | 0
Observed Slip (p.u.)
Corrected Slip (p.u.)
Corrected Speed (rpm)
Corrected Torque (N*m) | 0 | 0 | 0 | 0 | 0 | 0
Shaft Power (W)
Stator I2R Loss at tt (W)
Winding resistance at ts (Ω)
Stator I2R Loss at ts (W)
Stator Power Correction (W)
Corrected stator power (W)
Efficiency (%)
Power Factor (%)
Permissibility of Power Supply: | Data is permissible - may proceed with testing
Dynamometer Correction
Is a dynamometer correction required?
No-Load Test
Establish stability and run motor at rated voltage and frequency with no connected load record the following
Description | Value
Temperature (˚C)
Average Line Current (A)
Input Power (W)
Establish stability and test the following voltage points without increasing current
No-Load Index | Percentage of Rated Voltage (%) | Targeted Voltage Range (%)
1 |  | 100-125
2 |  | 100
3 |  | 75-100
4 |  | 20-50
5 |  | 20-50
6 |  | 20-50
No-Load Index
Data Observed | 1 | 2 | 3 | 4 | 5 | 6
Temperature (˚C)
Average Terminal Voltage (V)
Average Line Current (A)
Power input (W)
Frequency (Hz)
Total Harmonic Distortion (%)
Voltage Unbalance (%)
Resistance between terminals (Ω)
Stator I2R (W)
Total loss - Stator I2R loss (W)
Core Loss (W)
Variation from Average Frequency (%)
Average test frequency (Hz)
Variation from rated (%)
Data Permissibility: | Data is permissible - may proceed with testing
Analysis
Description | Value
Friction and Windage Loss (W)
Core Loss at Rated Voltage, Ph (W)
Correction
Test Index | Test Condition Details
A | Operate motor at rated voltage while coupled to the dynamometer with all electrical power removed from the dynamometer.
B | Uncouple the motor from the dynamometer and operate at no load at rated voltage.
Test Index
Data Observed | A | B
Electrical Input Power (W)
Line-to-line Voltage (V)
Line Current (A)
Stator winding resistance (Ω)
Slip (p.u.)
Speed (rpm)
Torque (N*m)
Calculations
Description | Value
Stator I2R Loss Test A (W) | 0
Stator I2R Loss Test B (W) | 0
Core Loss (W)
Associated Power Test A (W)
Associated Power Test B (W)
Torque correction of dynamometer (N*m) | 0

## IEEE 112-2017 Method B
Title Block |  |  |  |  | Back to Instructions tab
Test Report Template Name: | Electric Motors
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | IEEE 112-2017 Method B
File Name: | Electric Motors - v1.0.xlsx
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
Instrumentation Requirements
Before proceeding, please ensure the information regarding test equipment has been reported in the "Setup & Instrumentation" tab of this document. Verify the following: Instruments indication of limits of error shall be within ±0.2% of full scale. The total error for current measurements shall not exceed ±0.5% of the full-load reading, including all errors from the ammeter and CTs. The total error for power measurements shall not exceed ±1.0% of the full-load reading, including all errors from the wattmeter, CTs, and VTs. The errors of the transformers used shall be within ±0.3%. When instrument transformers and instruments for measuring voltage, current, or power are calibrated as a system, the system errors shall be ±0.2% of full scale. The instrument used to measure frequency shall have an accuracy of ±0.05%. The instruments shall bear record of calibration, within 12 months of the test, indicating limits of the error no greater than ±0.2% of full scale. If used, the dynamometer should be sensitive to a change of torque of 0.25% of the rated torque. Total error for torque measurements shall not exceed ±0.7%, which shall include all errors from all sources. For measurements for which the speed is less than or equal to 1800 rpm, the total error of the instrumentation used for speed or slip measurements shall not exceed ±1.0 rpm. For measurements for which the speed is greater than 1800 rpm, the total error for speed measurements shall not exceed ±(0.1 rpm + 0.05% of the reading). Slip measurements shall not exceed a value equivalent to ±(0.1 rpm + 0.05% of [synchronous rpm – slip rpm]).
Has instrumentation data been reported and does it meet conditions above?
Test Procedure Description
Method B of IEEE 112-2017 utilizes an input output approach with loss segregation to determine electric motor efficiency. The apparent total loss is segregated into its various components with stray-load loss defined as the difference between the apparent total loss and the sum of the conventional losses. A linear regression analysis of stray-load loss against torque squared is then used to calculate final value of total loss and efficiency.
Relevant Motor Characteristics
Description | Value
Rated Frequency (Hz) | 0
Rated Load (W) | 0
Number of poles | 0
Conductor Material | 0
k value | Winding material needed
Ambient ("cold") Temperature Data
Description | Value
Ambient Temperature (˚C)
Stator Winding Resistance, Rc (Ω)
Rated ("hot") Load Temperature Test - not required if previously performed on a duplicate machine
Is duplicate data being used?
Description | Value
Stator Winding Resistance, Rh (Ω)
Ambient Temperature (˚C)
Rated Load Temperature (˚C)
Temperature Rise by Resistance (˚C)
Specified Temperature, ts (˚C) | 0
Specified Temperature from duplicate, ts (˚C)
No-Load Test
Establish stability and run motor at rated voltage and frequency with no connected load record the following
Description | Value
Temperature (˚C)
Average Line Current (A)
Input Power (W)
Establish stability and test the following from highest to lowest voltage without increasing current
No-Load Index | Percentage of Rated Voltage | Targeted Voltage Range (%)
1 |  | 100-125
2 |  | 100
3 |  | 75-100
4 |  | 20-50
5 |  | 20-50
6 |  | 20-50
No-Load Index
Data Observed | 1 | 2 | 3 | 4 | 5 | 6
Temperature (˚C)
Average Terminal Voltage (V)
Average Line Current (A)
Power input (W)
Frequency (Hz)
Total Harmonic Distortion (%)
Voltage Unbalance (%)
Resistance between terminals (Ω)
Stator I2R (W)
Total loss - Stator I2R loss (W)
Core Loss (W)
Variation from Average Frequency (%)
Average test frequency (Hz)
Variation from rated (%)
Data Permissibility: | Data is permissible - may proceed with testing
Analysis
Description | Value
Friction and Windage Loss (W)
Core Loss at Rated Voltage, Ph (W)
Load Testing - Test the following points from highest to lowest load
Load Point Index | Percentage of Rated Load | Targeted Load Range (%)
1 |  | 100-150
2 |  | 100-150
3 |  | 25-100
4 |  | 25-100
5 |  | 25-100
6 |  | 25-100
Load Point Index
Data Observed | 1 | 2 | 3 | 4 | 5 | 6
Stator winding temp, tt (˚C)
Ambient Temperature (˚C)
Frequency (Hz)
Average Terminal Voltage (V)
Torque (N*m)
Average Line Current (A)
Stator power (W)
Speed (rpm)
Average winding resistance (Ω)
Total Harmonic Distortion (%)
Voltage Unbalance (%)
Variation from Average Frequency (%)
Data Permissibility: | Data is permissible - may proceed with testing
Dynamometer Correction
Is a dynamometer correction required?
Test Index | Test Condition Details
A | Operate motor at rated voltage while coupled to the dynamometer with all electrical power removed from the dynamometer.
B | Uncouple the motor from the dynamometer and operate at no load at rated voltage.
Test Index
Data Observed | A | B
Electrical Input Power (W)
Line-to-line Voltage (V)
Line Current (A)
Stator winding resistance (Ω)
Slip (p.u.)
Speed (rpm)
Torque (N*m)
Calculations
Description | Value
Stator I2R Loss Test A (W) | 0
Stator I2R Loss Test B (W) | 0
Core Loss, Ph (W)
Associated Power Test A (W)
Associated Power Test B (W)
Torque correction of dynamometer (N*m) | 0
Calculated Data
Load Point Index
Description | 1 | 2 | 3 | 4 | 5 | 6
Synchronous Speed (rpm)
Slip Speed (rpm)
Slip (p.u.)
Stator core voltage (V)
Core Loss (W)
Stator I2R loss (W) | 0 | 0 | 0 | 0 | 0 | 0
Power across air gap (W)
Rotor I2R Loss (W)
Friction and Windage loss (W) | 0 | 0 | 0 | 0 | 0 | 0
Total convention loss (W)
Corrected Torque (N*m) | 0 | 0 | 0 | 0 | 0 | 0
Shaft Power (W) | 0 | 0 | 0 | 0 | 0 | 0
Apparent total Loss (W) | 0 | 0 | 0 | 0 | 0 | 0
Stray load loss (W)
Stator I2R loss at ts (W)
Corrected power across air gap (W)
Corrected slip (p.u.)
Corrected Speed (rpm)
Corrected Rotor I2R Loss at ts (W)
Corrected stray load loss (W)
Corrected total loss (W)
Corrected shaft power (W)
Efficiency (%)
Power Factor (%)
Linear Regression Analysis
Load Point Index
Data | 1 | 2 | 3 | 4 | 5 | 6
Stray Load Loss
Torque Squared | 0 | 0 | 0 | 0 | 0 | 0
Intercept
Slope
Correlation Factor
Does worst data point need to be deleted? | No
Load point index deleted (if applicable)

## IEEE 114-2010
Title Block |  |  | Back to Instructions tab
Test Report Template Name: | Electric Motors
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | IEEE 114-2010
File Name: | Electric Motors - v1.0.xlsx
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
Instrumentation Requirements
Before proceeding, please ensure the information regarding test equipment has been reported in the "Setup & Instrumentation" tab of this document. Verify the following: The indicating instruments shall bear record of calibration, within the previous 12 months, indicating limits of the error no greater than ± 0.2% of full scale for determination of efficiency. The errors of the instrument transformers used shall not be greater the 0.3%. The dynamometer used should be sensitive to a change in torque of 0.1% of the rated torque.
Has instrumentation data been reported and does it meet conditions above?
Test Procedure Description
IEEE 114-2010 determines the efficiency of an electric motor using the ratio of measured output power to corrected input power. Applicable corrections for ambient temperature and dynamometer usage are made to measured input power and determined losses as needed.
Relevant Motor Characteristics
Description | Value
Nameplate Speed (rpm) | 0
Rated Load (W) | 0
Number of poles | 0
Synchronous Speed (rpm) | 0
Rated Motor Torque (N*m)
Conductor Material | 0
k constant value | Winding material needed
Initial Data Collection
Ambient ("Cold") Temperature Run - Reference ambient temperature of 25 °C
Description | Value
Cold Motor Winding Temp (˚C)
Motor Winding Resistance (Ω)
Ambient Temperature (˚C) |  | Ambient Temperature of test shall not be less than 10°C or greater than 40°C
Full Load ("Hot") Temperature Run - Stabilize motor at rated V and Hz, take data within 30 seconds of shutdown
Description | Value
Motor Winding Temperature (˚C)
Motor Winding Resistance (Ω)
Ambient Temperature (˚C) |  | Ambient Temperature of test shall not be less than 10°C or greater than 40°C
Calculations
Description | Value
Specified Temperature (˚C)
Temperature Rise as Measured (˚C) | 0
Temperature Rise by Resistance (˚C)
Load Point Testing
Load Point Index | Percentage of Rated Load (%) | Targeted Load Range (%)
1 |  | 125-150
2 |  | 115
3 |  | 100
4 |  | 75
5 |  | 50
6 |  | 25
Load Point Index
Data Observed | 1 | 2 | 3 | 4 | 5 | 6
Ambient Temperature (˚C)
Stator Main Winding Temp, tt (˚C)
Frequency (Hz)
Slip Speed (rpm)
Corrected Slip Speed (rpm)
Speed (rpm)
Torque (N*m)
Corrected Torque (N*m) | 0 | 0 | 0 | 0 | 0 | 0
Output Power (W)
Voltage (V)
Stator Current (A)
Input Power (W)
Stator resistance at tt (Ω)
Stator resistive loss at tt (W)
Stator resistance at ts (Ω)
Stator resistive loss at ts (W)
Input Power Correction (W)
Corrected Input Power (W)
Power Factor (%)
Efficiency (%)
Measured Load (% of rated Torque)
Dynamometer Correction
Is a dynamometer correction required?
Test Index | Test Condition Details
A | Motor running at no load and coupled to the dynamometer
B | Motor running at no load and uncoupled from the dynamometer
C | Motor running at 25% load test point
Test Index
Data Observed | A | B | C
Motor Torque (N*m)
Input Power (W)
Calculations
Description | Value
Slope
Dynamometer Correction Factor (N*m) | 0
Validation | Test is valid

## CSA C747-09
Title Block |  |  | Back to Instructions tab
Test Report Template Name: | Electric Motors
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | CSA C747-09
File Name: | Electric Motors - v1.0.xlsx
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
Instrumentation Requirements
Before proceeding, please ensure the information regarding test equipment has been reported in the "Setup & Instrumentation" tab of this document. Verify the following: Indicating instruments shall have been calibrated over the range of their intended use within the past 12 months to limits of error no greater than ±0.2% of full-scale deflection. The ratio errors of instrument transformers shall be no greater than 0.3%. Power shall have a maximum uncertainty of ±0.5% of the reading at the full-load rating of the motor under test. Voltage and current shall have a maximum uncertainty of ±0.5% of the reading at the full-load rating. Torque shall have a maximum uncertainty of ±1.0% of the reading at the full-load. Temperature shall have a maximum uncertainty of ±1.5 °C. Motor speed (RPM) shall have a maximum uncertainty of ±0.2% of the reading.
Has instrumentation data been reported and does it meet conditions above?
Test Procedure Description
CSA C747-09 determines the energy efficiency of small direct-current and single- and three-phase alternating-current rotating motors. Efficiency for various load points is calculated using corrected output torque in relation to measured input power and motor speed.
Relevant Motor Characteristics
Description | Value
EM Variety | 0
Rated Load (kW) | 0
Nameplate Speed (rpm) | 0
Rated Voltage (V) | 0
Rated Frequency (Hz) | 0
Initial Measurements
Description | Value
Initial Torque Offset (N*m)
Full-Load Torque (N*m)
Thermal Equilibrium - At rated voltage, frequency and full-load torque
Description | Value
Ambient Temperature (˚C) |  | Please maintain ambient temperature of 20-40 ˚C
Motor Winding Temperature (˚C)
Load Testing
Conduct testing at full load first, then move in descending order to lowest desired load point. Load Points shall be substantially equally spaced. Measure and record data within 30 seconds of establishing each load point. After each measurement, return the motor to full load equilibrium unless all measurements can be made within 3 minutes.
Load Point Index | Percentage of Rated Load (%) | Targeted Load Range (%)
1 |  | 100-125
2 |  | 25-100
3 |  | 25-100
4 |  | 25-100
5 |  | 25-100
Load Point Index
Description | 1 | 2 | 3 | 4 | 5
Line Voltage (V)
Line Current (A)
Speed (rpm)
Input Power (kW)
Torque output (N*m)
Frequency (Hz)
Ambient Temperature (˚C)
Winding Temperature (˚C)
Total Harmonic Distortion (%)
Frequency Variation (%)
Permissibility of Power Supply: | Data is permissible - may proceed with testing
Additional Conditions
Motors shall also be tested at each selectable speed, voltage, or frequency. Continuously adjustable speed motors shall be tested at 75% to 50% of full speed.
Selectable Metric Used
Selection Number
Description | 1 | 2 | 3 | 4 | 5
Line Voltage (V)
Line Current (A)
Speed (rpm)
Input Power (kW)
Frequency (Hz)
Ambient Temperature (˚C)
Winding Temperature (˚C)
Total Harmonic Distortion (%)
Load Torque (N*m)
Permissibility of Power Supply: | Data is permissible - may proceed with testing
Dynamometer Correction
Is a dynamometer correction necessary?
Low Load Point - Adjust dynamometer to 10-25% rated load
Description | Value
Percentage of rated power (%)
Line Voltage (V)
Line Current (A)
Speed (rpm)
Input Power (kW)
Torque output (N*m)
Frequency (Hz)
No Load Coupled - With dynamometer coupled, reduce load to minimum dynamometer load, with motor operating at rated voltage and frequency
Description | Value
Line Voltage (V)
Line Current (A)
Speed (rpm)
Input Power (kW)
Torque output (N*m)
Frequency (Hz)
No Load Uncoupled - Immediately disconnect dynamometer and apply rated voltage and frequency
Description | Value
Percentage of rated power (%)
Line Voltage (V)
Line Current (A)
Speed (rpm)
Input Power (kW)
Frequency (Hz)
Calculations
Description | Value
Slope
Actual No Load Coupled Torque (N*m)
Dynamometer Correction Factor (N*m) | 0
Final Measurements and Calculations
Description | Value
Final Torque Offset (N*m)
Absolute Difference of Torque Offsets (N*m) | 0
Data Validation
Load Point Index
Description | 1 | 2 | 3 | 4 | 5
Efficiency (%)

## IEC 61800-9-2
Title Block
Test Report Template Name: | Electric Motors |  |  |  | Back to Instructions tab
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | IEC 61800-9-2
File Name: | Electric Motors - v1.0.xlsx
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
Instrumentation Requirements
Before proceeding, please ensure the information regarding test equipment has been reported in the "Setup & Instrumentation" tab of this document. Verify the following: The uncertainty specified by the instrument manufacturer of the power meters shall be 0.2%. The bandwidth of power meters and sensors shall be sufficiently wide to ensure an error of the total active power of less or equal to 0.3 %. Units having a power rating below 7.5 kW shall be measured with a minimum of 15m shielded cable. If the manufacturer specifies less than 15 m of maximum cable length, use the highest admissible length. Disregard for integrated power drive systems.
Has instrumentation data been reported and does it meet conditions above?
Test Procedure Description
IEC 61800-9-2 determines energy efficiency of power drive systems used for motor driven equipment utilizing an input-output determination of losses. Input power is determined based on measured voltage and current values, while output power is determined by measured torque and speed of the motor. This test procedure determines the losses at 8 required load points at varying torque and speed values.
Relevant Motor Characteristics
Description | Value
Rated Load (kW) | 0
Rated Speed (rpm) | 0
Rated Torque (N*m) | 0
Load Testing
For each load point, several measurements over a period of time (at least several slip cycles, typically 1 min to 3 min) shall be simultaneously sampled and the average of these values shall be used for the determination of losses. This table represents the average load values for each trial conducted.
Load Point Index | Targeted Torque (N*m) | Targeted Speed (rpm)
1 | 0 | 0
2 | 0 | 0
3 | 0 | 0
4 | 0 | 0
5 | 0 | 0
6 | 0 | 0
7 | 0 | 0
8 | 0 | 0
Load Point Index
Description | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Supply Voltage (V)
Input Current (A)
Frequency (Hz)
Input Power Factor (%)
Shaft Torque (N*m)
Shaft Speed (rpm)
Output Torque (N*m)
Ambient Temperature (˚C)
Crest Factor of Supply Voltage
Short Circuit Ratio
Short Circuit Ratio Condition Met? | No | No | No | No | No | No | No | No
Input Power (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Percent Rated Load (%)
Output Power (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Determined Power Losses (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Efficiency (%)
Data Permissibility | Test conditions unmet - Ensure ambient temp is within 15-30 °C, crest factor is between 1.35-1.44, and short circuit ratio is within specified range at rated output power
Note on B51: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Brian Glasser I added this to put in the summary of test results section, but does it make sense to you?

## Photos
Title Block |  | Back to Instructions tab
Test Report Template Name: | Electric Motors
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | Photos
File Name: | Electric Motors - v1.0.xlsx
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
1. Photo of nameplate displaying relevant motor ratings
2. Photo showing industry performance requirement met (if applicable)
3. Photos of the unit from all sides
4. Arrival Photos
5. Additional photos (if necessary)

## Comments
Title Block |  | Back to Instructions tab
Test Report Template Name: | Electric Motors
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | Comments
File Name: | Electric Motors - v1.0.xlsx
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
Comments

## Report Sign-Off Block
Title Block |  |  | Back to Instructions tab
Test Report Template Name: | Electric Motors
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | Report Sign-Off Block
File Name: | Electric Motors - v1.0.xlsx
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
Test Report Sign-Off Block
By signing in the space below, we certify that the information and data in this report: (1) were obtained from the specific test unit under test; (2) were obtained during the specific test being reported; (3) were not copied from any other source, except where instructed to do so; and (4) were not altered or modified in any way.
Role |  | Date | Entity
Test Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Template Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]

## Drop-downs
Title Block |  | Back to Instructions tab
Test Report Template Name: | Electric Motors
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | Drop-downs
File Name: | Electric Motors - v1.0.xlsx
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
Test_Method_Used
NEMA MG 1-2016
CSA C390-10
IEC 60034-2-1 Method 2-1-1A
IEC 60034-2-1 Method 2-1-1B
IEEE 112-2017 Method A
IEEE 112-2017 Method B
IEEE 114-2010
CSA C747-09
IEC 61800-9-2
EM_Variety
Induction
Air-over
Synchronous
Brake
Close-coupled
Immersible
Partial
None of the above
Yes_No
Yes
No
Speed_Configuration
Single-speed
Dual-speed
Multi/variable-speed
Rotor_Type
Squirrel-cage (MG1)
Cage (IEC)
Locked
Wound
Duty_Type
Continuous Duty (MG1) / Type S1 (IEC)
Other
Frame_Size
Standard Frame Size
Two-digit NEMA (or IEC equivalent)
Three-digit NEMA (or IEC equivalent)
Four-digit NEMA (or IEC equivalent)
Enclosed 56 NEMA (or IEC equivalent)
Specialized frame size
Between two consecutive NEMA frame sizes (or IEC equivalent)
Performance_Req_Met
NEMA Design A
NEMA Design B
NEMA Design C
IEC Design N
IEC Design NE
IEC Design NEY
IEC Design NY
IEC Design H
IEC Design HE
IEC Design HEY
IEC Design HY
None of the above
Inverter_Capabilities
Can operate without an inverter
Inverter-only (inverter included)
Inverter-only (inverter not included)
Motor_Phase
Single-phase
Two-phase
Three-phase
Pole_Configuration
2
4
6
8
10
Other
Supply_Type
Direct-current
Alternating-current
Rated_Frequency
50
60
Other
Current_Waveform
Sinusoidal
Other
Conductor_Material
Aluminum
Copper
Capacitor_Configuration
Capacitor-Start Induction-Run
Capacitor-Start Capacitor-Run
Permanent Split Capacitor
N/A
Indication_MotorTempRise
Indicated numerically
Indicated by insulation class
Not indicated
Insulation_Class
A
B
F
H
Sensor_Location
On winding
On stator iron
CSA_Selectable_Metric
Speed
Voltage
Frequency
None

## Version Control
Title Block |  | Back to Instructions tab
Test Report Template Name: | Electric Motors
Version Number: | v1.0
Latest Template Revision: | 2024-10-02
Tab Name: | Version Control
File Name: | Electric Motors - v1.0.xlsx
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
Revisions List
Version | Date
v1.0 | 2024-10-02