## Instructions
Title Block
Test Report Template Name: | Uninterruptible Power Supplies
Version Number: | v1.2
Latest Template Revision: | 2024-07-16
Tab Name: | Instructions
File Name: | Uninterruptible Power Supplies - v1.2.xlsx
Reference Test Procedure
Appendix Y to Subpart B of Part 430—Uniform Test Method for Measuring the Energy Consumption of Battery Chargers
Table of Contents
Tab | Contents
Instructions | Instructions and Table of Template Contents
General Info & Test Results | Lab Information, Test Information, Product Information and Test Results
Setup & Instrumentation | Instrumentation Requirements and Space for Sensor Placement Descriptions
General Setup | General Preparation and Setup
Optional UPS Classification | Optional Test for Determining UPS Type
VFD Efficiency | Input for UPS Efficiency in VFD Mode
VI Efficiency | Input for UPS Efficiency in VI Mode
VFI Efficiency | Input for UPS Efficiency in VFI Mode
Output Efficiency Calculation | Calculation for Overall Efficiency
Comments | Inputs for Anomalies That Affect Test Results or Interpretations
Photos | Inputs for Product and Sensor Placement Photos
Report Sign-Off Block | Report Review History
Test Conditions | Table of Test Condition Requirements for Each Test
Abbreviations | Description of Abbreviations used throughout Report Template
Version Control | Report Template Revision History
LEGEND
Tabs | Tabs with input cells
Cells | Input cell
Auto-populated cell
Provided data
NOT USED
Instructions for Completing this Template
Follow the steps below, filling in all input cells (shaded light blue) in each tab you are instructed to complete. Using TAB to "hop" from input cell to input cell is useful, but does not ensure that all input cells are reached. To guarantee that you enter all required information, you must visually scan for light blue cells in the entire area bounded by yellow-shaded cells.
Important: Start with a clean (unused) template copy for each new report. Enter only data and information that are unique to the unit tested and the current test of that unit. All abbreviations and variable names should be consistent with the reference test procedure.
STEP: | FILL IN INPUT CELLS IN THIS TAB:
Step 1 | General Info & Test Results
Step 2 | Setup & Instrumentation
Step 3 | General Setup
Step 4 | Optional UPS Classification
Step 5 | VFD Efficiency
Step 6 | VI Efficiency
Step 7 | VFI Efficiency
Step 8 | Output Efficiency Calculation
Step 9 | Comments
Step 10 | Photos
Step 11 | Report Sign-Off Block
Step 12 | Send separate Raw Data files for "VFD Efficiency", "VI Efficiency", "VFI Efficiency" tabs

## General Info & Test Results
Title Block
Test Report Template Name: | Uninterruptible Power Supplies
Version Number: | v1.2 |  | Back to Instructions Tab
Latest Template Revision: | 2024-07-16
Tab Name: | General Info & Test Results
File Name: | Uninterruptible Power Supplies - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Lab Information |  | Figures of Merit for Tested Unit
Lab Name: |  | Variable |  | Result | Output Power in W
Lab Location: |  | Efficiency (for VFD only) | 25% Load
50% Load
Test Information |  |  | 75% Load
Date Test Started: | [MM/DD/YYYY] |  | 100% Load
Date Test Finished: | [MM/DD/YYYY] | Efficiency (for VI only) | 25% Load
50% Load
75% Load
UPS Information |  |  | 100% Load
Manufacturer: |  | Efficiency (for VFI only) | 25% Load
Brand: |  |  | 50% Load
Manufacturer Model Number: |  |  | 75% Load
Serial Number: |  |  | 100% Load
Date Manufactured: |  | Overall Average Efficiency for VFD (if applicable)
Date Product Received: | [MM/DD/YYYY] | Overall Average Efficiency for VI (if applicable)
Condition as Received: |  | Overall Average Efficiency for VFI (if applicable)
VFD Support:
VI Support: |  | NOTE: This is only a copy; sign off is done in the Report Sign-Off Block tab
VFI Support: |  | Test Report Sign-Off Block
Rated Output Power [W]: |  | We certify that the information and data in this report: (1) were obtained from the specific test unit under test; (2) were obtained during the specific test being reported; (3) were not copied from any other source, except where instructed to do so; and (4) were not altered or modified in any way.
Rated Apparent Power [VA]:
If the UPS has any additional features unrelated to maintaining continuity of load power in case of input AC power failure, please describe and note setting:
|  | Role |  | Date | Entity
Device Information (if, applicable) |  | Test Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Manufacturer: |  | Template Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Brand: |  | Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Manufacturer Model Number:
Serial Number: |  | Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Date Manufactured:
Date Product Received:
Condition as Received:
Battery Information (if, applicable)
Manufacturer:
Brand:
Manufacturer Model Number:
Serial Number:
Date Manufactured:
Date Product Received:
Condition as Received:
Battery Chemistry:
Rated Battery Voltage [V]:
Rated Battery Charge Capacity [Ah]:
Rated Battery Charge Energy [Wh]:

## Setup & Instrumentation
Title Block
Test Report Template Name: | Uninterruptible Power Supplies
Version Number: | v1.2 |  |  | Back to Instructions tab
Latest Template Revision: | 2024-07-16
Tab Name: | Setup & Instrumentation
File Name: | Uninterruptible Power Supplies - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Set-Up (This table should include instrumentation, sensors, and all equipment used during testing)
Instrument Type | Brand | Model # | Sensor Location |  | Accuracy | Date of Last Calibration | Deadline for Next Calibration
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[6 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
Required Uncertainty and Resolution of Measuring Instrumentation
The power or energy meter must provide true root mean square (r. m. s) measurements of the active input and output measurements, with an uncertainty at full rated load of less than or equal to 0.5% at the 95% confidence level notwithstanding that voltage and current waveforms can include harmonic components. The meter must measure input and output values simultaneously.

## General Setup
Title Block
Test Report Template Name: | Uninterruptible Power Supplies
Version Number: | v1.2 |  | Back to Instructions tab
Latest Template Revision: | 2024-07-16
Tab Name: | General Setup
File Name: | Uninterruptible Power Supplies - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Directions:
Configure the UPS according to Annex J.2 of IEC 62040–3 Ed. 2.0 (incorporated by reference, see § 430.3) with the following additional requirements:
1. If the UPS can operate in two or more distinct normal modes as more than one UPS architecture, conduct the test in its lowest input dependency as well as in its highest input dependency mode where VFD represents the highest possible input dependency, followed by VI and then VFI.
2. The UPS must not be modified or adjusted to disable energy storage charging features. Minimize the transfer of energy to and from the energy storage system by ensuring the energy storage system is fully charged (at the start of testing) as follows:
(1) If the UUT has a battery charge indicator, charge the battery for 5 hours after the UUT has indicated that it is fully charged.
(2) If the UUT does not have a battery charge indicator but the user manual shipped with the UUT specifies a time to reach full charge, charge the battery for 5 hours longer than the time specified.
(3) If the UUT does not have a battery charge indicator or user manual instructions, charge the battery for 24 hours.
3. All DC output port(s) of the UUT must remain unloaded during testing.
4. Additional features should be configured as prescribed in Section 4.2.2.
Energy Storage System Preparation
Description | Start Time | End Time
Charge Time | ##:##:## | ##:##:##

## Optional UPS Classification
Title Block
Test Report Template Name: | Uninterruptible Power Supplies
Version Number: | v1.2 |  | Back to Instructions tab
Latest Template Revision: | 2024-07-16
Tab Name: | Optional UPS Classification
File Name: | Uninterruptible Power Supplies - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
UPS Architecture Classification Tests
Note: The following tests are OPTIONAL to determine UPS architecture.
VFD UPS Test
1. Perform the AC input failure test in Section 6.2.2.7 of IEC 62040–3 Ed. 2.0 (incorporated by reference, see § 430.3).
2. Verify if the UPS switches from normal mode of operation to battery power while the input is interrupted.
VI UPS Test
1. Perform the steady state input voltage tolerance test in Section 6.4.1.1 of IEC 62040–3 Ed. 2.0.
2. Verify if the UPS remains in normal mode with the output voltage within the specified output range when the input voltage is varied by ±10% of the rated input voltage.
VFI UPS Test
1. Perform the steady state input voltage tolerance test and the input frequency tolerance test in Sections 6.4.1.1 and 6.4.1.2 of IEC 62040–3 Ed. 2.0 respectively.
2. Verify if the UPS produces an output voltage and frequency within the specified output range when the input voltage is varied by ±10 percent of the rated input voltage and the input frequency is varied by ±2 percent of the rated input frequency.
Optional Test(s) Performed
Test Name | Performed? | Pass?
VFD Test
VI Test
VFI Test

## VFD Efficiency
Title Block
Test Report Template Name: | Uninterruptible Power Supplies
Version Number: | v1.2 |  | Back to Instructions tab
Latest Template Revision: | 2024-07-16
Tab Name: | VFD Efficiency
File Name: | Uninterruptible Power Supplies - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Directions:
NOTE: If the UPS does not support VFD mode, this tab can be left blank.
1. Ensure the UPS is running in VFD setting.
2. Ensure the UPS has been properly set up according to Section 4.2.
3. Connect the data logging equipment to the UPS.
4. Test the UPS in the order of 100%, 75%, 50%, and 25%* of the rated output power with a reference load.
5. For each reference load tested, allow sufficient time for the UPS to reach steady state as specified in Section 4.3.2.
6. Calculate the efficiency of each tested reference load by using either the average power method, or the accumulated energy method as specified in Section 4.3.3.
*: The 25% loading point measurement is only required for UPSs in VFD mode with rated output power of less than or equal to 1,500 Watts.
Efficiency at Different Loading Points
| Loading Condition | 100% | 75% | 50% | 25%
Efficiency
Notes:

## VI Efficiency
Title Block
Test Report Template Name: | Uninterruptible Power Supplies
Version Number: | v1.2 |  | Back to Instructions tab
Latest Template Revision: | 2024-07-16
Tab Name: | VI Efficiency
File Name: | Uninterruptible Power Supplies - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Directions:
NOTE: If the UPS does not support VI mode, this tab can be left blank.
1. Ensure the UPS is running in VI setting.
2. Ensure the UPS has been properly set up according to Section 4.2.
3. Connect the data logging equipment to the UPS.
4. Test the UPS in the order of 100%, 75%, 50%, and 25%* of the rated output power with a reference load.
5. For each reference load tested, allow sufficient time for the UPS to reach steady state as specified in Section 4.3.2.
6. Calculate the efficiency of each tested reference load by using either the average power method, or the accumulated energy method as specified in Section 4.3.3.
*: The 25% loading point measurement is only required for UPSs in VFD mode with rated output power of less than or equal to 1,500 Watts.
Efficiency at Different Loading Points
| Loading Condition | 100% | 75% | 50% | 25%
Efficiency
Notes:

## VFI Efficiency
Title Block
Test Report Template Name: | Uninterruptible Power Supplies
Version Number: | v1.2 |  | Back to Instructions tab
Latest Template Revision: | 2024-07-16
Tab Name: | VFI Efficiency
File Name: | Uninterruptible Power Supplies - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Directions:
NOTE: If the UPS does not support VFI mode, this tab can be left blank.
1. Ensure the UPS is running in VFI setting.
2. Ensure the UPS has been properly set up according to Section 4.2.
3. Connect the data logging equipment to the UPS.
4. Test the UPS in the order of 100%, 75%, 50%, and 25%* of the rated output power with a reference load.
5. For each reference load tested, allow sufficient time for the UPS to reach steady state as specified in Section 4.3.2.
6. Calculate the efficiency of each tested reference load by using either the average power method, or the accumulated energy method as specified in Section 4.3.3.
*: The 25% loading point measurement is only required for UPSs in VFD mode with rated output power of less than or equal to 1,500 Watts.
Efficiency at Different Loading Points
| Loading Condition | 100% | 75% | 50% | 25%
Efficiency
Notes:

## Output Eff. Calculation
Title Block
Test Report Template Name: | Uninterruptible Power Supplies
Version Number: | v1.2 |  | Back to Instructions tab
Latest Template Revision: | 2024-07-16
Tab Name: | Output Eff. Calculation
File Name: | Uninterruptible Power Supplies - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Output Efficiency Calculation
Output Efficiency shall be calculated using the equation below:
UPS Load Weightings
Portion of Time Spent at Reference Load*
Rated Output Power (W) | UPS Architecture | 25% | 50% | 75% | 100%
P ≤ 1500W | VFD | 0.2 | 0.2 | 0.3 | 0.3
| VI or VFI | 0 | 0.3 | 0.4 | 0.3
P > 1500W | VFD, VI, or VFI | 0 | 0.3 | 0.4 | 0.3
*Measuring efficiency at loading points with 0 time weighting is not required.
Measurements
UPS Supported Input Dependency |  | VFD | VI | VFI
Loading Point Efficiency | 25% Load
50% Load
75% Load
100% Load
Average Load Adjusted Efficiency
〖𝐸𝑓𝑓〗_𝑎𝑣𝑔=(𝑡_(25%)∗├ 𝐸𝑓𝑓┤|_(25%) )+(𝑡_(50%)∗├ 𝐸𝑓𝑓┤|_(50%) )+(𝑡_(75%)∗├ 𝐸𝑓𝑓┤|_(75%) )+(𝑡_(100%)∗├ 𝐸𝑓𝑓┤|_(100%) )

## Comments
Title Block
Test Report Template Name: | Uninterruptible Power Supplies
Version Number: | v1.2 | Back to Instructions tab
Latest Template Revision: | 2024-07-16
Tab Name: | Comments
File Name: | Uninterruptible Power Supplies - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Comments

## Photos
Title Block
Test Report Template Name: | Uninterruptible Power Supplies
Version Number: | v1.2 | Back to Instructions tab
Latest Template Revision: | 2024-07-16
Tab Name: | Photos
File Name: | Uninterruptible Power Supplies - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
1. Nameplate showing model number and serial number (if applicable) |  | 2. FTC EnergyGuide label (if present)
3. Photograph of battery charger as received (including all parts and application) |  | 4. Photograph of battery, including any markings (if applicable)
5. Photograph of UPS connection to test load |  | 6a. Photograph of test room set-up, including all instrumentation
6b. Additional photograph of test room set-up, including all instrumentation |  | 7. Additional photos (if necessary)

## Report Sign-Off Block
Title Block
Test Report Template Name: | Uninterruptible Power Supplies
Version Number: | v1.2 |  | Back to Instructions tab
Latest Template Revision: | 2024-07-16
Tab Name: | Report Sign-Off Block
File Name: | Uninterruptible Power Supplies - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Test Report Sign-Off Block
By signing in the space below, we certify that the information and data in this report: (1) were obtained from the specific test unit under test; (2) were obtained during the specific test being reported; (3) were not copied from any other source, except where instructed to do so; and (4) were not altered or modified in any way.
Role |  | Date | Entity
Test Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Template Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]

## Test Conditions
Title Block
Test Report Template Name: | Uninterruptible Power Supplies
Version Number: | v1.2
Latest Template Revision: | 2024-07-16
Tab Name: | Test Conditions
File Name: | Uninterruptible Power Supplies - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Electric Supply Conditions
Description |  | Specification
AC Voltage | Electric Supply Voltage (provide plots of voltage vs. time showing compliance with requirements) | within 3% of the highest rated voltage
| Electric Supply Voltage Frequency (provide plots of frequency vs. time showing compliance with requirements) | within 1% of the highest rated frequency
Test Room Conditions
Description |  | Specification
Specification
Room Air Temperature |  | 20 - 30 °C
Air Speed immediately surrounding the UUT |  | ≤ 0.5 m/s

## Abbreviations
Title Block
Test Report Template Name: | Uninterruptible Power Supplies
Version Number: | v1.2
Latest Template Revision: | 2024-07-16
Tab Name: | Abbreviations
File Name: | Uninterruptible Power Supplies - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Abbreviations
Description |  | Abbreviation
Total Harmonic Distortion |  | THD
Uninterruptible Power Supply |  | UPS
Voltage and Frequency Dependent |  | VFD
Voltage and Frequency Independent |  | VFI
Voltage Independent |  | VI

## Version Control
Title Block
Test Report Template Name: | Uninterruptible Power Supplies
Version Number: | v1.2
Latest Template Revision: | 2024-07-16
Tab Name: | Version Control
File Name: | Uninterruptible Power Supplies - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Revisions List
Version | Date
v1.0 | 2024-01-23
v1.1 | 2024-02-27
v1.2 | 2024-07-16