## Measure Inputs
Building Technologies Office
Prioritization Tool Measure Addition and Input Update Form
Please use this form and market definition forms to submit your recommendations for new measures or updates for existing measures based on new data and literature references. If you are proposing to add a new measure, at a minimum, please provide the following: 1) Detailed measure description (C16); 3) End-user cost of new measure (C46, 48); 5) New measure's lifetime (C39) 2) Market description (C25) 4) Performance improvement/energy savings (C35-C37); INSTRUCTIONS: 1) Confirm that the Excel file calculation preferences are set to automatic by selecting Formulas -> Calculation Options -> Automatic. 2) If you are suggesting modifications to an existing measure, please insert the measure number in the C13 cell (blue) below. You may look up measure numbers in the "Measure List (Fall 2014)" tab. When you insert the measure number, data in this form will be auto-populated based on existing data in the Prioritization Tool. You may then make your edits in the cells directly. You will notice the cell will be highlighted in a different color to indicate a change has been made. Please provide literature and data references for any proposed changes. A change without published, verifiable references will not be considered. 3) If you are providing information for a new measure, type in "New" in the C13 cell (blue) below. We suggest you use data for existing measures as a reference to fill out the form. Identify the most relevant measure number, populate data in the form based on that number, type in "New" in the measure number field, and proceed by making changes associated with creating the new measure. 4) E-mail the completed measure input form to Prioritization.Tool@ee.doe.gov.
Measure/Technology Description
Measure number: | 890
Are you providing information for a new measure or edits to an existing measure? | Edits to an existing measure
Measure title: | C: Grey-Water HPWH*
Detailed description of measure (max. 200 characters): | A grey-water-source heat pump water heater can greatly reduce WH energy consumption when replacing a standard electric stoarage WH with 54kW capacity and thermal efficiency of 98%, especially in commercial buildings that have high WH loads (restaurants, laundromats, hotels, etc.) by recovering heat in grey water replacing electric storage WH via a water-to-water heat pump. Assume no impact on space heating and cooling of this measure.
Deployment Level: | 0: Roadmap Goal / Target
End-use: | Water Heating
Component: | System
Comments:
Market Characteristics
Sector(s): | Commercial
Market targeted (also, define in the Market Definition tab): | Total energy consumption by all commercial electric storage water heaters
Fuel Selection / Fuel Switching (FS) Option | 1 C/R: No FS: All electric to all electric
If another market is targeted, full market description (if relevant, include equipment class, building type (new, existing, all), climate zones, etc.):
Market data source(s): | AEO 2010 NEMS
If other, suggest market data source(s):
Year of market entry (based on target cost and performance): | 2016
Comments:
Measure/Technology Performance
Energy consumption or efficiency of a baseline unit: | 0.92
Measure's improvement in energy consumption or efficiency over the baseline unit: | 2.4
Units: | Energy Factor
Lifetime of a baseline unit (years): | 13
Lifetime of new measure (years): | 13
Data source(s): | 1) Baseline unit performance: Assuming roughly the same EF as a residential gas-fired storage WH for standard unit (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment) 2) Efficient unit performance: Assuming roughly the same performance as a ground-source heat pump, 3.5 COP (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) -Converting to 2.4 EF using a 0.698 conversion factor which accounts for differences between lab rating and typical field performance (Source: Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007)) 3) Baseline unit cost: Average installed cost for a 54 kW electric storage WH is $5,430 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) 4) Efficient unit cost: TARGET Installed Cost -Assuming a 48kBtu/Hr ground-source heat pump has a retail equipment cost of $7,000 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) -Assuming roughly 30% of that cost represents the water-to-air heat pump gives a cost of $2,100 (Source: COST CONTAINMENT FOR GROUND-SOURCE HEAT PUMPS, S. Kavanaugh, http://geoheat.oit.edu/pdf/tp72.pdf) -Assuming that the water-to-air heat pump is a reasonable proxy for a water-to-water heat pump and scaling this cost up to 200,000 kBtu/Hr capacity gives a cost of $8,750, and adding 40% for installation gives $12,250 -Assuming a 25% cost reduction for improved design results in a target installed cost of roughly $9,200
Comments:
Measure/Technology Cost*
End-user cost of a baseline unit: | 5430
End-user cost of new measure: | 9200
Incremental cost: | 3770
Units: | per unit
Data source(s): | 1) Baseline unit performance: Assuming roughly the same EF as a residential gas-fired storage WH for standard unit (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment) 2) Efficient unit performance: Assuming roughly the same performance as a ground-source heat pump, 3.5 COP (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) -Converting to 2.4 EF using a 0.698 conversion factor which accounts for differences between lab rating and typical field performance (Source: Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007)) 3) Baseline unit cost: Average installed cost for a 54 kW electric storage WH is $5,430 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) 4) Efficient unit cost: TARGET Installed Cost -Assuming a 48kBtu/Hr ground-source heat pump has a retail equipment cost of $7,000 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) -Assuming roughly 30% of that cost represents the water-to-air heat pump gives a cost of $2,100 (Source: COST CONTAINMENT FOR GROUND-SOURCE HEAT PUMPS, S. Kavanaugh, http://geoheat.oit.edu/pdf/tp72.pdf) -Assuming that the water-to-air heat pump is a reasonable proxy for a water-to-water heat pump and scaling this cost up to 200,000 kBtu/Hr capacity gives a cost of $8,750, and adding 40% for installation gives $12,250 -Assuming a 25% cost reduction for improved design results in a target installed cost of roughly $9,200
Comments:
*Please attempt to provide costs at large-scale market adoption price.
Contact Information
Name of person completing form:
Company/institution name:
Phone number:
Email:
Address:
Note on B15: Key: Buildings: (N): This measure is applicable only to new homes or buildings constructed after the technology or measure penetrates its market. (E): This measure is applicable only to existing homes or buildings constructed prior to 2010. Markets: C: Commercial R: Residential I: Industrial O: Outdoor Other: FS: Fuel Switching MYP: BTO Multi-Year Plan target * - target
Note on B17: Deployment Level Options: 0: Roadmap Goal / Target 1: Early R&D: not basic science, but still lab bench 2: Late R&D: cost reduction, performance improvement, may be available to early adopters 3: Early Deployment: savings not yet proven in whole building context 4: Late Deployment: savings proven, but need to transform the market 5: Standards: rule in place, underway, or ready to be planned
Note on B19: Technology's component or area of improvement in energy efficiency that is affected by each measure. Examples include, but are not limited to: system; use intensity; thermal transfer; maintenance; evaporator; heat exchanger; window; basement; roof; door; walls; infiltration; lamp; luminaire; ballast; controls, etc.
Note on B26: Key: Markets: C: Commercial R: Residential I: Industrial O: Outdoor
Note on B35: Baseline unit is a representative unit that typically comprises installed base in U.S. homes or buildings in a specific region (if appropriate). In some cases, it can be considered as a typical technology currently on the market that the new measure must compete for market share. Each measure's baseline metrics are derived based on EIA's Annual Energy Outlook (AEO) National Energy Modeling System's database. In some cases, a measure can be supplementary, and this field can be set to 0. Please make sure to include any assumptions about the baseline and its relevant metrics in the comments section (C41).
Note on B45: End-user cost should include cost of installation. However, if installation cost is approximately the same between new and baseline units, installation cost may be omitted.
Note on B46: End-user cost should include cost of installation. However, if installation cost is approximately the same between new and baseline units, installation cost may be omitted.
Note on B47: Incremental cost is the difference between scaled end-user cost of an efficient unit and a standard unit, adjusted for increase or decrease in new unit's lifetime when the difference is substantial. A $ value in parentheses means that an efficient unit's first or lifetime cost is lower than the first or lifetime cost of a standard unit.

## Measure List (Fall 2014)
Measure no. | Description | Brief description | R&D/ Deployment/ Standards | Sector | End-Use | Market | Efficiency Units | Efficient Unit Performance | Baseline Unit Performance | Market cost (per efficient unit, at scale) | Market cost (per standard unit), if needed | Market cost (per efficient unit, at scale) | Market Cost (per standard unit), if needed | Incremental measure cost | Lifetime of a new measure | Lifetime of a baseline unit | Data Sources
1 | Use most cost effective insulation in new commercial gas and electric fryers | C: Fryers - improved insulation | 3 | Commercial | Cooking | All commercial electric and gas fryers | Energy Savings (%) | 7% | 0% | 0 | 0 | 0 | 0 | 0 | 12 | 12 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. Other Supporting Sources: Cost data are from google searches of commercially available appliances
2 | Use most cost effective insulation in new commercial gas and electric griddles | C: Improved Insulation in Griddles | 3 | Commercial | Cooking | All commercial electric and gas griddles | Energy Savings (%) | 7% | 0% | 0 | 0 | 0 | 0 | 0 | 22 | 22 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy.
5 | Increase deployment of more efficient commercial gas connectionless steamers | C: Gas Connectionless Steamer | 5 | Commercial | Cooking | All commercial natural gas steamers | Energy Savings (%) | 73% | 0% | 0 | 0 | 0 | 0 | 3700 | 10 | 10 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy.
6 | Increase deployment of more efficient commercial electric connectionless steamers | C: Electric Connectionless Steamer | 5 | Commercial | Cooking | All commercial electric steamers | Energy Savings (%) | 73% | 0% | 0 | 0 | 0 | 0 | 2500 | 10 | 10 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy.
7 | Increase deployment of more efficient commercial gas ovens | C: Gas Oven | 5 | Commercial | Cooking | All commercial natural gas ovens | Energy Savings (%) | 29.09% | 0% | 0 | 0 | 0 | 0 | 0 | 10 | 10 | ENERGY STAR (n.d.). Savings Calculator for ENERGY STAR Qualified Commercial Kitchen Equipment. Retrieved from: http://www.energystar.gov/ia/business/bulk_purchasing/bpsavings_calc/commercial_kitchen_equipment_calculator.xls?ba38-b08e
8 | Increase deployment of more efficient commercial electric convection ovens | C: Convection Ovens | 5 | Commercial | Cooking | All commercial electric ovens | Energy Savings (%) | 15.41% | 0% | 0 | 0 | 0 | 0 | 800 | 10 | 10 | EnergyStar
11 | Improve electric ignition reliability for commercial gas cooking appliances | C: Gas Cooking Elec. Ignition | 2 | Commercial | Cooking | All commercial natural gas cooking | Energy Savings (%) | 3.555% | 0% | 0 | 0 | 0 | 0 | 100 | 10 | 10 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy.
14 | Commercial lighting: troffers 1-to-1 replacement (2x4,2x2,1x4) | C: LED Troffers | 4 | Commercial | Lighting | All commercial troffers | lumens/watt | 95 | 74 | 498.05 | 97.5 | 498.05 | 97.5 | 358.05 | 12 | 5 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
15 | Commercial lighting: troffers 1-to-1 replacement (2x4,2x2,1x4) with added controls | C: LED Troffers + Ctrls | 4 | Commercial | Lighting | All commercial troffers | lumens/watt | 109 | 74 | 648.05 | 97.5 | 648.05 | 97.5 | 508.05 | 12 | 5 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
16 | Replace metal halide parking lot lighting with LEDs | O: Parking Lot LEDs | 4 | Outdoor | Lighting | All metal halide lighting in parking lots | lumens/watt | 83 | 60 | 478 | 240 | 478 | 240 | -5.6 | 11 | 4 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
18 | Increase deployment of more efficient commercial gas fryers | C: Gas Fryers | 5 | Commercial | Cooking | All commercial natural gas fryers | Energy Savings (%) | 31.02% | 0% | 4113 | 2894 | 4113 | 2894 | 1219 | 12 | 12 | EnergyStar Primary Source: Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. Other Supporting Sources: Cost data are from google searches of commercially available appliances
19 | Increase deployment of more efficient commercial electric fryers | C: Electric Fryers | 5 | Commercial | Cooking | All commercial electric fryers | Energy Savings (%) | 6.48% | 0% | 0 | 0 | 0 | 0 | 275 | 12 | 12 | ENERGY STAR (n.d.). Savings Calculator for ENERGY STAR Qualified Commercial Kitchen Equipment. Retrieved from: http://www.energystar.gov/ia/business/bulk_purchasing/bpsavings_calc/commercial_kitchen_equipment_calculator.xls?ba38-b08e
23 | Standard Max Tech ASHP (FS only) | R: Max Tech ASHP (FS) | 0 | Residential | Heating & Cooling | All non-electric heating, proportion of cooling | Energy Savings (%) | 40.77% | 0% | 4508 | 3330 | 4508 | 3330 | 1178 | 15 | 15 | Hewitt et.al. demonstrates high COP; cost represnts road map target Primary Source: Hewitt, N.J., Huang, M.J., Anderson, M. & Quinn, M. Advanced air source heat pumps for UK and European domestic buildings. Applied Thermal Engineering 31, 3713-3719 (2011); ASHP TSD
24 | Increase deployment of more efficient commercial gas griddles | C: Gas Griddle | 5 | Commercial | Cooking | All commercial natural gas griddles | Energy Savings (%) | 12.25% | 0% | 800 | 0 | 800 | 0 | 800 | 22 | 22 | LBNL 2008 Primary Source: ENERGY STAR (n.d.). Savings Calculator for ENERGY STAR Qualified Commercial Kitchen Equipment. Retrieved from: http://www.energystar.gov/ia/business/bulk_purchasing/bpsavings_calc/commercial_kitchen_equipment_calculator.xls?ba38-b08e
25 | Increase deployment of more efficient commercial electric griddles | C: Electric Griddle | 5 | Commercial | Cooking | All commercial electric griddles | Energy Savings (%) | 11.06% | 0% | 800 | 0 | 800 | 0 | 800 | 22 | 22 | LBNL 2008 Primary Source: ENERGY STAR (n.d.). Savings Calculator for ENERGY STAR Qualified Commercial Kitchen Equipment. Retrieved from: http://www.energystar.gov/ia/business/bulk_purchasing/bpsavings_calc/commercial_kitchen_equipment_calculator.xls?ba38-b08e
26 | Early replacement of residential gas cook top with induction | R: Induction cooktop (FS) | 4 | Residential | Cooking | Total residential cooking energy consumption using natural gas stove | Energy Savings (%) | 70.1% | 0% | 1999 | 0 | 1999 | 0 | 1999 | 17 | 17 | Electrolux Appliances, http://www.electroluxappliances.com/kitchen-appliances/cooktops/induction/ew30ic60is; for payback period use EnergyStar oven assumptions with cost differential between gas and induction cook top
28 | National campaign for residential desktop users to employ energy saving settings | R: Desktop Power Management | 4 | Residential | MELs | Total energy use by residential desktop PCs | Energy Savings (%) | 44% | 0% | 0 | 0 | 0 | 0 | 0 | 4 | 4 | TIAX 2007, 2004 Primary Source: Roth, K.W., Mckenney, K., Ponoum, R. & Paetsch, C. Residential Miscellaneous Electric Loads: Energy Consumption Characterization and Savings Potential. Energy 197 (2007). Other Supporting Sources: Cost data are from google searches of commercially available appliances
29 | National campaign for residential notebook users to employ energy saving settings | R: Laptop Power Management | 4 | Residential | MELs | Total energy use by residential and commercial notebook PCs | Energy Savings (%) | 28% | 0% | 0 | 0 | 0 | 0 | 0 | 4 | 4 | TIAX 2007, 2004 Primary Source: Roth, K.W., Mckenney, K., Ponoum, R. & Paetsch, C. Residential Miscellaneous Electric Loads: Energy Consumption Characterization and Savings Potential. Energy 197 (2007). Other Supporting Sources: Cost data are from google searches of commercially available appliances
30 | Heat pipe griddle | C: Heat Pipe Griddle | 3 | Commercial | Cooking | All commercial electric and gas griddles | Energy Savings (%) | 4.3% | 0% | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 1. Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. 2. http://www.accutemp.net/accu-steam_main.htm
33 | Increase deployment of high efficiency motors in food preparation | C: Food Prep Motor | 5 | Commercial | Cooking | All commercial food preparation appliances energy use | Energy Savings (%) | 2.2% | 0% | 0 | 0 | 0 | 0 | 0 | 12 | 12 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy.
34 | Stock Pot Heat Transfer Fins | C: Stock Pot Heat Transfer Fins | 3 | Commercial | Cooking | All commercial natural gas griddles | Energy Savings (%) | 5% | 0% | 0 | 0 | 0 | 0 | 0 | 10 | 10 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy.
35 | Increase deployment of commercial electric ovens | C: Electric Oven | 5 | Commercial | Cooking | All commercial electric ovens | Energy Savings (%) | 39% | 0% | 8325 | 4500 | 8325 | 4500 | 3825 | 10 | 10 | LBNL 2008, U.S. Building-Sector Energy Efficiency Potential Primary Source: ENERGY STAR (n.d.). Savings Calculator for ENERGY STAR Qualified Commercial Kitchen Equipment. Retrieved from: http://www.energystar.gov/ia/business/bulk_purchasing/bpsavings_calc/commercial_kitchen_equipment_calculator.xls?ba38-b08e
36 | Increase deployment of more efficient commercial gas ranges | C: Gas Range | 5 | Commercial | Cooking | All commercial natural gas ranges | Energy Savings (%) | 25% | 0% | 4830 | 3000 | 4830 | 3000 | 1830 | 10 | 10 | LBNL 2008, U.S. Building-Sector Energy Efficiency Potential Primary Source: Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. Other Supporting Sources: Cost data are from google searches of commercially available appliances
37 | Increase deployment of more efficient commercial electric ranges | C: Electric Range | 5 | Commercial | Cooking | All commercial electric ranges | Energy Savings (%) | 24% | 0% | 7400 | 4000 | 7400 | 4000 | 3400 | 10 | 10 | LBNL 2008, U.S. Building-Sector Energy Efficiency Potential Primary Source: Brown, R., Borgeson, S., Koomey, J. & Biermayer, P. U . S . Building-Sector Energy Efficiency Potential. Environmental Protection 33 (2008).
38 | Increase deployment of more efficient commercial gas steam cookers | C: Gas Steamer | 5 | Commercial | Cooking | All commercial natural gas steamers | Energy Savings (%) | 43% | 0% | 10500 | 10500 | 10500 | 10500 | 0 | 10 | 10 | LBNL 2008, U.S. Building-Sector Energy Efficiency Potential Primary Source: Brown, R., Borgeson, S., Koomey, J. & Biermayer, P. U . S . Building-Sector Energy Efficiency Potential. Environmental Protection 33 (2008).
39 | Increase deployment of more efficient commercial electric steam cookers | C: Electric Steamer | 5 | Commercial | Cooking | All commercial electric steamers | Energy Savings (%) | 57% | 0% | 10000 | 10000 | 10000 | 10000 | 0 | 10 | 10 | LBNL 2008, U.S. Building-Sector Energy Efficiency Potential Primary Source: Brown, R., Borgeson, S., Koomey, J. & Biermayer, P. U . S . Building-Sector Energy Efficiency Potential. Environmental Protection 33 (2008).
41 | Reduce idle use in commercial gas broilers | C: Idle Energy Reduction in Gas Broilers | 3 | Commercial | Cooking | All commercial natural gas broilers | Energy Savings (%) | 26% | 0% | 0 | 0 | 0 | 0 | 0 | 10 | 10 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy.
42 | Eliminate idle energy use in new residential microwaves | R: Microwave: Deploy 0W Standby | 4 | Residential | Cooking | Total energy consumption by residential microwaves | Energy Savings (%) | 20% | 0% | 0 | 0 | 0 | 0 | 1 | 9 | 9 | TIAX LLC 2007, Residential Misc Electric Loads http://www.iepec.org/TIAX_MiscElecLoadsReportToDOE.pdf
44 | Deploy improved magnetrons in new residential microwaves | R: Microwaves - Improve magnetron efficiency | 4 | Residential | Cooking | Total energy consumption by residential microwaves | Magnetron efficiency | 0.75 | 0.71 | 0 | 0 | 0 | 0 | 15 | 9 | 9 | LBNL 1998 TSD, active 80% of energy consumption: TIAX 2007
45 | Deploy improved power supplies in new residential microwaves | R: Microwaves - Improve magnetron power supply efficiency | 4 | Residential | Cooking | Total energy consumption by residential microwaves | Energy Savings (%) | 2.9% | 0% | 0 | 0 | 0 | 0 | 9 | 9 | 9 | LBNL 1998 TSD, active 80% of energy consumption: TIAX 2007
46 | Replace residential gas cook top with induction at end of life | R: Induction Cooktop (FS) | 4 | Residential | Cooking | Total residential cooking energy consumption using natural gas stove | Energy Savings (%) | 70% | 0% | 1999 | 1199 | 1999 | 1199 | 800 | 17 | 17 | Electrolux. (n.d.). 30" Induction Cooktop. Retrieved from http://www.electroluxappliances.com/kitchen-appliances/cooktops/induction/ew30ic60is
47 | Replace residential electric cook top with induction at end of life | R: Induction Cooktop | 4 | Residential | Cooking | Total residential cooking energy consumption using electric stove | Energy Savings (%) | 20% | 0% | 1999 | 1449 | 1999 | 1449 | 550 | 17 | 17 | Electrolux. (n.d.). 30" Induction Cooktop. Retrieved from http://www.electroluxappliances.com/kitchen-appliances/cooktops/induction/ew30ic60is
49 | Move toward replacing conventional burners with infrared burners in new commercial gas fryers | C: Infrared Burners in Fryers | 4 | Commercial | Cooking | All commercial natural gas fryers | Energy Savings (%) | 30% | 0% | 0 | 0 | 0 | 0 | 750 | 12 | 12 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy.
50 | Standardize replacement of conventional burners with infrared burners in new commercial gas broilers | C: Infrared Burners in Broilers | 4 | Commercial | Cooking | All commercial natural gas broilers | Energy Savings (%) | 37% | 0% | 0 | 0 | 0 | 0 | 1750 | 10 | 10 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy.
51 | Standardize replacement of conventional burners with infrared burners in new commercial gas ovens | C: Infrared Burners in Gas Ovens | 4 | Commercial | Cooking | All commercial natural gas ovens | Energy Savings (%) | 30% | 0% | 0 | 0 | 0 | 0 | 1000 | 10 | 10 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy.
52 | Demonstrate and deploy infrared burners as replacement to conventional burners in new commercial gas ranges | C: Infrared Burners in Gas Ranges | 4 | Commercial | Cooking | All commercial natural gas ranges | Energy Savings (%) | 39% | 0% | 0 | 0 | 0 | 0 | 1700 | 10 | 10 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy.
54 | Increase deployment of efficient fans in new residential microwaves | R: Efficient fans in microwaves | 5 | Residential | Cooking | Total energy consumption by residential microwaves | Energy Savings (%) | 0.23% | 0% | 0 | 0 | 0 | 0 | 10 | 9 | 9 | LBNL 1998 TSD, active 80% of energy consumption: TIAX 2007
55 | Increase amount of heat transferred to surfaces in new gas fryers: Use a blower to force a premixed air-fuel mixture into the burner, allowing higher combustion gas temperature to be reached as the fuel mixture contains less excess air | C: Power Burners in Gas Fryers | 3 | Commercial | Cooking | All commercial natural gas fryers | Energy Savings (%) | 31% | 0% | 0 | 0 | 0 | 0 | 500 | 12 | 12 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy.
56 | Increase amount of heat transferred to surfaces in new gas ranges: Use a blower to force a premixed air-fuel mixture into the burner, allowing higher combustion gas temperature to be reached as the fuel mixture contains less excess air | C: Power Burners in Gas Ranges | 3 | Commercial | Cooking | All commercial natural gas ranges | Energy Savings (%) | 34% | 0% | 0 | 0 | 0 | 0 | 3000 | 10 | 10 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy.
57 | Development, demonstration and deployment of pulse combustion burners in commercial natural gas fryers and griddles | C: Pulse Combustion Burners in Gas Fryers and Griddles | 2 | Commercial | Cooking | All commercial natural gas fryers and griddles | Energy Savings (%) | 31% | 0% | 0 | 0 | 0 | 0 | 760 | 22 | 22 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy.
58 | Max tech microwave (combination of other measures) | R: Max tech microwave | 2 | Residential | Cooking | Total energy consumption by residential microwaves | Energy Savings (%) | 20% | 0% | 0 | 0 | 0 | 0 | 55 | 9 | 9 | TIAX LLC 2007, Residential Misc Electric Loads; LBNL 1998 TSD, active 80% of energy consumption Primary Source: Roth, K.W., Mckenney, K., Ponoum, R. & Paetsch, C. Residential Miscellaneous Electric Loads: Energy Consumption Characterization and Savings Potential. Energy 197 (2007).
60 | Increase deployment of commercial gas steam cookers | C: Gas Steam Cooker | 5 | Commercial | Cooking | All commercial natural gas steamers | Energy Savings (%) | 34.58% | 0% | 10568 | 6836 | 10568 | 6836 | 3732 | 10 | 10 | EnergyStar
61 | Increase deployment of commercial electric steam cookers | C: Electric Steam Cooker | 5 | Commercial | Cooking | All commercial electric steamers | Energy Savings (%) | 51.16% | 0% | 5890 | 3400 | 5890 | 3400 | 2490 | 10 | 10 | EnergyStar
65 | National campaign to improve power management of video game systems in homes | R: Video Game Power Management | 4 | Residential | MELs | Total energy use by residential video game consoles | Energy Savings (%) | 72% | 0% | 0 | 0 | 0 | 0 | 0 | 5 | 5 | MTAB Report; Priority Setting Estimates Primary Source: Desroches, L.B., & Garbesi, K. (2011). Max Tech and Beyond. Lawrence Berkeley National Laboratory.
69 | Demonstrate and deploy indirect evaporative (e.g., Coolerado) A/C in residential homes in mixed-dry and hot-dry climates. "Instead of using chemical refrigerants and compressors to cool recycled interior air, we use a new, patented process that runs fresh outside air through air filters and then a heat mass exchanger (HMX)." | R: Coolerado, mixed/hot-dry CZ | 3 | Residential | Cooling | Total cooling in mixed-dry and hot-dry climates | Energy Savings (%) | 87.5% | 0% | 9230 | 6545 | 9230 | 6545 | 2685 | 19 | 19 | Primary Source: Coolerado technical manuals,http://www.coolerado.com/solutions/ , Desroches, L.-B. et al. Max Tech and Beyond. 60 (2011). Dean, Herrmann, etc. NREL. 2012. Dew Point Evaporative Comfort Cooling. http://www.nrel.gov/docs/fy13osti/56256-1.pdf
70 | Demonstrate and deploy indirect evaporative (e.g., Coolerado) A/C in commercial buildings in mixed-dry and hot-dry climates. "Instead of using chemical refrigerants and compressors to cool recycled interior air, we use a new, patented process that runs fresh outside air through air filters and then a heat mass exchanger (HMX)." | C: Coolerado, mixed/hot-dry CZ | 3 | Commercial | Cooling | Total cooling in hot, dry climates in all commercial buildings | Energy Savings (%) | 87.5% | 0% | 6.1533 | 4.3633 | 6.1533 | 4.3633 | 1.79 | 15 | 15 | Coolerado technical manuals, http://www.coolerado.com/solutions/ , Desroches, L.-B. et al. Max Tech and Beyond. 60 (2011) Dean, Herrmann, etc. NREL. 2012. Dew Point Evaporative Comfort Cooling. http://www.nrel.gov/docs/fy13osti/56256-1.pdf
71 | Research, demonstrate, and deploy advanced liquid desiccant A/C (e.g., DeVAP, DuCool) in homes in mixed humid and hot humid climates | R: DEVAP, humid CZ | 1 | Residential | Cooling | Total residential central cooling in humid climates | Energy Savings (%) | -105.3% | 0% | 8100 | 2600 | 8100 | 2600 | 5500 | 17 | 17 | Kozubal, E.; Woods, J.; Judkoff, R.; "Development and Analysis of Desiccant Enhanced Evaporative Air Conditioner Prototype"; NREL, 2012. http://www.nrel.gov/docs/fy12osti/54755.pdf Kozubal, E. et. al.; "Desiccant Enhanced Evaporative Air-Conditioning (DEVap): Evaluation of a New Concept in Ultra Efficient Air Conditioning"; NREL, 2011. http://www.nrel.gov/docs/fy11osti/49722.pdf; NCI Internal DeVAP Report Cost (listed value is not consistent with this source: "Rooftop units using DEVAP design are initially expected to cost ~30% more than competing models." Kozubal. NREL. July 2 2012. http://www.nrel.gov/docs/fy12osti/55740.pdf
72 | Research, demonstrate, and deploy advanced liquid desiccant A/C (e.g., DeVAP, DuCool) in commercial buildings in mixed humid and hot humid climates | C: DEVAP, humid CZ | 1 | Commercial | Cooling | Total cooling in humid climates by all commercial RTUs | Energy Savings (%) | -44.24% | 0% | 19000 | 9300 | 19000 | 9300 | 1.6167 | 15 | 15 | Kozubal, E.; Woods, J.; Judkoff, R.; "Development and Analysis of Desiccant Enhanced Evaporative Air Conditioner Prototype"; NREL, 2012. http://www.nrel.gov/docs/fy12osti/54755.pdf Kozubal, E. et. al.; "Desiccant Enhanced Evaporative Air-Conditioning (DEVap): Evaluation of a New Concept in Ultra Efficient Air Conditioning"; NREL, 2011. http://www.nrel.gov/docs/fy11osti/49722.pdf; NCI Internal DeVAP Report Cost (listed value is not consistent with this source: "Rooftop units using DEVAP design are initially expected to cost ~30% more than competing models." Kozubal. NREL. July 2 2012. http://www.nrel.gov/docs/fy12osti/55740.pdf
76 | Launch campaign to encourage cleaning home A/C coils annually | R: Clean AC coils | 3 | Residential | Cooling | Total residential cooling by CAC and ASHPs as well as ASHP heating | Energy Savings (%) | 6% | 0% | 0 | 0 | 0 | 0 | 10 | 16 | 16 | http://www.fuller.com/products_detail.asp?cat=1&subcat=5&id=216 Primary Source: Choi-Granade et. Al.; "Unlocking Energy Efficiency in the U.S. Economy"; McKinsey & Company (2009)
80 | Demonstrate and deploy filters with lower pressure drop in homes with central air systems (furnace fans) | R: Low ΔP Air Filter | 3 | Residential | HVAC | Furnace Fans Pumps | Blower energy savings (%) | 10% | 0% | 30 | 15 | 30 | 15 | 15 | 0.25 | 0.25 | 1) Energy savings: LBNL's "System Effects of High Efficiency Filters" report 2) Costs from www. Homedepot.com 3) Other supporting sources: "Energy Savings Potential and RD&D Opportunities for Residential Building HVAC Systems. October 2012" http://www1.eere.energy.gov/buildings/pdfs/residential_hvac_research_opportunities.pdf; "System Effects of High Efficiency Filters in Homes." LBNL Environmental Energy Technology Division, March 2013. http://eetd.lbl.gov/sites/all/files/lbnl-6144e.pdf. ENERGY STAR "Maintenance Checklist". http://www.energystar.gov/index.cfm?c=heat_cool.pr_maintenance; Camfil, AFE journal, HPAC Engineering journal, NREL feedback. "Air-Filter Life-Cycle Cost", Seyffer, C.; HPAC Engineering 9/2010. Proper Air Filter Selection Goes a Long Way", Matela, D.AFE Journal 10/2010. Expert interviews suggest 25% is more typical savings.
81 | Demonstrate and deploy filters with lower pressure drop in variable air volume (VAV) systems in commercial buildings | C: Low ΔP Air Filter | 3 | Commercial | HVAC | Total commercial variable volume ventilation and air handlers in all commercial buildings | Energy savings (%) | 2.668% | 0% | 0 | 0 | 0 | 0 | 0.11 | 6 | 6 | Camfil, AFE journal, HPAC Engineering journal Primary Source: "Air-Filter Life-Cycle Cost", Seyffer, C.; HPAC Engineering 9/2010 Other Supporting Sources: Proper Air Filter Selection Goes a Long Way", Matela, D.AFE Journal 10/2010 Expert interviews suggest 25% is more typical savings
85 | Move to include duct insulation in building codes: residential | R: Duct Insulation (N) | 5 | Residential | HVAC | New homes lacking duct insulation | R-value | 8 | 4 | 518 | 0 | 518 | 0 | 518 | 20 | 20 | NREL Retrofit efficiency measures database; HES pro; ducts.lbl.gov Primary Source: Cost: NREL retrofit measure database Savings: First principles of moving ducts from R-4 to R-8 as per recent code changes Other Supporting Sources: LBNL. 2011. Thermal Energy Distribution Website. ducts.lbl.gov.
86 | Move to include duct insulation in building codes: commercial | C: Duct Insulation (N) | 5 | Commercial | HVAC | All commercial heating and cooling in new buildings with uninsulated ducts | R-value | 8 | 4 | 0 | 0 | 0 | 0 | 0.32 | 20 | 20 | ducts.lbl.gov Primary Source: Cost: NREL retrofit measure database Savings: First principles of moving ducts from R-4 to R-8 as per recent code changes Other Supporting Sources: LBNL. 2011. Thermal Energy Distribution Website. ducts.lbl.gov.
87 | Demonstrate and deploy natural ventilation in new homes in temperate climates | R: Natural ventilation/controls (N), temp. CZ | 3 | Residential | Cooling | Central cooling in new homes in mixed-humid and marine climates | Energy Savings (%) | 46% | 0% | 3000 | 6000 | 3000 | 6000 | -3000 | 17 | 17 | Aarhus Engineering college, windowmaster.com Primary Source: Cardinale, N., Micucci, M. & Ruggiero, F. Analysis of energy saving using natural ventilation in a traditional Italian building. Energy and Buildings 35, (2003). Walker, A (2010). "Natural Ventilation". Whole Building Design Guide(http://www.wbdg.org/resources/naturalventilation.php) Price: Windowmaster/ Aarhus Engineering College websites Other Supporting Sources: Choi-Granade et. Al.; "Unlocking Energy Efficiency in the U.S. Economy"; McKinsey & Company (2009)
91 | Deploy enhanced duct sealing | R: Enhance Duct Sealing (N) | 3 | Residential | HVAC | New homes with IECC 2009 code-compliant duct sealing | Energy Savings (%) | 5% | 0% | 0 | 0 | 0 | 0 | 638.22 | 20 | 20 | NREL Retrofit efficiency measures database, McKinsey; Aeroseal website: http://www.aeroseal.com/commercial_duct_sealing.html; Modera 2005: Fixing Duct Leaks, ASHRAE Journal; typical new home duct leakage from BA House Simulation Protocols (http://www.nrel.gov/docs/fy11osti/49246.pdf) Primary Source: Hendron, R., and Engebrecht, C. 2010. Building America House Simulation Protocols. DOE/GO-102010-3141. http://apps1.eere.energy.gov/buildings/publications/pdfs/building_america/house_simulation_revised.pdf Modera, M Fixing Duct Leaks in Commercial Buildings ASHRAE Journal June 2005
92 | Move to include duct sealing in commercial codes | C: Duct Sealing (N) | 5 | Commercial | HVAC | All furnaces and A/C heating and cooling (i.e., ducts) in new commercial buildings | Energy Savings (%) | 10% | 0% | 0 | 0 | 0 | 0 | 0.33 | 20 | 20 | Aeroseal website: http://www.aeroseal.com/commercial_duct_sealing.html; Modera 2005: Fixing Duct Leaks, ASHRAE Journal; Primary Source: Modera, M Fixing Duct Leaks in Commercial Buildings ASHRAE Journal June 2005 Aeroseal website. http://www.aeroseal.com/problem-we-solve/FAQ-commercial.html Other Supporting Sources: 13. Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. 289 (2011).
93 | Launch campaign to encourage steam cleaning commercial A/C coils annually | C: Steam Clean AC Coils | 4 | Commercial | Heating & Cooling | All commercial cooling, and heating with ASHPs | Energy Savings (%) | 10% | 0% | 0 | 0 | 0 | 0 | 0.2 | 15 | 15 | SavetheWatts.com, National Steam Clean, Rejuvinair, Air Conditioning, Heating and Refrigeration News (achrnews.com) Primary Source: Checket-Hanks, B. "Contractor Offers Hope For PTAC IAQ". The Air Conditioning, Heating and Refrigeration NEWS, March 10, 2004 Rejuvinair website
94 | Demonstrate and deploy thermal energy storage (including chilled water and ice) for central chiller systems | C: Cold Storage for Large Chillers | 4 | Commercial | Cooling | All commercial cooling | Energy Savings (%) | 5% | 0% | 0 | 0 | 0 | 0 | 9600 | 15 | 15 | http://www.calmac.com/office/engineer.asp, www.pge.com/includes/docs/pdfs/about/edusafety/training/pec/inforesource/thrmstor.pdf; Thermal Energy Storage Strategies for Commercial HVAC Systems, PG&E Energy Efficiency Information Primary Source: Pacific Gas & Electric. "Thermal Energy Storage Strategies for Commercial HVAC Systems". PG&E, 1997 Calmac (Manufacturer) website
95 | Launch campaign to encourage adoption of EER 10.8 room A/C's @ end of life | R: Energy Star Room A/C (EER 10.8) | 4 | Residential | Cooling | All residential cooling using room A/Cs | EER (BTU/W-h) | 10.8 | 9.8 | 707.5 | 574.9 | 707.5 | 574.9 | 132.6 | 10 | 10 | NREL Retrofit efficiency measures database Primary Source: Savings: First principles Cost: NREL retrofit measure database
96 | Launch campaign to encourage adoption of max tech Room A/Cs | R: EER 13 Room AC | 2 | Residential | Cooling | All residential cooling using room A/Cs | EER (BTU/W-h) | 13 | 9.8 | 724 | 385 | 724 | 385 | 339 | 10 | 10 | 1) Costs: Used a more recent, not yet published version of: "Updated Building Sector Appliance and Equipment Costs and Efficiency." August 2013. EIA. http://www.eia.gov/analysis/studies/buildings/equipcosts/pdf/full.pdf. Room Air Conditioner Standards Rulemaking. http://www1.eere.energy.gov/buildings/appliance_standards/product.aspx/productid/41. Residentical Energy Consumption Survey (RECS) 2005. http://www.eia.gov/consumption/residential/data/2005/c&e/airconditioning/pdf/alltables1-11.pdf 2) Savings: First principles; Bouza
97 | Need to develop SEER 24 Central A/C in homes at end of life - TARGET | R: SEER 24 CAC* | 0 | Residential | Cooling | Total energy consumption by residential central air conditioning in single- and multi-family homes | SEER (BTU/W-h) | 24 | 12.225 | 7322.4 | 4680 | 7322.4 | 4680 | 2642.4 | 17 | 17 | Navigant consulting, Web search (Westinghouse vs. SEER 13), www.acwholesalers.com; CAC & HP TSD; Peer reviewer expressed concerns over data quality because it was a manufacturer case study in an ideal climate (therefore reduced data quality from 5 to 4) Primary Source: Savings: first principles Cost: Navigant Consulting, personal communication
99 | Launch campaign to encourage adoption of whole house fans in existing buildings in temperate and north climates | R: Add whole house fan [E] | 3 | Residential | Cooling | Central cooling in single family existing homes in very cold/cold, mixed-humid, and marine climates | Energy Savings (%) | 24.75% | 0% | 0 | 0 | 0 | 0 | 692 | 17 | 17 | Web search ($292)+ 8 hours labor for retrofit at $50/hr Primary Source: Southface Energy Institiute & Oak Ridge National Laboratory FEMP Technology Fact Sheet: Whole House Fan. (1999)
100 | Launch campaign to encourage adoption of whole house fans in new buildings in temperate and north climates | R: Add whole house fan (N) | 3 | Residential | Cooling | Central cooling in new homes in very cold/cold, mixed-humid, and marine climates | Energy Savings (%) | 24.75% | 0% | 392 | 0 | 392 | 0 | 392 | 17 | 17 | Web search ($292)+ 2 hours labor for installation at $50/hr Primary Source: Southface Energy Institiute & Oak Ridge National Laboratory FEMP Technology Fact Sheet: Whole House Fan. (1999)
102 | Develop a standard for adoption of variable speed motors in residential blowers | R: Variable Speed Blower | 4 | Residential | Ventilation | Furnace Fans Pumps | Blower energy savings (%) | 0.51 | 0 | 0 | 0 | 0 | 0 | 296 | 20 | 20 | Lekov et. Al. ; Electricity and Natural Gas Efficiency Improvements for Residential Gas Furnaces in the U.S.; Residential HVAC Electronically Commutated Motor Retrofit Report Primary Source: Murray, M. & Fitzpatrick, S. Residential HVAC Electronically Commutated Motor Retrofit Report Table of Contents. Advanced Energy (2012) Other Supporting Sources: Franco, V., Lutz, J., Lekov, A. & Gu, L. Furnace Blower Electricity: National and Regional Savings Potential. Florida Solar Energy Center(2008)
104 | Move to standardize variable speed motors in commercial HVAC compressors | C: Var-speed compressor in AC | 4 | Commercial | Heating & Cooling | All commercial cooling, and heating with ASHPs | Energy Savings (%) | 25.3% | 0% | 0 | 0 | 0 | 0 | 0.066667 | 15 | 15 | "Potential electricity savings by variable speed control of compressor for air conditioning systems", Henry Nasution; Mat Nawi Wan Hassan
105 | Encourage retro-commissioning of commercial buildings for all buildings (only HVAC is considered, and assumes no new equipment costs) | C: Retro-commissioning (HVAC only) | 4 | Commercial | HVAC | All commercial HVAC energy use | Energy Savings (%) | 16% | 0% | 0.3 | 0 | 0.3 | 0 | 0.3 | 5 | 5 | Costs and energy savings for buildings > 100,000 SF: Pg . 145,155, 158. "Building Commissioning: A Golden Opportunity for Reducing Energy Costs and Greenhouse Gas Emissions", Mills, E.; Energy Efficiency (2011) 4:145–173.
109 | Move to standardize PSC motors in commercial blowers | C: Comm. PSC blowers | 4 | Commercial | Ventilation | All commercial ventilation | Blower energy savings (%) | 0.14 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 20 | Home energy magazine article
110 | Standardize high efficiency circulator pumps in homes | R: Heating circulator pumps | 3 | Residential | Heating/Cooling/Water | Furnace Fans Pumps | Energy Savings (%) | 21.6% | 0% | 0 | $82-92 | 0 | $82-92 | 59 | 20 | 20 | Home energy magazine article; Assessment of New Circulator Pump Technology, EPRI 1020132, 11/15/2010; Multiple sources from online vendors such as Amazon, PexUniverse.com, Grainger, etc. Primary Source: Waide, P. & Brunner, C. Energy-Efficiency Policy Opportunities for Electric Motor-Driven Systems. International Energy Agency (2011).
111 | Increase deployment of high efficiency circulator pumps in commercial buildings | C: Efficient circulator pumps | 5 | Commercial | Heating/Cooling/Water | All commercial circulator pumps | Energy Savings (%) | 60% | 0% | 0 | 0 | 0 | 0 | 0.05 | 20 | 20 | Primary Source: pg. 58 quotes 80-90% improvement. Waide, P. & Brunner, C. Energy-Efficiency Policy Opportunities for Electric Motor-Driven Systems. International Energy Agency (2011). Other Supporting Sources: Byrne, Jeanne, "Motors Matter". Home Energy Magazine Online 1-7 (2000)
112 | Move to standardize condensers in natural gas residential furnaces | R: Condensing Gas Furnace | 4 | Residential | Heating | Total residential heating energy use by natural gas furnaces in all homes. | Energy Savings (%) | 11% | 0% | 0 | 0 | 0 | 0 | 840 | 23 | 23 | NREL Retrofit efficiency measures database; Weil-McLain
114 | Demonstrate and deploy sprayed mesh residential AC's | R: Sprayed mesh AC | 3 | Residential | Cooling | Total residential cooling (CAC & ASHP) other than room A/Cs | Energy Savings (%) | 6% | 0% | 6818.44 | 6545 | 6818.44 | 6545 | 273.44 | 16 | 16 | Friterm, table 1 cooling/power draw ratios,ecomesh; Assume 1.7 year payback as listed for other technologies plus 4 hours to retrofit; Condenser-Air Evaporative Pre-Cooler Test Protocol report for SoCal Edison (Nov 2012) Primary Source: Acul, H. Air Cooled Condensers And Their Effect On Energy. 1-13 (2008) Other Supporting Sources: Choi-Granade et. Al.; "Unlocking Energy Efficiency in the U.S. Economy"; McKinsey & Company (2009)
115 | Demonstrate and deploy sprayed mesh commercial AC's | C: Sprayed mesh AC | 3 | Commercial | Cooling | Total commercial electric load of rooftop AC units (residential style) | COP | 3.71 | 3.03 | 0 | 0 | 0 | 0 | 3.2812 | 15 | 15 | Friterm, table 1 cooling/power draw ratios Primary Source: Acul, H. Air Cooled Condensers And Their Effect On Energy. 1-13 (2008) Other Supporting Sources: Choi-Granade et. Al.; "Unlocking Energy Efficiency in the U.S. Economy"; McKinsey & Company (2009)
118 | Move to standardize improved motors in ceiling fans | R: Efficient Ceiling Fan Motors | 4 | Residential | MELs | Total energy use by residential ceiling fans | CFM/W | 272 | 100 | 86 | 0 | 86 | 0 | 86 | 14 | 14 | Energy Star database for performance (http://downloads.energystar.gov/bi/qplist/ceiling_fan_only_prod_list.pdf?419d-5d10), Energy Star savings calculator for cost (http://www.energystar.gov/ia/business/bulk_purchasing/bpsavings_calc/Ceiling_Fan_Savings_Calculator_Consumer.xls?e8fd-5d0d) Primary Source: Environmental Protection Agency, "ENERGY STAR Ceiling Fan Product List", 2012
119 | Launch campaign to encourage adoption of duct insulation in existing homes | R: Duct Insulation (E) | 4 | Residential | HVAC | Existing homes lacking duct insulation | Energy Savings (%) | 20% | 0% | 910 | 0 | 910 | 0 | 910 | 20 | 20 | Primary Source: Hendron, R., and Engebrecht, C. 2010. Building America House Simulation Protocols. DOE/GO-102010-3141. http://apps1.eere.energy.gov/buildings/publications/pdfs/building_america/house_simulation_revised.pdf NREL Residential Efficiency Measures Database. http://www.nrel.gov/ap/retrofits/measures.cfm?gId=2&ctId=16 Mills, E.. et al. 2007. "Home Energy Saver: Documentation of Calculation Methodology, Input Data, and Infrastructure." Lawrence Berkeley National Laboratory Report No. 51938. http://evanmills.lbl.gov/pubs/pdf/home-energy-saver.pdf
120 | Launch campaign to encourage adoption of duct insulation in existing commercial buildings | C: Duct Insulation (E) | 4 | Commercial | HVAC | All commercial heating and cooling in existing buildings without insulated ducts | Energy Savings (%) | 40% | 0% | 0.88 | 0 | 0.88 | 0 | 0.88 | 20 | 20 | Primary Source: Same as above
121 | Launch campaign to encourage annual maintenance of heaters in homes | R: Heater Maintenance | 4 | Residential | Heating | All homes heating (including sectional/secondary) | Energy Savings (%) | 5% | 0% | 300 | 0 | 300 | 0 | 300 | 1 | 1 | Choi-Granade et. al. (2009). "Unlocking Energy Efficiency in the U.S. Economy". McKinsey and Company
122 | Demonstrate and deploy predictive control thermostats in all homes | R: Predictive Thermostats (NEST) | 3 | Residential | HVAC | Total residential central AC and heating energy consumption | Energy Savings (%) | 10.47% | 0% | 370 | 0 | 370 | 0 | 370 | 35 | 35 | Savings: Cho, Energy Conservation and Management 44 (2003); Cost: Nest (http://www.nest.com/inside-and-out/)
123 | Demonstrate and deploy predictive control thermostat in all commercial buildings | C: Predictive Thermostats | 3 | Commercial | HVAC | All commercial HVAC energy use | Energy Savings (%) | 10.47% | 0% | 0 | 0 | 0 | 0 | 0.24533 | 35 | 35 | Savings: Cho, Energy Conservation and Management 44 (2003); Cost: Nest (http://www.nest.com/inside-and-out/)
124 | Deploy programmable thermostats in existing homes | R: Programmable Thermostats | 4 | Residential | HVAC | All heating and cooling in existing homes | Energy Savings (%) | 3.75% | 0% | 0 | 0 | 0 | 0 | 50 | 35 | 35 | RECS 2009 survey analysis (46% have thermostats; 60% use for setback to save 200 HDD -> 5%), so 75% of 5% savings Primary Source: Energy Information Agency. "Residential Energy Consumption Survey, 2009". Department of Energy (2012)
125 | Reduce over sizing in home heaters | R: Right Sized Heater | 4 | Residential | Heating | Total residential heating in all homes | Energy Savings (%) | 5% | 0% | 0 | 0 | 0 | 0 | -100 | 18 | 18 | SWAG Primary Source: Djunaedy, E., Van Den Wymelenberg, K., Acker, B., Thimmana, H. (n.d.). "Oversizing of HVAC System: Signatures and Penalties. Energy and Buildings" Energy and Buildings, In Press Florida Solar Energy Center, "Right-Size Heating and Cooling Equipment", Department of Energy (2002) NREL Measure Database (for cost per unit capacity) Other Supporting Sources: Choi-Granade et. Al.; "Unlocking Energy Efficiency in the U.S. Economy"; McKinsey & Company (2009)
126 | Reduce over sizing in commercial heaters | C: Right Sized Heater | 4 | Commercial | Heating | All commercial heating | Energy Savings (%) | 5% | 0% | -0.08 | 0 | -0.08 | 0 | -0.08 | 15 | 15 | McKinsey report (based on residential) Primary Source: Djunaedy, E., Van Den Wymelenberg, K., Acker, B., Thimmana, H. (n.d.). "Oversizing of HVAC System: Signatures and Penalties. Energy and Buildings" Energy and Buildings, In Press Florida Solar Energy Center, "Right-Size Heating and Cooling Equipment", Department of Energy (2002) NREL Measure Database (for cost per unit capacity) Other Supporting Sources: Choi-Granade et. Al.; "Unlocking Energy Efficiency in the U.S. Economy"; McKinsey & Company (2009)
127 | Launch campaign to encourage adoption of duct sealing in existing homes | R: Duct Sealing (E) | 3 | Residential | HVAC | Existing homes with unsealed ducts | Energy Savings (%) | 10% | 0% | 638.22 | 0 | 638.22 | 0 | 638.22 | 20 | 20 | 1) Energy savings from: a) http://www.aeroseal.com/what-we-do/introduction.html; http://www.aeroseal.com/problem-we-solve/FAQ-commercial.html; b) $0.40/sq.ft. from "Energy Savings Potential and RD&D Opportunities for Residential Building HVAC Systems. October 2012. http://www1.eere.energy.gov/buildings/pdfs/residential_hvac_research_opportunities.pdf
128 | Launch campaign to encourage adoption of duct sealing in existing commercial buildings | C: Duct Sealing (E) | 3 | Commercial | HVAC | All commercial heating and cooling in existing buildings with unsealed ducts | Energy Savings (%) | 20% | 0% | 0 | 0 | 0 | 0 | 0.405 | 20 | 20 | Aeroseal website: http://www.aeroseal.com/commercial_duct_sealing.html Primary Source: Modera, M Fixing Duct Leaks in Commercial Buildings ASHRAE Journal June 2005 TIAX. Energy Impact of Commercial Building Controls and Performance Diagnostics?: Market Characterization , Energy Impact of Building Faults and Energy Savings Potential. Construction 413 (2005).
129 | Demonstrate and deploy household nighttime economizers | R: Night Economizer | 3 | Residential | Cooling | Total energy consumption by residential central air conditioning in single-family homes | Energy Savings (%) | 10% | 0% | 0 | 0 | 0 | 0 | 780 | 16 | 16 | Itron Inc., Kema, Inc. "California Energy Efficiency Potential Study" Pacific Gas & Electric (2008)
132 | Demonstrate and deploy low temperature heat pumps, climate zones 1 & 2 (no fuel switching) | R: Cold Climate HP, Coldest CZ | 2 | Residential | Heating | Electric heating, proportion of cooling in coldest 2 climates | Energy Savings (%) | 23% | 0% | 6300 | 3300 | 6300 | 3300 | 3000 | 18 | 18 | 1) Savings and incremental cost: Sachs et al, 2009, "Emerging Energy-Saving HVAC Technologies and Practices for the Buildings Sector" 2) Base unit cost: EIA - Technology Forecast Updates – Residential and Commercial Building Technologies, September 2013 3) Assuming energy savings are reduced by roughly 10% between ASHP operating at 17 degF and below 0 degF (Product & Technology Review PTR #19 December 2007 Acadia Heat Pump, http://www.energyideas.org/documents/Factsheets/PTR/AcadiaHeatPump.pdf) Also, based on energy savings of CC ASHP in measure 778 (25%) (Sachs et al, 2009, "Emerging Energy-Saving HVAC Technologies and Practices for the Buildings Sector")
133 | Demonstrate and deploy reverse cycle chiller (heat pump water heater) to heat water in multifamily homes. The RCC is a water heater which uses a refrigeration cycle with an air‐side evaporator and a water‐side condenser. | R: Reverse Cycle Chiller (multi family) | 2 | Residential | Water heating | Total electric water heating in all multi-family homes | kWh/unit | 1000 | 2700 | 677 | 0 | 677 | 0 | 677 | 13 | 13 | Heller, J. & Cejudo, C. Reverse Cycle Chillers for Multifamily Buildings in the Pacific Northwest : Phase I Final Report. Bonneville Power Administration (2009)
134 | Demonstrate and deploy reverse cycle chiller (heat pump water heater) to heat water in select commercial buildings. The RCC is a water heater which uses a refrigeration cycle with an air‐side evaporator and a water‐side condenser. | C: Reverse Cycle Chiller | 2 | Commercial | Water heating | All electric commercial water heating | kWh/100,000 sq. ft | 138723.4043 | 374553.1915 | 0.94 | 0 | 0.94 | 0 | 0.94 | 13 | 13 | Heller, J. & Cejudo, C. Reverse Cycle Chillers for Multifamily Buildings in the Pacific Northwest : Phase I Final Report. Bonneville Power Administration (2009)
135 | Research, demonstrate, and deploy air-to-air heat exchangers in homes | R: Air-to-Air Exchangers | 3 | Residential | Heating | Total residential heating in all homes | Energy Savings (%) | 6.813% | 0% | 1375 | 463 | 1375 | 463 | 912 | 18 | 18 | Beopt default costs Primary Source: Hellevang, K. & Pedersen, C. Air-to-Air Heat Exchangers. North Dakota State University (2009)
138 | Demonstrate and deploy desiccant wheel A/C in commercial buildings in hot-humid climates | C: Desiccant wheel AC, hot-humid CZ | 4 | Commercial | Cooling | Total cooling in hot, humid climates in all commercial buildings | Energy Savings (%) | 25% | 0% | 0.5 | 0.16667 | 0.5 | 0.16667 | 0.33333 | 15 | 15 | S.J. Slayzak and J.P. Ryan; Desiccant Dehumidification Wheel Test Guide (2000) Desroches, L.-B. et al. Max Tech and Beyond (2011)
139 | Demonstrate and deploy desiccant wheel A/C in homes in hot-humid climates | R: Desiccant wheel AC, hot-humid CZ | 4 | Residential | Cooling | Total cooling in hot-humid climates | Energy Savings (%) | 25% | 0% | 0 | 0 | 0 | 0 | 720 | 16 | 16 | S.J. Slayzak and J.P. Ryan; Desiccant Dehumidification Wheel Test Guide (2000) Desroches, L.-B. et al. Max Tech and Beyond (2011)
140 | Demonstrate and deploy chilled beams for heating and cooling in new commercial buildings, except two coldest climates | C: Chilled Beams (N), warm/moderate CZ | 4 | Commercial | Cooling | Total commercial heating and cooling in new buildings, except two coldest climates | Energy Savings (%) | 20% | 0% | 0 | 0 | 0 | 0 | -1 | 15 | 15 | Roth, K., John, D., Zogg, R. & Brodrcik, J. Chilled Beam Cooling. ASHRAE Journal 84-86 (2007) Sachs, H..; Lin, W.; Lowenberger, A.; "Emerging Energy Savings HVAC Technologies and Practices for the Buildings Sector"; ACEEE (2009)
141 | Demonstrate and deploy demand control ventilation in all commercial buildings | C: DCV | 4 | Commercial | Ventilation | All commercial HVAC energy use | Energy Savings (%) | 20% | 0% | 0.17 | 0 | 0.17 | 0 | 0.17 | 15 | 15 | 1) pg. 92-96 of Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. Navigant Consulting (2011) 2) Cost of $617/zone or $0.17/SF from pg. 6 of Hong, T. Fisk, W. Assessment of Energy Savings Potential form the Use of Demand Control Ventilation Systems in General Office Spaces in California. LBNL. July 8, 2009. 3) Data confirmed by pg. 2&8, of Demand-Controlled Ventilation Using CO2 Sensors. Federal Technology Alert. DOE/EE-0293. March 2004.
142 | Demonstrate and deploy displacement ventilation in new commercial buildings | C: Disp. Ventilation (N) | 2 | Commercial | Heating & Cooling | Total HVAC load in new commercial buildings | Energy Savings (%) | 10% | 0% | 0 | 0 | 0 | 0 | 1 | 20 | 20 | Primary Source: Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. (2011) [Cost and efficiency values from page 118] Awbi, Energy Efficient Room Air Distribution ; Renewable Energy (15); Argon Air
143 | Demonstrate and deploy DOAS (dedicated outdoor air systems) with ERV (Energy Recovery Ventilation) in all commercial buildings | C: DOAS w/ ERV | 4 | Commercial | HVAC | Total commercial HVAC energy consumption in all office buildings | Energy Savings (%) | 10%heating, 17% cooling over VAV | 0% | 0.08 | 0 | 0.08 | 0 | 0.0825 | 15 | 15 | PNNL technical support document 19341, MGAE Primary Source: BA Thornton; W Wang; Y Huang; MD Lane; B Liu; "Technical Support Document: 50% Energy Savings for Small Office Buildings"
144 | Demonstrate and deploy dual source heat pumps in homes in non-coldest climates, no fuel switching | R: Dual Source HP | 4 | Residential | Heating & Cooling | Electric heating, proportion of cooling not in coldest 2 climates | Energy Savings (%) | 34.3% | 0% | 7560 | 4680 | 7560 | 4680 | 2880 | 18 | 18 | FEMP Technology alert DOE/E-0220; savings and costs relative to ASHP. Ground loop from Navigant 2009 (Ground‐Source Heat Pumps: Overview of Market Status, Barriers to Adoption, and Options for Overcoming Barriers) $3000/ton for residential retrofit. Baseline cost from NREL Retrofit Measures Database. Primary Source: Hadley, D., Collins, T., Parkerk, S., Cornett, G. & Cavedo, F. Energy Savings from Dual-Source Heat Pump Technology Federal Energy Management Program E-0220 (2000)
146 | Demonstrate and deploy dual source heat pumps in commercial buildings in non-coldest climates, no fuel switching | C: Dual Source HP | 4 | Commercial | Heating & Cooling | Electric space heating, proportion of cooling, excluding coldest climate | Energy Savings (%) | 34.3% | 0% | 11.1542 | 8.65 | 11.1542 | 8.65 | 2.5042 | 15 | 15 | FEMP Technology alert DOE/E-0220; savings relative to ASHP. Baseline cost from RS Means Assemblies Cost Data, 33rd Edition ($8.65 for 40 ton packaged rooftop heat pump, including ductwork and controls). ORNL Residential Retrofti Tech potential ($7000/ton for commercial retrofit) Primary Source: Hadley, D., Collins, T., Parkerk, S., Cornett, G. & Cavedo, F. Energy Savings from Dual-Source Heat Pump Technology Federal Energy Management Program E-0220 (2000)
147 | Demonstrate and deploy improved ground coupling in GSHP in homes | R: Enhance ground HX effectiveness | 1 | Residential | Heating & Cooling | Total residential geothermal heating and cooling | Energy Savings (%) | 30% | 0% | 0 | 0 | 0 | 0 | 0 | 25 | 18 | ORNL Fact sheet
148 | Demonstrate and deploy improved ground coupling in GSHP in commercial buildings | C: Enhance Ground HX Effectiveness | 1 | Commercial | Heating & Cooling | Total commercial ground source heat pump (GSHP) load | Energy Savings (%) | 30% | 0% | 0 | 0 | 0 | 0 | 0 | 25 | 25 | ORNL Fact sheet
149 | Demonstrate 50% more efficient building designs with no capital cost increase | C: 50% whole building savings, same capital cost | 2 | Commercial | All End Uses | All energy consumption in new buildings | Energy Savings (%) | 50% | 0% | 0.14286 | 0 | 0.14286 | 0 | 0.14286 | 40 | 40 | NREL Commercial Buildings team
152 | Demonstrate and deploy attic radiant barrier in existing homes | R: Attic Radiant Barrier, 4% (E) | 3 | Residential | HVAC | Total heating and cooling lost through attics in homes built before 2010 | Energy Savings (%) | 4.286% | 0% | 0 | 152.712 | 0 | 152.712 | 152.712 | 30 | 30 | Next generation troofs.pdf; itron pdf Primary Source: Miller, W. & Kosny, J. Next-Generation Roofs and Attics for Homes. ACEEE Summer Study on Energy Efficiency in Buildings 180-195 (2008)
153 | Replace all commercial lighting with LEDs | C/I: LED (replace all) | 4 | Commercial/Industrial | Lighting | All lighting in all types of commercial and industrial buildings | lumens/watt | 95 | 68 | 498.05 | 97.5 | 498.05 | 97.5 | 358.05 | 13 | 5 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
154 | Replace all residential lighting with LEDs | R: LED (replace all) | 4 | Residential | Lighting | Total lighting energy consumption in all homes | lumens/watt | 76 | 26 | 25.34 | 2.88 | 25.34 | 2.88 | -28.97 | 43 | 2 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization 4) Daily operating hours from the PNNL: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/2012_residential-lighting-study.pdf
155 | Demonstrate and deploy radiant flooring systems in new homes | R: Radiant Heat (N) | 3 | Residential | Heating | Forced hot air systems in new homes | Energy Savings (%) | 9.5% | 0% | 10000 | 3000 | 10000 | 3000 | 7000 | 80 | 20 | http://www.radiantec.com/why/technical-explanation.php Primary Source: Watson, Richard D. Advantages of radiant heat. Fine Homebuilding June-July 1992. http://www.radiantec.com/why/technical-explanation.php Robert Hendron, Ed Hancock; Greg Barker; Paul Reeves. 2006. An Evaluation of Affordable Prototype Houses at Two Levels of Energy Efficiency. NREL/CP-550-38774. Joseph D'agnese. 2009. Radiant Floor Heating. This Old House magazine. http://www.thisoldhouse.com/toh/article/0,,1548320,00.html
156 | Move to standardize improved duct routing in residential codes | R: Duct Routing (N) | 4 | Residential | HVAC | Forced hot air systems in new homes | Duct efficiency | 0.8 | 0.67 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | BTP Technology Fact Sheet Primary Source: Southface Energy Institute, FEMP Technology Alert: Air Distribution System Design, 2003
157 | Move to standardize improved duct routing in commercial codes | C: Duct Routing (N) | 4 | Commercial | HVAC | All furnaces and A/C heating and cooling (i.e., ducts) in new commercial buildings | Duct efficiency | 0.8 | 0.67 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | BTP Technology Fact Sheet Primary Source: Southface Energy Institute, FEMP Technology Alert: Air Distribution System Design, 2003
161 | Demonstrate and deploy minisplit heat pumps in homes | R: Minisplits | 4 | Residential | Heating & Cooling | Total electric heating and cooling in all homes | Energy Savings (%) | 40% | 0% | 6084 | 4680 | 6084 | 4680 | 1404 | 20 | 20 | ACEEE; BOA report; NREL measure database for standard A/C cost Primary Source: Geraghty, K., Baylon, D. & Davis, B. Residential Ductless Mini-Split Heat Pump Retrofit Monitoring. Bonneville Power Administration (2009). Desroches, L.-B. et al. Max Tech and Beyond, Appendix F. Lawrence Berkeley National Laboratory (2011).
162 | Move to standardize variable air volume (VAV) ventilation | C: Move from CAV to VAV | 4 | Commercial | HVAC | All constant air volume (CAV) ventilation in all commercial buildings | Energy Savings (%) | 25% | 0% | 0 | 0 | 0 | 0 | 0.26667 | 20 | 20 | Estimated incremental cost and energy savings were calculated by Phil based on detailed NEMS data tables and Indoor Air Quality Building Education and Assessment Model (I-BEAM). Energy Information Administration. http://www.epa.gov/iaq/largebldgs/i-beam/text/hvac.html#F6.1
168 | Research, demonstrate, and deploy homes that meet Passivhaus specifications | R: Ultra-efficient design (e.g., Passivhaus) | 3 | Residential | All End Uses | Total residential energy consumption in all new homes | Energy Savings (%) | 66% | 0% | 116.0147 | 102.9412 | 116.0147 | 102.9412 | 23532.3529 | 30 | 30 | Passivehouse.us
171 | Move to include building commissioning in new commercial buildings (data for bldgs>100,000SF, taken as max cost & savings for the market for all new bldgs) | C: Commissioning (N) | 5 | Commercial | Building | Total HVAC load in new commercial buildings | Energy Savings (%) | 13% | 0% | 1.16 | 0 | 1.16 | 0 | 1.16 | 5 | 5 | "Building Commissioning: A Golden Opportunity for Reducing Energy Costs and Greenhouse Gas Emissions", Mills, E.; Energy Efficiency (2011) 4:145–173 Other Supporting Sources: Mills, E., Friedman, H., Powell, T., Bourassa, N., Claridge, D., Haasl, T., & Piette, M. A. (2004). “The cost-effectiveness of commercial-buildings commissioning: A meta-analysis of energy and non-energy impacts in existing buildings and new construction in the United States.” Lawrence Berkeley National Laboratory Report No.56637 http://cx.lbl.gov/2004-assessment.html.
180 | Increase deployment of Energy Star 2011 CFLs for residential general use lighting in place of incandescents and halogen | R: Energy Star CFLs | 5 | Residential | Lighting | Total residential incandescent and halogen General Service Lamp (GSL) Medium Screw Bulb (MSB) lighting | lumens/watt | 55 | 15 | 2.72 | 1.2 | 2.72 | 1.2 | -7.05 | 17 | 2 | 1) 2010 U.S. Lighting Market Characterization; 2012 Energy Savings Potential of SSL 2) Daily operating hours from the PNNL: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/2012_residential-lighting-study.pdf
181 | Research, develop, and demonstrate daylight-responsive dimming (Photosensor-Based Lighting Controls) in commercial buildings | C: Perimeter Zone Day Lighting | 4 | Commercial | Lighting | All commercial fluorescents in a perimeter zone | Energy Savings (%) | 40% | 0% | 184.9315 | 0 | 184.9315 | 0 | 184.9315 | 5 | 5 | Cost from PNNL 2005, K-12 Schools AERG (draft) Primary Source: Brambley, M. et al. Advanced sensors and controls for building applications: Market assessment and potential R&D pathways. Energy 156 (2005).at <http://citeseerx.ist.psu.edu/viewdoc/download?doi=10.1.1.111.8772&amp;rep=rep1&amp;type=pdf>
182 | LEDs for holiday lights | R/C: LED Holiday Lights | 4 | Residential and Commercial | Lighting | Total energy use by residential decorative light strings | Energy Savings (%) | 70% | 0% | 8 | 38 | 8 | 38 | -30 | 86 | 3 | Energy.gov LED Lighting - Holiday Lights, http://energy.gov/energysaver/articles/led-lighting
184 | Increase deployment of replacement of incandescent lighting with CFLs for commercial lighting | C: CFLs | 5 | Commercial | Lighting | All commercial incandescent | lumens/watt | 53 | 9.6 | 2.72 | 1.2 | 2.72 | 1.2 | -7.05 | 2.6 | 0.36 | 2010 U.S. Lighting Market Characterization; 2012 Energy Savings Potential of SSL
185 | Demonstrate and deploy dimmable instant start ballasts in commercial and industrial lighting | C/I: Dimmable Instant-Start Ballasts | 2 | Commercial/Industrial | Lighting | All commercial linear fluorescent lighting (T-12, T-8, T-5) | Energy Savings (%) | 15% | 0% | 31.19 | 10.89 | 31.19 | 10.89 | 20.3 | 5 | 5 | Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005).
188 | Residential and commercial fluorescent lighting ballast standard, effective in 11/2011 with compliance date of 11/2014. | C/R: Electronic Ballast Standard (2014) | 5 | Residential and Commercial | Lighting | All residential and commercial fluorescent lighting (GSL medium screw CFL MSB, CFL Reflector, T12, T8, T5, and other miscellaneous fluorescent lamps). | Energy Savings (%) | 6.97% | 0% | 7.45 | 7.32 | 7.45 | 7.32 | 0.13 | 5 | 5 | Navigant Consulting & Pacific Northwest National Laboratory Final Rule Technical Support Document Energy Conservation Program for Consumer Products and Certain Commercial And Industrial Equipment: Fluorescent Lamp Ballasts. Department of Energy (2011)
190 | Demonstrate elimination of constant electrode heating resulting in more efficient commercial and industrial ballasts | C/I: Elimination of Constant Electrode Heating | 2 | Commercial/Industrial | Lighting | Rapid-Start/Dimming Ballasts, Comm/Industrial | Energy Savings (%) | 5% | 0% | 31.19 | 10.89 | 31.19 | 10.89 | 20.3 | 23 | 23 | Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005).
193 | Deploy HID ceramic arc tubes to replace mercury vapor (MV) and quartz metal halide (MH) lamps in all sectors | C/R/I/O: Ceramic HID Arc Tube to replace MV & quartz MH | 2 | Commercial/Industrial/Outdoor/Residential | Lighting | All residential mercury-vapor and metal halide HID lighting | lumens/watt | 67.5 | 56 | 38 | 35 | 38 | 35 | 3 | 23 | 23 | Navigant 2005 Lighting Market Characterization II; Navigant 2002 Lighting Market Characterization I
195 | Deploy HID dimmable ballasts in commercial, industrial, and outdoor HID and fluorescent lighting | C/I/O: HID Dimmable Ballasts to replace HID and Fluorescents | 3 | Commercial/Industrial/Outdoor | Lighting | HIDs and Fluorescents - Dimmable Ballasts (Comm/Indust/Outd) | Energy Savings (%) | 15% | 0% | 223 | 98 | 223 | 98 | 125 | 20 | 20 | Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005).
200 | Demonstrate HID instant restrike to enable HIDs to have larger market share over incandescent and halogen lamps in commercial and industrial applications | C/I: HID Instant Restrike | 2 | Commercial/industrial | Lighting | Incandescents/Halogen for HID instant restrike (Comm/Indus) | lumens/watt | 85 | 24.8 | 0 | 0 | 0 | 0 | 92.5926 | 0.36 | 0.36 | Navigant 2005 Lighting Market Characterization II
202 | Research HID novel gas as a replacement to incandescents in commercial lighting | C: HID Novel Gas (e.g. Cesium) | 1 | Commercial | Lighting | Incandescent | lumens/watt | 45 | 24.8 | 41 | 13.68 | 41 | 13.68 | 101.1852 | 0.36 | 0.36 | Navigant 2005 Lighting Market Characterization II
204 | Standardize high efficiency ballasts in fluorescent lights in commercial and residential buildings | C/R: High-efficiency ballasts | 4 | Residential and Commercial | Lighting | All residential and commercial fluorescent lighting (GSL medium screw CFL MSB, CFL Reflector, T12, T8, T5, and other miscellaneous fluorescent lamps). | Electricity consumption (W/ballast) | 48.5 | 54.5 | 25 | 16 | 25 | 16 | 9 | 5 | 5 | Universal Lighting Technologies http://www.unvlt.com/literature/flyers/he-el_flyer.pdf; http://www.unvlt.com/literature/brochures/ultim8_brochure.pdf Primary Source: Universal Lighting Technologies, "Triad High Efficiency System". Manufacturer (2011)
206 | Deploy wireless occupancy sensors and corresponding wireless lighting snap-on relay in commercial buildings | C: Wireless Lighting Occ. Sensor System | 4 | Commercial | Lighting | All commercial lighting, per square foot stock | Energy Savings (%) | 13% | 0% | 0.05 | 0 | 0.05 | 0 | 0.05 | 5 | 5 | 1) Pg. 173 from Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005). 2) Costs obtain from pg. 121, NREL. 2011. Advanced Energy Retrofit Guide for K-12 Schools (Draft). EERE Report DOE/GO-102011-3467. Project Lead: Robert Hendron 3) Pg 2.21 from Brambley, M. et al. Advanced sensors and controls for building applications: Market assessment and potential R&D pathways. Pacific Northwest National Laboratory (2005).
208 | Decrease cost & deploy indirect, active solar water heating with gas back up to commercial buildings (no fuel switching) | C: Solar WH Ind Act, Gas BU | 4 | Commercial | Water Heating | Total energy consumption by all commercial gas storage water heaters | Energy Savings (%) | 61% | 0% | 24710.985 | 0 | 24710.985 | 0 | 24710.985 | 13 | 13 | Itron, Inc.; "California Center for Sustainable Energy Solar Water Heating Pilot Program" (3/2011) Federal Energy Management Program, "Solar Water Heating with Low-Cost Plastic Systems" (1/2012) Other Supporting Sources: Hudon, Burch "Solar Water Heating Roadmap" (in preperation)
209 | Demonstrate and deploy integrated white LED package for residential and commercial lighting | C/R: Integrated White LED Package | 3 | Commercial/Residential/Industrial | Lighting | Total residential and commercial lighting | Quads consumed | 2.8 | 8.3 | 40 | 15 | 40 | 15 | 25 | 3 | 3 | Navigant 2005 Lighting Market Characterization II -- assumes access to 20% of sockets in lighting market
210 | Efficient power supplies (aggregated other measures) | C/R: Improved power supplies | 2 | Residential and Commercial | MELs | Total energy use by residential desktop PCs | Energy Savings (%) | 25% | 0% | 0 | 0 | 0 | 0 | 32 | 4 | 4 | TIAX 2004
211 | Max tech desktop (combining other measures) | C: Max tech desktop | 2 | Commercial | MELs | Total energy use by residential desktop PCs | Energy Savings (%) | 80% | 0% | 882.625 | 490 | 882.625 | 490 | 392.625 | 4 | 4 | TIAX 2007, 2004, ACEEE 2009 Primary Source: Roth, K.W., Mckenney, K., Ponoum, R. & Paetsch, C. Residential Miscellaneous Electric Loads: Energy Consumption Characterization and Savings Potential. Energy 197 (2007). Other Supporting Sources: Cost data are from google searches of commercially available appliances
212 | Research, demonstrate and deploy low-wattage HID lighting as replacement to incandescent | C/R: Low-Wattage HID | 2 | Residential and Commercial | Lighting | Total residential and commercial incandescent lighting (MSB, reflectors, and other) | lumens/watt | 85 | 24.8 | 6.6667 | 0.8 | 6.6667 | 0.8 | 5.8667 | 0.36 | 0.36 | Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005). Other Supporting Sources: Cost data are from google searches of commercially available appliances
213 | Demonstrate and deploy Metal Halide Electronic Ballasts for use in commercial, industrial and outdoor lighting | C/I/O: Metal Halide Electronic Ballasts | 3 | Commercial/Industrial/Outdoor | Lighting | MH (C,I,O) | Energy Savings (%) | 25% | 0% | 140 | 80 | 140 | 80 | 60 | 23 | 23 | Navigant 2005 Lighting Market Characterization II
215 | Demonstrate and deploy LED PARs as replacement for incandescent reflectors in residential, commercial, industrial and outdoor lighting | R/C/I/O: PAR LEDs | 4 | Commercial/Industrial/Outdoor | Lighting | All residential, commercial, industrial and outdoor reflector lamps | lumens/watt | 67 | 15 | 39.5 | 4.7 | 39.5 | 4.7 | -12.2 | 23 | 2 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
216 | Display innovative power management for desktop PCs and TVs | R: Display Power Management | 2 | Residential | MELs | All commercial and residential computers and TVs for power management | Energy Savings (%) | 20% | 0% | 0 | 0 | 0 | 0 | 0.8 | 4 | 4 | Personal communication: Nordman, LBNL (12/2010)
218 | Deploy hard-wired occupancy sensors to reduce energy use for commercial lighting | C: Hard-wired lighting occupancy sensors | 4 | Commercial | Lighting | All commercial lighting, per square foot stock | Energy Savings (%) | 13% | 0% | 0.335 | 0 | 0.335 | 0 | 0.335 | 5 | 5 | PNNL 2005 Primary Source: Leach, M., Hale, E., Hirsch, A. & Tocellini, P. Grocery Store 50 % Energy Savings Technical Support Document Grocery Store 50 % Energy Savings Technical Support Document. 174 (2009). Other Supporting Sources: Brambley, M. et al. Advanced sensors and controls for building applications: Market assessment and potential R&D pathways. Pacific Northwest National Laboratory (2005).
219 | Demonstrate and deploy off-grid luminaires for outdoor lighting | O: Solar outdoor lighting | 2 | Outdoor | Lighting | All lighting, Outdoor | Energy Savings (%) | 100% | 0% | 0 | 0 | 0 | 0 | 80.03 | 8 | 8 | Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005). Other Supporting Sources: Cost data are from google searches of commercially available appliances
220 | Deploy personal controls over lighting in commercial buildings | C: PDA lighting controls | 4 | Commercial | Lighting | Fluorescent/Incandescent, Commercial office | Energy Savings (%) | 25% | 0% | 0 | 0 | 0 | 0 | 57 | 3.87 | 3.87 | Navigant 2005 Lighting Market Characterization II
221 | Deploy personal controls over lighting in residential buildings | R: PDA lighting controls | 4 | Residential | Lighting | Total lighting energy consumption in all homes | Energy Savings (%) | 5% | 0% | 0 | 0 | 0 | 0 | 2500 | 5 | 5 | Navigant 2005 Lighting Market Characterization II
222 | Move from standardized T-12 lighting to T-8 in commercial, industrial and outdoor lighting | C/I/O: T-12 to T-8 Standard (2014) | 5 | Commercial/Industrial/Outdoor | Lighting | T12 Fluorescents, C/I/O | lumens/watt | 90 | 78 | 12.37 | 14.7 | 12.37 | 14.7 | -2.33 | 5 | 5 | FLB Final Rule TSD, Chapter 5, pg. 5-23
223 | Deploy spectrally enhanced lighting to commercial buildings | C: Spectrally Enhanced Lighting | 3 | Commercial | Lighting | All commercial linear fluorescent lighting (T-12, T-8, T-5) | Quads consumed | 1.97 | 2.37 | 4.95 | 3 | 4.95 | 3 | 1.95 | 5 | 5 | Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005).
224 | Increase deployment of solid state lighting (SSL) signage fixtures in commercial lighting | C: SSL Signs | 5 | Commercial | Lighting | All energy consumption of all types of commercial signs | Quads consumed | 0.012 | 0.112 | 0 | 0 | 0 | 0 | -1854.86 | 15 | 15 | Primary Source: Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005). Other sources: Navigant 2008 Energy Savings LEDs Niche Apps. 3) Lifetime: 15 years from Niche LIghting Final Report. NCI. 2008. pg. 26
226 | More efficient set-top boxes: Service Provider Pays (SPP) | R: Set-Top Box | 5 | Residential and Commercial | MELs | Total energy use by residential set-top boxes | Energy Savings (%) | 25% | 0% | 0 | 0 | 0 | 0 | 0.5 | 5 | 5 | Personal communication: Nordman, LBNL (12/2010)
229 | Replace commercial lighting with OLEDs - TARGET | C: OLEDs, SSL Program Goal (2020)* | 0 | Commercial | Lighting | All lighting in all types of commercial and industrial buildings | lumens/watt | 190 | 67 | 85 | 97.5 | 85 | 97.5 | -55 | 13 | 5 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
232 | Deploy switch-based occupancy sensors/fixture with a controller in residential buildings | R: Lighting Occ. Sensor/Fixture + ctrl | 4 | Residential | Lighting | Total lighting energy consumption in all homes | Energy Savings (%) | 10% | 0% | 44 | 0.56 | 44 | 0.56 | 5.43 | 20 | 5 | Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005). Other Supporting Sources: Cost data are from google searches of commercially available appliances
233 | Audio/video inter-device power control | R: Audio/video inter-device power control | 2 | Residential | MELs | Total residential audio/video power control energy use | Energy Savings (%) | 10% | 0% | 0 | 0 | 0 | 0 | 0.1 | 7 | 7 | Personal communication: Nordman, LBNL (12/2010)
234 | Increase deployment of efficient pool pump motors, pipe design and fittings, and filter selection in residential pools | R: Improved Pool Pump System Design | 5 | Residential | MELs | Total energy use by residential pool pumps | Energy Savings (%) | 63% | 0% | 0 | 0 | 0 | 0 | 79 | 10 | 10 | 1) Pacific Gas & Electric, Sempra Energy; "Codes and Standards Enhancement Initiative: Draft Report Residential Swimming Pools", (2007) 2) Roth, K.W., Mckenney, K., Ponoum, R. & Paetsch, C. Residential Miscellaneous Electric Loads: Energy Consumption Characterization and Savings Potential. Tiax (2007)
240 | Residential Sector Energy Efficient Ethernet (IEEE 802.3az) | R: EE Ethernet (802.3az) | 5 | Residential | MELs | Total commercial and residential energy use by energy efficient ethernet | Energy Savings (%) | 12% | 0% | 0 | 0 | 0 | 0 | 0.03 | 4 | 4 | 1) 12% savings updated according to pg. 9-175 of Lanzisera, Nordman, Brown. LBNL. ACEEE Summer Study on Energy Efficiency of Buildings. 2010. http://www.aceee.org/files/proceedings/2010/data/papers/2195.pdf
248 | Increase deployment of infrared toaster ovens | R: Infrared toaster | 3 | Residential | MELs | Total energy use by residential toaster ovens | Energy Savings (%) | 20% | 0% | 125 | 88 | 125 | 88 | 37 | 7 | 7 | TIAX 2007
250 | Introduce minimum active power standard for new residential TVs | R: Introduce TV Active Power Standard | 5 | Residential | MELs | Total energy consumption by residential TVs | Energy Savings (%) | 50% | 0% | 180 | 170 | 180 | 170 | 10 | 5 | 5 | TIAX 2007 Primary Source: Roth, K.W., Mckenney, K., Ponoum, R. & Paetsch, C. Residential Miscellaneous Electric Loads: Energy Consumption Characterization and Savings Potential. Energy 197 (2007). Other Supporting Sources: Cost data are from google searches of commercially available appliances
252 | Distribution transformers standard effective in 2013, with compliance date of 2016. | C: Distribution Transformers Standard (2016) | 3 | Commercial | MELs | All types of distribution transformers in all commercial buildings (mmBTUs, site) | Energy Savings (%) | 9.901% | 0% | 39061.0703 | 38024.5009 | 39061.0703 | 38024.5009 | 1036.5694 | 32 | 32 | TSD 2013
269 | Residential/commercial televisions that meet Energy Star specifications. % energy savings was obtained from 2011 Energy Star specifications. | R/C: Energy Star TVs | 4 | Residential | MELs | Total energy consumption by residential TVs | kWh/yr | 130.086 | 197.246 | 0 | 0 | 0 | 0 | 30.3907 | 10 | 10 | 1) Baseline consumption obtained from NCI MEL report. 2013. http://www.eia.gov/analysis/studies/demand/miscelectric/pdf/miscelectric.pdf 2) Improved performance obtained from Energy Star Program Requirements v5.3, effective in 09/30/2011. http://www.energystar.gov/sites/default/files/specs//private/Televisions_Program_Requirements_V5_3.pdf
272 | PC network presence proxying | C: PC Network Presence | 2 | Commercial | MELs | All commercial and residential standby power losses | Energy Savings (%) | 30% | 0% | 0 | 0 | 0 | 0 | 0 | 7 | 7 | Personal communication with Nordman (LBNL) on Dec 15, 2010
275 | Deploy restructured laboratory fume hoods with automatic sash closure. This technology has an automatic sash closure system on a VAV hood that is controlled by an occupancy sensor. | C: Auto Sash Fume Hoods | 4 | Commercial | MELS | Total energy use by fume hoods | Energy Savings (%) | 50% | 0% | 0 | 0 | 0 | 0 | 5100 | 10 | 10 | 1) Pg. 5&7 of the Advanced Technologies for High Performance Laboratory Fume Hoods Scoping Report. Craig Wray, Paul Mathew. Lawrence Berkeley National Laboratory. November 30, 2012. * Cost calculated from page 5 of the report, where cost of standard CAV unit is $11,000. A standard VAV adds $2000 per hood, and for a 12" valve and controller and $300-$600 for a VAV blower. An automated sash costs an additional $2,500-$2,700 per unit including IR sensors and closure control. Therefore, incremental cost of VAV with auto closure over a standard CAV was estimated to be $2000+$2,600+$500 = $5,100. 2) Federal to commercial scaling of 26.8% based on Federal lab space square footage of 175.5 mil SF, and 654 mil SF of total lab space in the US (Craig Wray, LBNL). To check with CBECs: commercial other building types category SF, which includes labs is 2,043 mil SF.
281 | Introduce standby standards for residential electric appliances | R: 1W Standby | 5 | Residential | MELs | Total residential standby power losses | Standby energy used, TWh/yr | 50 | 150 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | Choi-Granade, C. e. (2009). Unlocking Energy Efficiency in the U.S. Economy. McKinsey & Company.
282 | Introduce standby standards for commercial electric appliances | C: 1W Standby | 5 | Commercial | MELs | Total standby power energy loss in all commercial buildings | Standby energy used, TWh/yr | 45 | 135 | 0 | 0 | 0 | 0 | 0.50803 | 5 | 5 | Choi-Granade, C. e. (2009). Unlocking Energy Efficiency in the U.S. Economy. McKinsey & Company.
287 | Small motors, beyond standards | C/R: Small motors, max tech | 4 | Residential and Commercial | MELs | Total residential, commercial and industrial small motors (not in other analyzed products) | Energy Savings (%) | 92% | 62% | 402 | 243 | 402 | 243 | 159 | 12 | 12 | MTAB Report, Appendix A Motors; TSD Primary Source: Department of Energy, Small Electric Motors Final Rule Technical Support Document (2010) Desroches, L.-B. et al. Max Tech and Beyond (2011)
288 | Deploy variable speed motors in place of single-speed motors in multiple residential & commercial applications | C/R: Motors in other products | 4 | Residential and Commercial | MELs | Total energy use by variable speed drive (VSD) motors in A/C, refrigeration, washing machines, and freezers | Energy Savings (%) | 30% | 0% | 0 | 0 | 0 | 0 | 175 | 12 | 12 | MTAB Report, Appendix A Motors
289 | Deploy best practice energy management for data centers | C: Data center energy management | 4 | Commercial | MELs | Total energy use by data centers (OYP: it seems this is electricity consumption/IT equipment consumption only, but need to verify the market against a reliable source) | Energy Savings (%) | 40% | 0% | 80000000 | 100000000 | 80000000 | 100000000 | -14000000 | 4 | 4 | 1) Pg. 9-10, Report to Congress on Server and Data Center Energy Efficiency Public Law 109-431. US EPA. Energy Star Program. August 2, 2007. 2) Costs vary. The cost estimates were generated by Phil.
291 | Adjusts time between defrost cycles based on need (time of last cycle, humidity sensor, number of door openings) in residential refrigerators | R: Refrig. Adaptive Defrost | 4 | Residential | Refrigeration | All residential refrigerators and freezers | Energy Savings (%) | 3.5% | 0% | 0 | 0 | 0 | 0 | 8 | 17 | 17 | DOE TSD, http://www.aps.com/main/services/business/WaysToSave/BusWaysToSave_59.html, web search for comparing products, article (http://www.rdmag.com/New-To-Market/2010/06/Manufacturing-Thermal-Green-refrigerator-controller-helps-conserve-wasted-energy/ Primary Source: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation
292 | Improve supermarket compressor rack in new systems by using compressor modulation | C: Supermarket Compressor Racks Modulation | 3 | Commercial | Refrigeration | All supermarket compressor racks | Energy Savings (%) | 5% | 0% | 0 | 0 | 0 | 0 | 19008 | 15 | 15 | Table 5-9, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
293 | Encourage supermarket owners to add doors to display cases | C: Display Cases + Doors | 4 | Commercial | Refrigeration | All energy use by supermarkets' medium temperature refrigerated display cases without doors | Energy Savings (%) | 30% | 0% | 0 | 0 | 0 | 0 | 400 | 10 | 10 | http://supermarketnews.com/technology/new_tests_support_1004/; http://www.aps.com/main/services/business/WaysToSave/BusWaysToSave_59.html; http://arstechnica.com/science/news/2011/10/redesign-improves-energy-efficiency-of-supermarket-cold-food-cases.ars ATE 31: 3055 Primary Source: Garry, M; "New Tests Support Doors on Cases", Supermarket News 10/4/2010 Garry, M; "Fresh & Easy Installs Case Doors in 35 Stores" Supermarket News 9/20/2011; NCI Internal Report & Market Study
294 | Use efficient DC condenser fans (ECM motors) in new commercial refrigeration equipment. This will be ubiquitous - the DOE standard compliance date is 2017, published in March 2014. | C: Refrig. Efficient Condenser Fans, Standard, 2017 | 4 | Commercial | Refrigeration | All commercial high efficiency compressor and condenser fans | Energy Savings (%) | 8% | 0% | 0 | 0 | 0 | 0 | 44.5 | 10 | 10 | Table 5-13,14,17,19,20,22,24,26,27, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
295 | Improve expansion valves and control technology in new commercial walk-in refrigerators | C: Controls and expansion valves in walk in refrig | 4 | Commercial | Refrigeration | Walk-In Coolers, Supermarkets | Energy Savings (%) | 16% | 0% | 0 | 0 | 0 | 0 | 348 | 11 | 11 | Table 5-13, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
296 | Deploy display cases with advanced air curtains for containing cold air | C: Advanced Display case air curtains | 1 | Commercial | Refrigeration | Display Cases, Supermarkets | Energy Savings (%) | 7.5% | 0% | 0 | 0 | 0 | 0 | 150 | 10 | 10 | Table 6-1, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
298 | Add fan to freezer compressors in new residential upright freezers | R: Add fans to upright freezer | 3 | Residential | Refrigeration | Total energy use by all residential upright freezers | Energy Savings (%) | 8% | 0% | 1.449 | 0 | 1.449 | 0 | 1.449 | 17 | 17 | p. 5-53 and Table 5-A.3.7, DOE TSD Primary Source: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation
301 | Standardize Max Tech option for commercial ice machines | C: Max Tech Ice Machine | 2 | Commercial | Refrigeration | All commercial ice machines | Energy Savings (%) | 23% | 0% | 0 | 0 | 0 | 0 | 334 | 8.5 | 8.5 | Table 5-24, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment Primary Source: DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment (http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_refrig_report_10-09.pdf) Other Supporting Sources: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation
303 | Install intelligent defrost controls in commercial reach-in and walk-in freezers. | C: Defrost Controls in Freezers | 3 | Commercial | Refrigeration | All commercial freezers | Energy Savings (%) | 3% | 0% | 0 | 0 | 0 | 0 | 103 | 12 | 12 | Table 5-14,19, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
306 | National campaign to retire older refrigerators at 14 years instead of 18 years | R: Accel. Retire pre-2010 fridges | 4 | Residential | Refrigeration | All residential refrigerators eligible for early retirement | kWh/yr reduction per unit | 435 | 1165 | 0 | 0 | 0 | 0 | 81 | 17 | 17 | TSD, ENERGY STAR market data, http://www.energystar.gov/ia/partners/manuf_res/downloads/Refrigerator_Market_Profile_2009.pdf Primary Source: Department of Energy, "New Opportunities Multiply Savings:Refrigerator Market Report, 2009", 2009 Other Supporting Sources: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation
308 | Reduction or elimination of heaters due to gas-filled glass doors in commercial walk-in refrigeration systems | C: Anti-Sweat Heater Controls | 4 | Commercial | Refrigeration | All walk-in coolers and freezers | Energy Savings (%) | 4% | 0% | 0 | 0 | 0 | 0 | 627 | 15 | 15 | Table 5-13,14, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
310 | Use high efficiency compressors in new commercial refrigeration equipment (variable-speed, etc.) | C: High Efficiency Refrig. Compressor | 3 | Commercial | Refrigeration | All commercial high efficiency compressor and condenser fans | Energy Savings (%) | 10% | 0% | 0 | 0 | 0 | 0 | 342 | 10 | 10 | Table 5-13,14,17,19,20,22,24, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
313 | Use high efficiency condensers in new supermarket refrigeration equipment | C: High Efficiency Rack System Condenser in Supermarket Refrigeration | 4 | Commercial | Refrigeration | All supermarket condensers | Energy Savings (%) | 28% | 0% | 0 | 0 | 0 | 0 | 5000 | 10 | 10 | Table 5-10, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
314 | Encourage use of best practices in design of commercial refrigeration systems | C: Refrig. best practice and designs | 2 | Commercial | Refrigeration | All supermarket refrigeration systems (cond, comp, walk-ins, & display) | Energy Savings (%) | 15% | 0% | 0 | 0 | 0 | 0 | 0 | 12 | 12 | Table 6-1, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
316 | Use high efficiency fan blades in new commercial refrigeration equipment | C: High Efficiency Fan Blades in refrig. | 4 | Commercial | Refrigeration | All commercial high efficiency compressor and condenser fans | Energy Savings (%) | 5.5% | 0% | 0 | 0 | 0 | 0 | 41 | 10 | 10 | Table 5-13,14,17,19,20,22,24 DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
317 | Use brushless DC motors in new compressors for commercial refrigeration equipment | C: Brushless DC Compressor Motor | 3 | Commercial | Refrigeration | All commercial compressors (DC) | Energy Savings (%) | 9% | 0% | 0 | 0 | 0 | 0 | 63 | 15 | 15 | Table 5-17,19,20,22,26,27, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment Primary Source: DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment (http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_refrig_report_10-09.pdf) Other Supporting Sources: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation
318 | Use enhanced evaporator coils in new supermarket display cases | C: Display Cases Enhanced Evaporator Coil | 4 | Commercial | Refrigeration | Display Cases, Supermarkets | Energy Savings (%) | 3% | 0% | 0 | 0 | 0 | 0 | 224.5 | 10 | 10 | Table 5-6,7,8, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
319 | More efficient anti-sweat heating, vinyl/composite frame, and high-performance glass in display cases | C: Refrig. Display case glass doors | 4 | Commercial | Refrigeration | Display Cases, Supermarkets | Energy Savings (%) | 40% | 0% | 0 | 0 | 0 | 0 | 1630 | 10 | 10 | Table 5-7,8, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
320 | Deploy brushless DC evaporator and condenser fan motors in new residential refrigerator-freezers | R: Brushless fan motors in all refrig. | 4 | Residential | Refrigeration | All residential refrigerators and freezers | Energy Savings (%) | 7.56% | 0% | 1.449 | 0 | 1.449 | 0 | 1.449 | 17 | 17 | Table 2.2.1 and p. 5-51, DOE TSD; Byrne motor article suggests condenser fans and evaporator fans represent ~6% of national motor consumption each, compared to compressors
323 | Use advanced controllers in new refrigeration system installs | C: Advanced refrigeration controllers | 4 | Commercial | Refrigeration | All supermarket display cases, compressors, and condensers | Energy Savings (%) | 20% | 0% | 0 | 0 | 0 | 0 | 90000 | 10 | 10 | Table 5-11, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
326 | Use brushless DC motors in evaporators for all commercial refrigeration equipment. ECM evaporator fan motors will be almost ubiquitous starting in 2017 (compliance date) based on DOE standards published in March 2014. | C: Refrig. Evap. B-less DC Motors Standard 2017 | 5 | Commercial | Refrigeration | All commercial refrigeration equipment, except compressor racks and supermarket condensers | Energy Savings (%) | 17% | 0% | 0 | 0 | 0 | 0 | 98 | 12 | 12 | Table 5-6,7,8,13,14,17,19,20,22,26,27, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment Primary Source: Navigant Consulting Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Final Report. Department of Energy (2009)
327 | Use hot gas devices for anti-sweat applications in new display cases, etc. | C: Hot Gas Anti-Sweat | 3 | Commercial | Refrigeration | All energy use by walk-In freezers, reach-ins, and food preparation table | Energy Savings (%) | 14% | 0% | 0 | 0 | 0 | 0 | 127 | 13 | 13 | Table 5-14,17,19,20, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
329 | Use hot gas devices for defrost applications in new display cases, etc. | C: Hot Gas Defrost | 3 | Commercial | Refrigeration | All commercial freezers | Energy Savings (%) | 6% | 0% | 0 | 0 | 0 | 0 | 119.5 | 12.5 | 12.5 | Table 5-14,19, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
330 | Place condenser external to unit in new equip | C: Refrigeration: external heat rejection | 3 | Commercial | Refrigeration | All walk-in freezers | Energy Savings (%) | 10% | 0% | 0 | 0 | 0 | 0 | 1003 | 11 | 11 | Table 5-14, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
331 | Encourage use of refrigerators without ice makers | R: Remove icemakers from refrig. | 3 | Residential | Refrigeration | All residential primary refrigerators with icemakers | kWh/yr/refrigerator - W-hr/cycle; max 9 cycles per day | 512.56 | 596 | 0 | 0 | 0 | 0 | -110 | 17 | 17 | also Meier (1997), Energy and Buildings; Meier A. Energy Use of Ice Making in Domestic Refrigerators. Lawrence Berkeley National Laboratory Report No. LBL-31976, 1995. Primary Source: Meier, A. Martinex, M; "Energy Use of Icemaking in Domestic Refrigerators", LBNL-39183 (1996)
333 | Deploy most efficient ice makers in commercial applications | C: Max Tech Ice Makers | 2 | Commercial | Refrigeration | All commercial ice machines | Energy Savings (%) | 15% | 0% | 0 | 0 | 0 | 0 | 140 | 8.5 | 8.5 | http://www.cee1.org/resrc/facts/com-ice-fx.pdf; http://www.energystar.gov/index.cfm?fuseaction=find_a_product.showProductGroup&pgw_code=CIM Primary Source: Consortium for Energy Efficiency (2007), "Commercial Ice Makers" (http://www.cee1.org/resrc/facts/com-ice-fx.pdf) Other Supporting Sources: ENERGY STAR, "Commercial Ice Machines", http://www.energystar.gov/index.cfm?fuseaction=find_a_product.showProductGroup&pgw_code=CIM
334 | Improve compressor efficiency in new residential refrigerators & freezers | R: Compressor Improvements | 3 | Residential | Refrigeration | All residential refrigerators and freezers | Energy Savings (%) | 14% | 0% | 14.02 | 0 | 14.02 | 0 | 14.02 | 17 | 17 | See calculation in additional market data tab; Tables 5-A.3.2 (and .4, .6) (and also p.5-46), DOE (2009): Preliminary TSD, EE Program for Consumer Products, Refrigerators, Refrigerator-Freezers, and Freezers Primary Source: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation
338 | Refrigerator rulemaking: Residential refrigerator standards were amended/effective in 09/2011 with compliance date in 09/2014. | R: All Refrig. Standard, 2014 | 5 | Residential | Refrigeration | All residential refrigerators and freezers | Energy Savings (%) | 24.5% | 0% | 1.449 | 0 | 1.449 | 0 | 1.449 | 17 | 17 | TSD Primary Source: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation
339 | Deploy and standardize Max Tech refrigerator | R: Max tech refrigerator | 2 | Residential | Refrigeration | All residential refrigerators' energy consumption | Energy Savings (%) | 35% | 0% | 0 | 0 | 0 | 0 | 290.41 | 17 | 17 | Combined 4 other sources "in parallel" Primary Source: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation
340 | Use of high efficiency evaporator fans in new residential refrigerators | R: Improved Evaporator Fan Efficiency in refrig | 3 | Residential | Refrigeration | All residential refrigerators and freezers | Energy Savings (%) | 7% | 0% | 0 | 0 | 0 | 0 | 17.9076 | 17 | 17 | http://www.homeenergy.org/article_preview.php?id=21&article_title=Motors_Matter
341 | Improve insulation in new reach-in, etc. commercial refrigeration equipment | C: Improved Insulation in refrig | 4 | Commercial | Refrigeration | All reach-ins, beverage merchandisers, and display cases | Energy Savings (%) | 3% | 0% | 0 | 0 | 0 | 0 | 331 | 13 | 13 | Table 5-19,20,22,6,7,8, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
342 | Increased insulation thickness for residential freezers and compact refrigerators | R: Increased freezer insulation | 4 | Residential | Refrigeration | Total energy use by residential freezers and compact refrigerators | Energy Savings (%) | 1.5% | 0% | 0 | 0 | 0 | 0 | 28.44 | 17 | 17 | DOE (2009) TSD; see calculation on Addl Markets Tab Primary Source: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation
344 | Replace lighting with LEDs in remote-condensing commercial refrigeration equipment | C: Refrig. Retrofit Lights to LEDs | 4 | Commercial | Refrigeration | All commercial medium temperature and remote condensing display cases where lights can be retrofitted | Energy Savings (%) | 7% | 0% | 0 | 0 | 0 | 0 | 975 | 10 | 10 | 1) TSD for commercial refrigeration, Engineering Analysis Chapter 3. See Additional Data Tab for savings/cost calculation; Only Remote Condensing units can be retrofitted, and there are different potential energy savings with a LED retrofit. For an open display case, the potential energy savings are 6%, and for a display case with doors, the energy savings are 18%. Using Table 10.2.4 from the commercial refrigeration TSD, calculated a weighted average for potential energy savings of commercial refrigerators capable of an LED retrofit. 2) Example: Geolights: http://geolights.com/products_detail.php?id=117 3) Costs obtained from calculations derived by Phil. 4) http://www.lrc.rpi.edu/programs/solidstate/pdf/freezerlighting-finalreport.pdf
345 | Replace lighting with LEDs in residential refrigerators | R: Refrigerator LED lighting | 4 | Residential | Refrigeration | All residential standard size refrigerators | Energy Savings (%) | 0.9% | 0% | 0 | 0 | 0 | 0 | 7.99 | 17 | 17 | LEDLight.com, "Standard Appliance LED Light Bulb ", http://www.ledlight.com/standard-appliance-led-light.aspx
347 | Use of no or low heating elements to eliminate sweating on doors | C: Low-heat door anti-sweating | 3 | Commercial | Refrigeration | All walk-in coolers and freezers | Energy Savings (%) | 13.5% | 0% | 0 | 0 | 0 | 0 | 876 | 15 | 15 | Table 5-13,14, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
348 | Demonstrate and deploy magnetic refrigeration in homes | R: Magnetocaloric refrigeration | 1 | Residential | Refrigeration | All residential refrigerators and freezers | Energy Savings (%) | 25% | 0% | 0 | 0 | 0 | 0 | 2293.6957 | 17 | 17 | based on Torregrosa-Jaime, B., Payá, J., Corberan, J., Malvicino, C., Di Sciullo, F., ICE Project: Mobile Air-Conditioning System Based on Magnetic Refrigeration, Technical Paper 2013-01-0238, 2013, doi:10.4271/2013-01-0238 and Torregrosa-Jaime, B., Vasile, C., Risser, M., Muller, C., Corberan, J., Payá, J., Application of Magnetocaloric Heat Pumps in Mobile Air-Conditioning, Technical Paper 2013-01-0239, 2013, doi:10.4271/2013-01-0239; --> cost based on presentation during the conference is 500 euros ~ $653 for a 2.3 kW system ==> assume a typical home requires 3 TR ==> cost premium = 3*3.517/2.3*500
355 | Use non-electric devices for anti-sweat applications in walk-in coolers, etc. | C: Non-Electric door anti-sweat | 2 | Commercial | Refrigeration | Walk-In Coolers, Supermarkets | Energy Savings (%) | 6% | 0% | 0 | 0 | 0 | 0 | 1244 | 15 | 15 | Table 5-13, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
356 | Demonstrate and deploy linear oil-free compressor applicable to all residential refrigerators and freezers | R: Oil-Free Linear Compressor in Refrig and Freezers | 3 | Residential | Refrigeration | All residential refrigerators and freezers | Energy Savings (%) | 25% | 0% | 0 | 0 | 0 | 0 | 50 | 17 | 17 | 1) TSD, LG product website (11/12), http://www.acr-news.com/news/news.asp?id=2231, 2) http://www.applianceassistant.com/news/AM091610.html 3) Primary Source: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, 4) Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation 5) http://docs.lib.purdue.edu/cgi/viewcontent.cgi?article=2363&context=icec 6) http://docs.lib.purdue.edu/cgi/viewcontent.cgi?article=1786&context=icec
358 | Reduce thermal cycling of evaporator in new commercial ice machines | C: Ice Mach, Reduce Evaporator Thermal Cycling | 3 | Commercial | Refrigeration | All commercial ice machines | Energy Savings (%) | 5% | 0% | 0 | 0 | 0 | 0 | 25 | 8.5 | 8.5 | Table 5-24, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment (http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_refrig_report_10-09.pdf) Other Supporting Sources: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation
359 | Reduce ice meltage during harvest in commercial ice machines | C: Reduced Meltage During Harvest in ice machine | 3 | Commercial | Refrigeration | All commercial ice machines | Energy Savings (%) | 4% | 0% | 0 | 0 | 0 | 0 | 110 | 8.5 | 8.5 | Table 5-24, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment (http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_refrig_report_10-09.pdf) Other Supporting Sources: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation
363 | Use proximity sensors in new beverage merchandisers | C: Beverage Merchandisers Lighting Proximity Sensors | 4 | Commercial | Refrigeration | All commercial beverage merchandisers | Energy Savings (%) | 35% | 0% | 0 | 0 | 0 | 0 | 100 | 15 | 15 | Table 5-22, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
369 | Demonstrate thermoacoustic method for residential refrigerators | R: Thermoacoustic Refrigeration | 1 | Residential | Refrigeration | All residential refrigerators and freezers | Energy Savings (%) | 15% | 0% | 3748.75 | 2199 | 3748.75 | 2199 | 1549.75 | 17 | 17 | Table 6-1, Navigant Consulting Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Final Report. Department of Energy (2009)
377 | Use most cost effective insulation thickness in commercial walk-ins | C: Walk-in wall insulation | 4 | Commercial | Refrigeration | All walk-in coolers and freezers | Energy Savings (%) | 2% | 0% | 0 | 0 | 0 | 0 | 457 | 15 | 15 | Table 5-13,14, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
378 | Use vacuum insulated panels for all residential refrigeration | R: VIP in refrigerators | 3 | Residential | Refrigeration | All residential refrigerators and freezers | Energy Savings (%) | 19% | 0% | 1.449 | 0 | 1.449 | 0 | 1.449 | 17 | 17 | TSD; http://www.appliancemagazine.com/new_products.php?article=4971&zone=204&first=1 LG Korea: http://www.lg.com/global/sustainability/environment/greener-products/products-application/refrigerator.jsp
380 | Improve supermarket compressor rack in new systems by using vapor injection economizer for low temperature supermarket compressors | C: Vapor Injection Economizer for Low Temp Supermarket Compressors | 3 | Commercial | Refrigeration | All supermarket compressor racks | Energy Savings (%) | 4% | 0% | 0 | 0 | 0 | 0 | 19008 | 15 | 15 | Table 5-9, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
381 | Deploy advanced white roofs to commercial buildings in the hottest climate zones (4&5) with SR 0.75 | C: Cool Roofs, Hot CZ, 0.75 SR | 4 | Commercial | HVAC | All commercial cooling in the hottest 2 climates | Energy Savings (%) | 24.02% | 0% | 0.10333 | 0 | 0.10333 | 0 | 0.10333 | 40 | 40 | 1) Savings from pg. 2 Sleiman, Mohamad. Kirchstetter, Thomas.Gilbert, Haley. Preble, Chelsea. Accelerated aging method to mimic changes in solar reflectance of roofing materials. LBNL. July 18, 2012. 2) Cost in source is .31/sqft of roof area. Use average of 3 floors per building to get cost/ total floor space (from CBECS). Non-residential Cool Roof Cost Summary. Architectural Energy Corporation. February 8, 2012. Table 1. http://www.coolrooftoolkit.org/wp-content/uploads/2012/07/CEC-Non-Res-Cool-3) 3) Duro Last. Energy Efficient Roofing, Inc. http://www.fseer.com/DuroLastFacts.aspx 4) Data reviewed and submitted by experts from Fraunhofer Center for Sustainable Energy Systems during peer review.
382 | Use variable speed compressors in select new commercial refrigeration equipment | C: VSCs for Refrigeration | 4 | Commercial | Refrigeration | All commercial compressors (DC) | Energy Savings (%) | 20% | 0% | 0 | 0 | 0 | 0 | 86 | 15 | 15 | Tables 5-17,19,20,22,26,27, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment Primary Source: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation
383 | Use variable speed compressors in residential refrigerators | R: VSCs for Refrigeration | 4 | Residential | Refrigeration | All residential refrigerators and freezers | Energy Savings (%) | 20% | 0% | 0 | 0 | 0 | 0 | 93.96 | 17 | 17 | DOE TSD; http://www.homeenergy.org/article_preview.php?id=21&article_title=Motors_Matter
384 | Use variable speed evaporator fans (using ECM fan motors) in select new commercial refrigeration equipment | C: Refrig. Var Speed Evaporator Fan | 4 | Commercial | Refrigeration | All walk-in coolers and freezers | Energy Savings (%) | 4.5% | 0% | 0 | 0 | 0 | 0 | 138 | 11 | 11 | Table 5-13, 14, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment
387 | Launch campaign to encourage building sealing in homes | R: Reduce Infiltration (25%) | 4 | Residential | HVAC | Total heating and cooling lost through infiltration in all homes | Energy Savings (%) | 25% | 0% | 300 | 0 | 300 | 0 | 300 | 30 | 30 | NREL measure database
388 | Move to 2x4+1" sheathing in residential codes | R: Code: 2x4 + 1" sheathing | 4 | Residential | HVAC | Total heating and cooling lost through walls in new single/multi/mobile homes | R-value | 17.1 | 11.1 | 728 | 0 | 728 | 0 | 728 | 30 | 30 | http://www.toolbase.org/Technology-Inventory/walls/structural-insulated-sheathing
389 | Move to 2x4+ radiant barrier in residential codes | R: Code: 2x4 + radiant | 4 | Residential | HVAC | Total residential heating and cooling lost through walls in all homes | R-value | 18.1 | 11.1 | 494 | 0 | 494 | 0 | 494 | 30 | 30 | http://www.toolbase.org/Technology-Inventory/walls/structural-insulated-sheathing
390 | Move to 2x6 (advanced framing, 24" OC + R-19) construction in residential codes | R: R-19 Code: 2x6, 24" On Center Framing | 4 | Residential | HVAC | Total heating and cooling lost through walls in new single/multi/mobile homes | R-value | 19.6 | 11.1 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | NREL technology fact sheet 26449.pdf Primary Source: NAHB Research Center; Southface Energy Institute; Oark Ridge National Laboratory; National Renewable Energy Laboratory; "Technology Fact Sheet: Advanced Framing" (2000
396 | Insulate crawl spaces to R-17 in all homes | R: R-17 Crawl Spaces | 3 | Residential | HVAC | Total heating and cooling energy lost through crawl space foundation in all homes | R-value | 17 | 4 | 228 | 0 | 228 | 0 | 228 | 30 | 30 | http://www.radiantguard.com/how-to-install-radiant-barrier.aspx Primary Source: Savings: First principles (market and baseline drawn from RECs analysis) Cost: NREL measure database
397 | Continue better buildings program targeting 25% whole-home consumption | R: Better buildings (25%)* | 0 | Residential | All End Uses | Total residential energy consumption by existing (pre-2010) single-family homes | Energy Savings (%) | 25% | 0% | 0 | 0 | 0 | 0 | 10000 | 30 | 30 | EERE website
398 | Launch campaign to encourage "drill-and-fill" insulation in existing single family homes (FOA TARGET) | R: "Drill & Fill" pre-70's* | 0 | Residential | HVAC | Total heating and cooling energy lost through walls in all single family homes built before 1970 | R-value | 15 | 6 | 3120 | 0 | 3120 | 0 | 3120 | 30 | 30 | Savings: first principles. Cost: NREL retrofit measure database
399 | Research, demonstrate, and deploy dynamic windows in new commercial buildings | C: Dynamic Windows (N) (MYP2025)* | 0 | Commercial | HVAC | Total commercial solar heat gain cooling + total commercial conductive window loss in new commercial buildings | Energy Savings (%) | 38.34% | 0% | 6.48 | 3.6 | 6.48 | 3.6 | 2.88 | 40 | 40 | Lee, E.S., Yazdanian, M. & Selkowitz, S.E. The Energy-Savings Potential of Electrochromic Windows in the US Commercial Buildings Sector. Building 1-42 (2004). Cost: Personal communication - manufacturers and experts Other Supporting Sources: Arasteh, D.; Selkowitz, S.; Apte, J.; "Zero Energy Windows"; 2006 ACEEE Summer Study on Energy Efficiency in Buildings
400 | Research, demonstrate, and deploy dynamic windows in new homes | R: Dynamic Windows (N)(MYP2025)* | 0 | Residential | HVAC | Total heating and cooling energy lost through windows in all new homes due to conduction and radiation | Energy Savings (%) | 51.37% | 0% | 3996 | 1920 | 3996 | 1920 | 2076 | 30 | 30 | Program Primary Source: Arasteh, D.; Selkowitz, S.; Apte, J.; "Zero Energy Windows"; 2006 ACEEE Summer Study on Energy Efficiency in Buildings Other Supporting Sources: Lee, E.S., Yazdanian, M. & Selkowitz, S.E. The Energy-Savings Potential of Electrochromic Windows in the US Commercial Buildings Sector. Building 1-42 (2004). Cost: Personal communication - manufacturers and experts
401 | Research, demonstrate, and deploy dynamic windows in existing homes | R: Dynamic Windows (E)(MYP2025)* | 0 | Residential | HVAC | Total heating and cooling energy lost through windows in homes built pre-2010 due to conduction and radiation (use for dynamic windows that would not cause reduction in heat gain during winter) | Energy Savings (%) | 51.37% | 0% | 3996 | 1920 | 3996 | 1920 | 2076 | 30 | 30 | Program Primary Source: Arasteh, D.; Selkowitz, S.; Apte, J.; "Zero Energy Windows"; 2006 ACEEE Summer Study on Energy Efficiency in Buildings Other Supporting Sources: Lee, E.S., Yazdanian, M. & Selkowitz, S.E. The Energy-Savings Potential of Electrochromic Windows in the US Commercial Buildings Sector. Building 1-42 (2004). Cost: Personal communication - manufacturers and experts
402 | Research, demonstrate, and deploy dynamic windows in existing commercial buildings | C: Dynamic Windows (E)(MYP2025)* | 0 | Commercial | HVAC | Total commercial solar heat gain cooling + total commercial conductive window loss in existing building (use for dynamic windows where heat gain during winter is not affected) | Energy Savings (%) | 38.34% | 0% | 6.48 | 3.6 | 6.48 | 3.6 | 2.88 | 40 | 40 | Program Primary Source: Lee, E.S., Yazdanian, M. & Selkowitz, S.E. The Energy-Savings Potential of Electrochromic Windows in the US Commercial Buildings Sector. Building 1-42 (2004). Cost: Personal communication - manufacturers and experts Other Supporting Sources: Arasteh, D.; Selkowitz, S.; Apte, J.; "Zero Energy Windows"; 2006 ACEEE Summer Study on Energy Efficiency in Buildings
405 | Develop integrated roofing package for new homes in non-hot climates using phase change materials (PCM) for R-75 equivalent | R: R-75 PCM Roof, non-hot CZ (N) | 2 | Residential | HVAC | Total heating and cooling energy lost through attics in all new homes in all non-hot climates | R-value | 75 | 38 | 1801.3328 | 0 | 1801.3328 | 0 | 1801.3328 | 40 | 40 | Miller, W. & Kosny, J. Next-Generation Roofs and Attics for Homes. ACEEE Summer Study on Energy Efficiency in Buildings 180-195 (2008)
406 | Implement R-11 basement insulation in all homes | R: Basement, +R-11 | 3 | Residential | HVAC | Total heating and cooling energy lost through basements in all homes | R-value | 15 | 4 | 1196 | 0 | 1196 | 0 | 1196 | 30 | 30 | Savings: First principles (market and baseline drawn from RECs analysis). Cost: NREL measure database
410 | Implement R-60 attic insulation in poorly insulated home attics | R: Poorly Ins. Attics, +R-60 [E] | 4 | Residential | HVAC | Total heating and cooling energy loss through attics in all homes with poorly insulated attics | R-value | 64 | 4 | 5460 | 0 | 5460 | 0 | 5460 | 30 | 30 | Primary Source: Savings: first principles increasing R-value. Cost: NREL measure database
411 | Implement R-60 attic insulation in well insulated home attics | R: Well Ins. Attics, +R-41 [E] | 4 | Residential | HVAC | Total heating and cooling energy loss through attics in all homes with moderately insulated attics | R-value | 64 | 23 | 3900 | 0 | 3900 | 0 | 3900 | 30 | 30 | Savings: first principles increasing R-value. Cost: NREL measure database
414 | Launch campaign to encourage cool coating choices for homes in hot climates | R: Cool Paint Color | 3 | Residential | HVAC | Total cooling in all homes in hot climates | Energy Savings (%) | 4% | 0% | 280 | 0 | 280 | 0 | 280 | 15 | 15 | HES pro runs, ORNL CoolWall report Primary Source: Tom Petrie, Jerry Atchley, Phil Childs, and André Desjarlais; "Energy Savings for Stucco Walls Coated with Cool Colors" ORNL (12/2007) Other Supporting Sources: Additional support by running HES Pro in multipl climate zones to verify savings
415 | Launch campaign to encourage cool coating choices for comm. Buildings in hot climates | C: Cool Paint Color | 3 | Commercial | HVAC | All commercial cooling in the hottest 2 climates | Energy Savings (%) | 6% | 0% | 0 | 0 | 0 | 0 | 0.34444 | 15 | 15 | 1) Tom Petrie, Jerry Atchley, Phil Childs, and André Desjarlais; "Energy Savings for Stucco Walls Coated with Cool Colors" ORNL (12/2007) 2) Additional support by running HES Pro in multiple climate zones to verify savings. 3) Incremental cost of cool coating has not been developed yet, but it is assumed to be the same as the cost for cool roofs coating. Data reviewed and submitted by experts from Fraunhofer Center for Sustainable Energy Systems during peer review.
419 | Move to standardize advanced wall construction techniques in new homes | R: Adv. Framing in Codes (N) | 4 | Residential | HVAC | Total heating and cooling lost through walls in new single/multi/mobile homes | R-value | 14.6 | 11.1 | 0 | 0 | 0 | 0 | -750 | 30 | 30 | http://www.energysavers.gov/your_home/designing_remodeling/index.cfm/mytopic=10090 Primary Source: National Assocation of Home Builders, Southface Energy Institiute & Oak Ridge National Laboratory ADVANCED WALL FRAMING. U.S. Department of Energy (2000). Other Supporting Sources: Straube, J. & Smegal, J. Building America Special Research Project: High-R Walls Case Study Analysis. Building Science 68 (Somerville, MA, 2009).
421 | Research and demonstrate R-10 windows in homes | R: R-10 Windows | 2 | Residential | HVAC | Total heating and cooling lost through windows due to conduction in all homes | R-value | 10 | 1.61 | 3330 | 0 | 3330 | 0 | 3330 | 30 | 30 | Southwall, Alpeninc, PNNL Lost Opportunities Primary Source: 6. Apte, J. & Arasteh, D. Window-Related Energy Consumption in the US Residential and Commercial Building Stock. Buildings 1-38 (Berkeley, CA, 2006). Personal communication: various window experts Other Supporting Sources: Arasteh, Dariush; Selkowitz, Steve; Apte, Josh; LaFrance, Marc. Energy Impacts of Today’ s Window Stock
422 | Research and demonstrate R-10 windows in commercial buildings | C: R-10 Windows | 2 | Commercial | HVAC | Total window conductive loss in all commercial buildings | R-value | 10 | 1.86 | 10.6632 | 0 | 10.6632 | 0 | 10.6632 | 40 | 40 | Southwall, Alpeninc, PNNL Lost Opportunities Primary Source: 6. Apte, J. & Arasteh, D. Window-Related Energy Consumption in the US Residential and Commercial Building Stock. Buildings 1-38 (Berkeley, CA, 2006). Personal communication: various window experts Other Supporting Sources: Arasteh, Dariush; Selkowitz, Steve; Apte, Josh; LaFrance, Marc. Energy Impacts of Today’ s Window Stock
423 | Deploy and move to standardize residential door R-values | R: R-7 Doors | 4 | Residential | HVAC | Total heating and cooling lost through doors in all homes | R-value | 7.1429 | 1.8182 | 90 | 0 | 90 | 0 | 90 | 30 | 30 | Lowe's, NREL database Primary Source: Savings: First principles (market and baseline drawn from RECs analysis) Cost: NREL measure database
425 | Launch campaign to encourage addition of sheathing and insulation when replacing siding in existing homes | R: Sheathing & Insulation [E] | 4 | Residential | HVAC | Total heating and cooling lost through walls in homes built before 2010 | R-value | 20 | 6 | 17420 | 10250 | 17420 | 10250 | 7170 | 30 | 30 | NREL measure database
426 | Increase deployment of home wrap on new homes | R: Building Wrap (N) | 5 | Residential | HVAC | Total heating and cooling lost through infiltration in all new homes | Energy Savings (%) | 13% | 0% | 1040.5644 | 0 | 1040.5644 | 0 | 1040.5644 | 30 | 30 | Program Primary Source: Architectural Energy Company, "Impact of Title 24 Residential Air Leakage Reduction Credit on Water-Resistive Barriers in California Homes", 2006
427 | Increase deployment of building wrap on new commercial buildings | C: Building Wrap (N) | 5 | Commercial | HVAC | Total heating and cooling lost through infiltration in new commercial buildings | ACH | 0.015 | 0.038 | 1.26 | 0 | 1.26 | 0 | 1.26 | 40 | 40 | NREL 46100 building research Primary Source: Elaine Hale, Matthew Leach, Adam Hirsch, and Paul Torcellini, "General Merchandise 50% Energy Savings Technical Support Document"; NREL/TP-550-46100 September 2009
431 | Move to standardize vestibules on commercial buildings | C: Vestibules | 4 | Commercial | Building | No vestibule infiltration | ACH | 0.158 | 0.253 | 0.7804 | 0 | 0.7804 | 0 | 0.7804 | 40 | 40 | 1) pg. 47. Elaine Hale, Matthew Leach, Adam Hirsch, and Paul Torcellini, "General Merchandise 50% Energy Savings Technical Support Document"; NREL/TP-550-46100 September 2009. 2) http://www.hortondoors.com/content.aspx?cid=1232
432 | Demonstrate and deploy whole-building designs for new homes | R: New home (40%)* | 0 | Residential | All End Uses | Total residential energy consumption in all new homes | Energy Savings (%) | 40% | 0% | 150000 | 0 | 150000 | 0 | 3615 | 30 | 30 | BeOPT/ OPT Eplus
433 | Demonstrate and deploy 40% whole-building designs for new commercial buildings | C: New building (40%)* | 0 | Commercial | HVAC/Lighting | All energy consumption in new buildings | Energy Savings (%) | 40% | 0% | 9.5 | 0 | 9.5 | 0 | 9.5 | 40 | 40 | Extrapolated based on 50% TSD Opt-E-Plus runs
434 | Adjusts washer operation and washing conditions based on soil load, etc., in coin-op class commercial washers | C: CW Soil Sensors | 3 | Commercial | Washing & Drying | Total water heating energy use by single load coin operated washers | Energy Savings (%) | 10% | 0% | 0 | 0 | 0 | 0 | 100 | 7.1 | 7.1 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf
435 | Adjusts washer operation and washing conditions based on soil load, etc., in residential washers | R: CW Soil Sensors | 3 | Residential | Washing & Drying | Total water heating energy use by residential clothes washers | Energy Savings (%) | 10% | 0% | 0 | 0 | 0 | 0 | 100 | 11 | 11 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf
436 | Deploy improved agitator design to reduce hot water usage in coin-op commercial washers | C: Advanced Agitation CW | 3 | Commercial | Washing & Drying | Total water heating energy use by top loading coin operated washers | Energy Savings (%) | 15% | 0% | 0 | 0 | 0 | 0 | 0 | 7.1 | 7.1 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf
437 | Implement ozone laundry systems as a retrofit that dissolve ozone in cold water to reduce hot water usage in any multi-load/washer-extractor clothes washers. | C: Multi-load CW Ozone Laundry Systems | 4 | Commercial | Washing & Drying | Total water heating energy use by multi-load washers | Energy Savings (%) | 89% | 0% | 35500 | 0 | 35500 | 0 | 35500 | 15 | 15 | 1) Tables 8-24 and 8-25, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf 2) Savings confirmed in Pg. 10 of Cold Facts EcoTex. Clear Water Tech 2013. 3) Typical cost of an ozone system is an average between the smallest and the largest capacity systems, and includes shipping and installation from pg.21 of Riesenberger, James. PBMP - Commercial Laundry Facilities. Koeller and Company. This is a system that is installed as an addition/retrofit to any washer-extractor/multi-load washer system.
438 | Increase deployment of improved design tunnel washers for even less hot water use | C: Advanced Tunnel Washers | 3 | Commercial | Washing & Drying | Total energy use by commercial tunnel washers (assuming all WH energy use) | Energy Savings (%) | 60% | 0% | 0 | 0 | 0 | 0 | 1200000 | 11 | 11 | Tables 8-26 and 8-27, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf
440 | Deploy sensors and controls to detect size of load and adjust water level appropriately in commercial clothes washers | C: CW - Auto Fill Control | 3 | Commercial | Washing & Drying | Total water heating energy use by top loading coin operated washers | Energy Savings (%) | 15% | 0% | 0 | 0 | 0 | 0 | 20 | 7.1 | 7.1 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Control is available in residential units; approximate cost based on replacement of water level control sensor for *residential* unit
441 | Deploy automatic sprayer shutoff sensors that detect the presence of dish racks in conveyor-type commercial dishwashers | C: DW Auto Sprayer Shutoff | 3 | Commercial | Washing & Drying | Total water heating energy use by conveyor type dishwashers | Energy Savings (%) | 50% | 0% | 24000 | 20000 | 24000 | 20000 | 4000 | 20 | 20 | Tables 4-11,4-21, and 4-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances Primary Source: Hobart Cle Warewasher Opti-Rinse, http://www.hobartcorp.com/products/warewashing/conveyor-type/cle-warewasher/
442 | Replace conventional dry cleaning with liquid CO2 in new systems | C: Carbon Dioxide Dry Cleaning | 3 | Commercial | Washing & Drying | Total dry cleaning energy use | Energy Usage, BTU/100lbs | 13700000 | 22300000 | 0 | 0 | 0 | 0 | 97500 | 15 | 15 | Figure 8-33, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances
444 | Deploy economical heat exchanger in existing commercial standard capacity dryers | C: CD Exhaust Heat Recovery | 3 | Commercial | Washing & Drying | Total energy use by single load coin operated dryers | Energy Savings (%) | 45% | 0% |  | 0 |  | 0 | 200 | 11 | 11 | Tables 8-32, 8-36, Navigant Consulting; "Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances" (2009)
448 | Replace residential gas clothes dryers with modulating gas clothes dryers | R: Modulating Gas Dryer | 2 | Residential | Washing & Drying | Total energy use by all natural gas clothes dryers | Energy Savings (%) | 15% | 0% | 23.9231 | 0 | 23.9231 | 0 | 23.9231 | 12 | 12 | Tables 8-32, 8-35, 8-36, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost assumes 5-year payback of savings of $6.09 per year
450 | Increase adoption of residential heat pump clothes dryers | R: HP Clothes Dryer | 2 | Residential | Washing & Drying | Total energy use by all electric clothes dryers | Energy Savings (%) | 50% | 0% | 879 | 455 | 879 | 455 | 424 | 12 | 12 | Market Cost: AHAM-2 Direct Final Rule (2011) TSD, Chapter 8, Table 8.2.9 Lifetime: AHAM-2 Direct Final Rule (2011) TSD, Chapter 8, Table 8.2.39 (http://www.regulations.gov/#!documentDetail;D=EERE-2007-BT-STD-0010-0053). Market Consumption and Stock: AHAM-2 Direct Final Rule (2011) TSD, Residential Clothes Dryer National Impact Analysis Spreadsheet (http://www.regulations.gov/#!documentDetail;D=EERE-2007-BT-STD-0010-0054). Market consumption is calculated as the product of market stock and per unit annual energy consumption in 2030.
451 | Increase deployment of commercial low-temp door type dishwashers: to include reduced water heating needs; low-flow sprayers, redesigned tanks, wall insulation | C: Low-temp door DW | 5 | Commercial | Washing & Drying | Total energy use by low temperature dishwashers (with doors) | Energy Savings (%) | 36% | 0% | 0 | 0 | 0 | 0 | 2000 | 15 | 15 | Tables 4-22 (pg.104) and 4-8, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf
452 | Increase deployment of commercial high-temp door type dishwashers: to include reduced water heating needs; low-flow sprayers, redesigned tanks, wall insulation | C: High-temp door DW | 5 | Commercial | Washing & Drying | Total energy use by high temperature dishwashers (with doors) | Energy Savings (%) | 33% | 0% | 0 | 0 | 0 | 0 | 2100 | 15 | 15 | Tables 4-22 (pg.104) and 4-8, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf
453 | Increase deployment of commercial low-temp conveyer type dishwashers: to include reduced water heating needs; low-flow sprayers, redesigned tanks, wall insulation, auto sprayer shutoff, waste heat recovery | C: Low-temp conveyor DW | 5 | Commercial | Washing & Drying | Total energy use by conveyor low temperature dishwashers | Energy Savings (%) | 30% | 0% | 0 | 0 | 0 | 0 | 3500 | 20 | 20 | Tables 4-22 (pg.104) and 4-8, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf
454 | Increase deployment of commercial high-temp conveyer type dishwashers: to include reduced water heating needs; low-flow sprayers, redesigned tanks, wall insulation, auto sprayer shutoff, waste heat recovery | C: High-temp conveyor DW | 5 | Commercial | Washing & Drying | Total energy use by conveyor high temperature dishwashers | Energy Savings (%) | 30% | 0% | 0 | 0 | 0 | 0 | 3500 | 20 | 20 | Tables 4-22 (pg.104) and 4-8, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf
455 | Highest efficiency standard-sized residential dishwashers defined as level 5 in 05/2012 rulemaking TSD | R: Max tech DW (L5 of 5) | 3 | Residential | Dishwashing | All residential dishwashing and its water heating energy use | Energy Usage, kWh/yr | 180 | 355 | 2099 | 400 | 2099 | 400 | 1699 | 19 | 19 | Standards rulemaking TSD published in 05/2012
456 | Deploy temperature and humidity sensors to reduce cycle time in commercial clothes dryers | C: CD: Impr. Cycle Termination | 3 | Commercial | Washing & Drying | Total energy use by single load coin operated dryers | Energy Savings (%) | 15% | 0% |  | 0 |  | 0 | 21 | 11 | 11 | Tables 8-32, 8-36, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost estimated from part currently in use in residential units.
457 | Deploy automatic temperature and humidity termination sensors to reduce cycle time in residential clothes dryers | R: Clothes Dryer: Impr. Cycle Termination | 5 | Residential | Washing & Drying | Total energy use by all electric and natural gas clothes dryers | Energy Savings (%) | 12% | 0% | 521 | 500 | 521 | 500 | 21 | 12 | 12 | 1) Cost: According to James Battaglia (NCI), no known credible estimates for the cost of improved automatic termination. Cost is approximated by Phil Pharese as the price of replacement temperature sensors. 2) Energy Savings: ENERGY STAR Market & Industry Scoping Report – Residential Clothes Dryers. November 2011 (http://www.energystar.gov/ia/products/downloads/ENERGY_STAR_Scoping_Report_Residential_Clothes_Dryers.pdf). Lifetime: AHAM-2 Direct Final Rule (2011) TSD, Chapter 8, Table 8.2.39 (http://www.regulations.gov/#!documentDetail;D=EERE-2007-BT-STD-0010-0053). 3) Market Consumption and Stock: AHAM-2 Direct Final Rule (2011) TSD, Residential Clothes Dryer National Impact Analysis Spreadsheet (http://www.regulations.gov/#!documentDetail;D=EERE-2007-BT-STD-0010-0054). Market consumption is calculated as the product of market stock and per unit annual energy consumption in 2030. 4) Tables 8-32, 8-36, page 272, see "improved cycle termination" Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf
459 | Demonstrate and deploy improved drum design for single-load commercial clothes washers | C: CW Improved Drum Design | 3 | Commercial | Washing & Drying | Total energy use by single load coin operated dryers | Energy Savings (%) | 20% | 0% | 640.666 | 0 | 640.666 | 0 | 640.666 | 7.1 | 7.1 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost assumes 3-year payback from annual savings of $246
460 | Deploy sprayers with smaller size holes to improve efficiency of residential dishwashers | R: DW: Impr. Hydraulic Efficiency | 4 | Residential | Dishwashing | Total dishwashing energy use, not including water heating consumption | Energy Savings (%) | 25% | 0% | 0 | 0 | 0 | 0 | 0 | 19 | 19 | Dries, John, (2008), "Improving Dishwasher Efficiency", http://www.appliancemagazine.com/editorial.php?article=1978
461 | Improved water extraction in commercial clothes washers to reduce drying time | C: CW: Improved Water Extraction | 4 | Commercial | Washing & Drying | Total energy use by single load coin operated dryers | Energy Savings (%) | 25% | 0% | 800.8325 | 0 | 800.8325 | 0 | 800.8325 | 7.1 | 7.1 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost assumes 3-year payback based on annual savings of $308.06
462 | Improved water extraction in residential clothes washers to reduce drying time | R: CW: Improved Water Extraction | 4 | Residential | Washing & Drying | Total energy use by all electric and natural gas clothes dryers | Energy Savings (%) | 25% | 0% | 58.4191 | 0 | 58.4191 | 0 | 58.4191 | 11 | 11 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost assumes 3-year payback based on annual savings of $25.69
463 | Increase motor efficiency in single-load commercial clothes washers | C: Single-load CW motor | 3 | Commercial | Washing & Drying | Total machine energy use by single load coin operated washers | Energy Savings (%) | 10% | 0% | 0 | 0 | 0 | 0 | 0 | 7.1 | 7.1 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf
466 | Add condensing heat exchanger from exhaust air to intake air in commercial single-load dryers | C: CD Condensing single load | 2 | Commercial | Washing & Drying | Total energy use by single load coin operated dryers | Energy Savings (%) | 14% | 0% | 747.4437 | 0 | 747.4437 | 0 | 747.4437 | 11 | 11 | Tables 8-32, 8-36, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost assumes 5-year payback based on annual savings of $172.51
467 | Add condensing heat exchanger from exhaust air to intake air in standard residential dryers - NOT FEASIBLE TECHNOLOGY | R: Condensing clothes dryer | 2 | Residential | Washing & Drying | Total energy use by all natural gas clothes dryers | Energy Savings (%) | 14% | 0% | 55.367 | 0 | 55.367 | 0 | 55.367 | 12 | 12 | Tables 8-32, 8-36, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost assumes 5-year payback based on annual savings of $14.29
468 | Add condensing heat exchanger from exhaust air to intake air in commercial tumble dryers | C: CD Condensing tumble | 2 | Commercial | Washing & Drying | Total energy use by commercial tumble dryers | Energy Savings (%) | 14% | 0% | 228.6308 | 0 | 228.6308 | 0 | 228.6308 | 11 | 11 | Table 8-37, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost assumes 5-year payback based on annual savings of $41.73
469 | Increase usage of low-temperature detergent in single-load commercial clothes washers | C: Single-load CW: Low-T Detergent | 3 | Commercial | Washing & Drying | Total water heating energy use by single load coin operated washers | Energy Savings (%) | 20% | 0% | 504.5423 | 409.9406 | 504.5423 | 409.9406 | 94.6017 | 1 | 1 | Chemical and Engineering News, Vol. 85 #5, Jan. 2007; Other Primary Source: Tables 8-24 and 8-25, Navigant Consulting; "Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances" (2009) Other Supporting Sources: Chemical and Engineering News, Vol. 85 #5, Jan. 2007
470 | Increase usage of low-temperature detergent in on-site multi-load commercial clothes washers and tunnel washers | C: Multi-load CW: Low-T Detergent | 4 | Commercial | Washing & Drying | Total water heating energy use by tunnel and multi-load washers | Energy Savings (%) | 20% | 0% | 5316.568 | 4319.7115 | 5316.568 | 4319.7115 | 996.8565 | 1 | 1 | Chemical and Engineering News, Vol. 85 #5, Jan. 2007; Other Primary Source: Tables 8-24 and 8-25, Navigant Consulting; "Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances" (2009) Other Supporting Sources: Chemical and Engineering News, Vol. 85 #5, Jan. 2007
471 | Increase usage of low-temperature detergent in homes; clothes washing | R: Low Temp Detergent in clothes washers | 3 | Residential | Washing & Drying | Total water heating energy use by residential clothes washers | Energy Savings (%) | 20% | 0% | 57.5962 | 46.7969 | 57.5962 | 46.7969 | 10.7993 | 1 | 1 | Chemical and Engineering News, Vol. 85 #5, Jan. 2007; Other Primary Source: Tables 8-24 and 8-25, Navigant Consulting; "Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances" (2009) Other Supporting Sources: Chemical and Engineering News, Vol. 85 #5, Jan. 2007
472 | Increase adoption of low-flow sprayers in low-temp under counter dishwashers | C: Low-Flow Sprayers in low temp DW | 4 | Commercial | Dishwashing | Total water heating energy use by undercounter low temperature dishwashers | Energy Savings (%) | 11% | 0% | 0 | 0 | 0 | 0 | 1000 | 10 | 10 | Tables 4-22 and 4-8, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances
473 | Increase adoption of low-flow sprayers in high-temp under counter dishwashers | C: Low-Flow Sprayers in high temp DW | 4 | Commercial | Dishwashing | Total water heating energy use by undercounter high temperature dishwashers | Energy Savings (%) | 40% | 0% | 0 | 0 | 0 | 0 | 1000 | 10 | 10 | Tables 4-22 and 4-8, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances
475 | Demonstrate and deploy residential microwave clothes dryers | R: Microwave CD | 2 | Residential | Washing & Drying | Total energy use by all electric clothes dryers | Energy Savings (%) | 21% | 0% | 0 | 0 | 0 | 0 | 212 | 12 | 12 | Table 8-36, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. (p. 270) http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf
477 | Replace conventional dry cleaning with petroleum in new systems | C: Petroleum Dry Cleaning | 3 | Commercial | Washing & Drying | Total dry cleaning energy use | Energy Usage, BTU/100lbs | 9440000 | 22300000 | 0 | 0 | 0 | 0 | 52500 | 15 | 15 | Figure 8-33, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: EPA, "Case Study: Liquid Carbon Dioxide (CO2) Surfactant System For Garment Care", http://www.epa.gov/dfe/pubs/garment/lcds/micell.htm
478 | Demonstrate and Deploy Nylon Bead Clothes Washers in Homes | R: Nylon Bead Clothes Washer | 2 | Residential | Washing & Drying | Total residential clothes washing, drying, and water heating energy consumption | Energy Savings (%) | 83% | 0% | 532.016 | 0 | 532.016 | 0 | 532.016 | 11 | 11 | LBNL: Priority Setting Estimates spreadsheet: 83% UEC source energy savings, 61% primary energy savings (use 83%... Makes sense b/c commercial front loader is only 7% washer energy, rest is HW and drying) Primary Source: Desroches, L et al. (2011). MaxTech and Beyond, Maximizing Appliance and Equipment Efficiency by Design, http://efficiency.lbl.gov/drupal.files/ees/MTAB%20Final%20LBNL%20Report.pdf
479 | Replace conventional dry cleaning with professional wet cleaning in new systems | C: Professional Wet Cleaning instead of dry | 3 | Commercial | Washing & Drying | Total dry cleaning energy use | Energy Usage, BTU/100lbs | 16000000 | 22300000 | 0 | 0 | 0 | 0 | 1565 | 15 | 15 | Figure 8-33, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances
480 | Standard Sized Front-Loading Clothes Washer (L7 of 8) of the 05/2012 Rulemaking TSD | R: Front Load Standard-Sized CW (L7 of 8) | 4 | Residential | Washing & Drying | Total electricity usage, excluding hot water usage, by all residential front-loading washers | Modified Energy Factor (incl. RMC) | 2.26 | 1.26 | 0 | 0 | 0 | 0 | 0 | 11 | 11 | Standards rulemaking TSD published in 05/2012, Chapter 7, Table 7.2.1.
481 | Standard-Sized Top-Loading Clothes Washer | R: Top Load Standard-sized CW (L8 of 8) | 4 | Residential | Washing & Drying | Total electric energy use [excludes hot water] by all residential top-loading washers | Modified Energy Factor (incl. RMC) | 2.04 | 1.29 | 0 | 0 | 0 | 0 | 0 | 11 | 11 | Standards rulemaking TSD published in 05/2012
482 | Deploy and Increase deployment of more efficient compact size front-loading clothes washers. The new efficiency level of 1.7 was proposed in Energy Efficiency and Smart Appliance Agreement of 2010. From the 05/2012 Rulemaking (TSD), all clothes washers manufacturered on or after March 2015 should have modified EF of 1.13 (L1 of 1). No other higher level EF was identified. | R: Efficient Compact Size Front-Loading CW | 5 | Residential | Washing & Drying | Total electricity usage, excluding hot water usage, by all residential front-loading, compact washers | Modified Energy Factor (incl. RMC) | 1.7 | 1.13 | 0 | 0 | 0 | 0 | 0 | 11 | 11 | Energy Efficiency and Smart Appliance Agreement of 2010, AHAM power point
483 | Compact Size Top-Loading Clothes Washer standard effective in 2012, must be in compliance in 2018. | R: Compact Size Top-Loading CW Standard (2018) | 5 | Residential | Washing & Drying | Total electric energy use [excludes hot water] by all residential top-loading, compact washers | Modified Energy Factor (incl. RMC) | 1.15 | 0.65 | 0 | 0 | 0 | 0 | 0 | 11 | 11 | Standards rulemaking TSD published in 05/2012
484 | Standard-sized Vented Electric Clothes Dryers standard has a compliance date of 01/2015, effective in 08/2011. | R: Vented Electric CD Standard (2015) | 5 | Residential | Washing & Drying | Total energy use by all electric clothes dryers | Energy Factor | 3.73 | 3.01 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | Standards rulemaking, effective in 08/2011 with compliance in 01/2015. http://www1.eere.energy.gov/buildings/appliance_standards/product.aspx/productid/36
485 | Compact Vented Electric 120V Clothes Dryer Standard effective in 08/2011 with compliance date of 01/2015. | R: Compact Vented Electric 120V CD Standard (2015) | 5 | Residential | Washing & Drying | Total energy consumption by vented electric compact (120V) clothes dryers | Energy Factor | 3.61 | 3.13 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | Standards rulemaking, effective in 08/2011 with compliance in 01/2015. http://www1.eere.energy.gov/buildings/appliance_standards/product.aspx/productid/36
486 | Compact Vented Electric 240V Clothes Dryer Standard effective in 08/2011 with compliance date of 01/2015. | R: Compact Vented Electric 240V CD Standard (2015) | 5 | Residential | Washing & Drying | Total energy consumption by vented electric compact (240V) clothes dryers | Energy Factor | 3.27 | 2.9 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | Standards rulemaking, effective in 08/2011 with compliance in 01/2015. http://www1.eere.energy.gov/buildings/appliance_standards/product.aspx/productid/36
487 | Standard-sized Vented Gas Clothes Dryer effective in 08/2011 with compliance date of 01/2015. | R: Vented Gas Dryer Standard (2015) | 5 | Residential | Washing & Drying | Total energy use by all natural gas clothes dryers | Energy Factor | 3.3 | 2.67 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | Standards rulemaking, effective in 08/2011 with compliance in 01/2015. http://www1.eere.energy.gov/buildings/appliance_standards/product.aspx/productid/36
488 | Compact Ventless Electric 240V Clothes Dryer Max Tech (TSD 2011) | R: Max Tech Compact Ventless Electric 240V CD | 5 | Residential | Washing & Drying | Total energy consumption by ventless electric (240V) clothes dryers | Energy Factor | 4.03 | 2.55 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | TSD 2011
489 | Ventless Electric Combination Washer-Dryer Max Tech (TSD 2011) | R: Max Tech Ventless Electric Combination W/D | 5 | Residential | Washing & Drying | Total energy consumption by ventless combination washer/dryer | Energy Factor | 3.69 | 2.08 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | TSD 2011
493 | Increase deployment of soil sensors in new residential dishwashers | R: DW Soil Sensors | 3 | Residential | Dishwashing | Total dishwashing energy use, not including water heating consumption | Energy Savings (%) | 25% | 0% | 0 | 0 | 0 | 0 | 30 | 19 | 19 | ACEEE, "Dishwashing", http://www.aceee.org/consumer/dishwashing
495 | Deploy commercial top-loading clothes washers with spray rinse technology (instead of filling tank for rinse cycle) | C: Top-loading CW Spray Rinse | 2 | Commercial | Washing & Drying | Total water heating energy use by single load coin operated washers | Energy Savings (%) | 50% | 0% | 201.716 | 0 | 201.716 | 0 | 201.716 | 7.1 | 7.1 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost assumes 5-year payback based on annual savings of $34.81
496 | Demonstrate and Deploy Nylon Bead Clothes Washers in Off-Site Commercial Laundries | C: Nylon Bead CW | 3 | Commercial | Washing & Drying | Total energy use by all commercial washers and dryers, except tunnel and multi-family washers and dryers | Energy Savings (%) | 94.13% | 0% | 34000 | 40000 | 34000 | 40000 | -6000 | 15 | 15 | LBNL: Priority Setting Estimates spreadsheet; Misra et.al. presentation showing cost analysis; Xeros website Primary Source: Misra, A., Pimphalkhute, H., Murthi, S. & Kamdar, T. Pricing strategy: Waterless Washing Machine (2010) Xeros website, Desroches, L.-B. et al. Max Tech and Beyond (2011)
497 | Offer incentives or awareness campaign to move multi-load washing to offsite tunnel washers | C: Multi-Load to Tunnel Washers | 4 | Commercial | Washing & Drying | Total water heating energy use by multi-load washers | Energy Savings (%) | 82% | 0% | 68750 | 190000 | 68750 | 190000 | -121250 | 15 | 15 | Tables 8-24 and 8-25, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances; NY times article on Hilton case study/business model Primary Source: Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. Navigant Consulting (2011) Garbarine, R. Commercial Property / New Jersey ; In Piscataway , a Central Laundry for Region Hiltons. New York Times 5 (1999)
499 | Retrofit multi-load and tunnel washers to reuse wash water and reduce need for hot water | C: Multi-/Tunnel CW: Waste-H2O Recycling | 4 | Commercial | Washing & Drying | Total water heating energy use by tunnel and multi-load washers | Energy Savings (%) | 53% | 0% | 22758.75 | 0 | 22758.75 | 0 | 22758.75 | 15 | 15 | Tables 8-24 and 8-25, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances; Lake Arrowhead resort Case Study Primary Source: Savings: Navigant Consulting; "Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances" (2009) Cost: RMC Water nd Environment; Integrated Water Resources Program Report, Appendix H (12/2007)
502 | Decrease cost and deploy thermosiphon (indirect, passive) solar water heaters (electric to electric back-up) | R: Solar WH, Elec. - Ind. Passive | 2 | Residential | Water Heating | Total electric water heating energy consumption | Energy Savings (%) | 44.94% | 0% | 0 | 0 | 0 | 0 | 2030 | 13 | 13 | SWH roadmap; Cold Climate Solar Domestic Water Heating Systems: Cost/Benefit Analysis and Opportunities for Improvements (Burch et. Al.) Primary Source: Itron, Inc.; "California Center for Sustainable Energy Solar Water Heating Pilot Program" (3/2011) Federal Energy Management Program, "Solar Water Heating with Low-Cost Plastic Systems" (1/2012) Other Supporting Sources: Hudon, Burch "Solar Water Heating Roadmap" (in preperation)
505 | Increase deployment of low flow fixtures in existing and new homes | R: Low-flow Faucets | 4 | Residential | Water Heating | Total residential energy use in high flow water heating for showers and faucets | Energy Savings (%) | 52% | 0% | 0 | 0 | 0 | 0 | -409.1496 | 15 | 15 | http://eartheasy.com/live_lowflow_aerators.htm, cost from 2005 FEMP study of water conservation (http://www.pnl.gov/main/publications/external/technical_reports/PNNL-15320.pdf), total water use from Aquacraft study; East Bay Muni. Water District report Primary Source: Water Resources Engineering, I. Water Conservation Market Penetration Study. East Bay Municipal Utility District (2002) Other Supporting Sources: McMordie-Stoughton, K.L., Elliott, D., Parker, G., Solana, A. & Sullivan, G. Update of Market Assessment for Capturing Water Conservation Opportunities in the Federal Sector. Pacific North West National Laboratory (2005).
506 | Demonstrate and Deploy Zeolithic Dishwashers to Reduce Energy for Drying | R: Zeolithic DW | 2 | Residential | Dishwashing | Total dishwashing energy use, not including water heating consumption | kWh/cycle | 0.83 | 1.37 | 0 | 0 | 0 | 0 | 486 | 19 | 19 | LBNL Priority Setting Estimates spreadsheet; http://www.siemens.com/innovation/en/publications/publications_pof/pof_spring_2010/zeolith.htm Primary Source: Siemens product description (available in the UK)
507 | Demonstrate and deploy heat pump water heating in commercial kitchens for water heating and space cooling | C: Kitchen: HPWH | 3 | Commercial | Water Heating | Total electric cooling and electric, NG, and distillate water heating in all food service buildings | COP | 0.4457 | 0 | 5000 | 1500 | 5000 | 1500 | 3500 | 13 | 13 | WSU fact sheet (2003), http://www.energy.wsu.edu/documents/engineering/comm_water_htrs.pdf Primary Source: Washington State University (2005), "Energy Efficiency Fact Sheet: Commercial Water Heaters" Other Supporting Sources: Estimated new unit cost is $5,000, $3,500 more than a traditional water heater
508 | Improve insulation in new oil water heaters | R: Improved oil WH insulation | 4 | Residential | Water Heating | Total residential water heating by LPG and distillate fuel oil | Energy Factor | 0.62 | 0.53 | 848 | 795 | 848 | 795 | 53 | 13 | 13 | DOE TSD (2010) Ch5, Table 5.13.2, http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr.html Primary Source: U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy (EERE). (2011, March 30). Residential Heating Products Final Rule Analytical Tools. Retrieved from Appliance & Equipment Standards: http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html
509 | Replace standard gas storage water heaters with condensing gas storage water heaters | R: Condensing Gas WH | 4 | Residential | Water Heating | Total residential storage natural gas water heaters | Energy Factor | 0.77 | 0.59 | 1893 | 1079 | 1893 | 1079 | 814 | 13 | 13 | EPA ENERGY STAR, http://www.energystar.gov/index.cfm?c=water_heat.pr_crit_water_heaters Primary Source: Water Resources Engineering, I. Water Conservation Market Penetration Study. East Bay Municipal Utility District (2002)
510 | Replace commercial gas storage water heaters with condensing gas storage water heaters | C: Condensing Gas WH | 4 | Commercial | Water Heating | Total energy consumption by all commercial gas storage water heaters | Energy Savings (%) | 21.5% | 0% | 6630 | 5430 | 6630 | 5430 | 1200 | 13 | 13 | 1) Tables 6-11, 6-21, and 6-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf 2) Costs from distributors, CEC, and Navigant. September 2013. 2) Typical unit costs obtained from NCI data. Assumes 3 tankless WH with typical capacity of 180-250 kBtu/hr would be necessary to replace one typical storage unit with 200 kBtu/hr capacity.
511 | Deploy and standardize max tech tankless instantaneous gas water heaters to replace commercial storage water heaters in buildings with small hot water demands | C: Max Tech Tankless Gas WH for small loads | 3 | Commercial | Water Heating | All commercial gas small water heaters | Energy Savings (%) | 15% | 0% | 5625 | 5430 | 5625 | 5430 | 195 | 13 | 13 | Tables 6-8, 6-11, 6-21, and 6-23, Navigant Consulting. (2009). Energy Savings 1) Tables 6-8, 6-11, and 6-21, Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf 2) Typical unit costs obtained from NCI data. Assumes 3 tankless WH with typical capacity of 180-250 kBtu/hr would be necessary to replace one typical storage unit with 200 kBtu/hr capacity.
512 | Deploy and standardize max tech gas tankless water heaters (Level 8) to replace residential storage water heaters | R: Tankless Gas WH, level 8 (No FS) | 4 | Residential | Water Heating | Total residential storage natural gas water heaters | Energy Factor | 0.95 | 0.59 | 3083 | 1079 | 3083 | 1079 | 2004 | 19 | 13 | Rheem website, http://www.rheem.com/product.aspx?id=5AE02BB6-A8A9-49DE-8F3A-08DA596EB980, prices based on large WH in residential TSD
513 | Encourage adoption of system that captures waste heat from space cooling (desuperheater) for water heating | C: AC waste heat recovery (for WH) - desuperheater | 3 | Commercial | Water Heating | Total commercial water heating in the hottest two climates | Energy Savings (%) | 10% | 0% | 600 | 0 | 600 | 0 | 600 | 13 | 13 | Savings from NCI Commercial Appliances 2009 report. P. 207, Table 6-19. Cost: See 1. http://www.cdhenergy.com/presentations/ASHRAE%20Chicago%201999%20Desuperheater%20Impact.pdf; 2. http://stampededrive.net/PDF/BuilderGuide3E.pdf; 3. http://www.bpa.gov/energy/n/reports/evaluation/commercial/pdf/BPA-Evaluation_Reverse-Cycle-Chillers_09-30-09.pdf
516 | Decrease cost and deploy thermosiphon (indirect, passive) solar water heaters (gas to gas back-up) | R: Solar WH, Gas - Ind. Passive | 2 | Residential | Water Heating | Total gas water heating energy consumption | Energy Savings (%) | 44.26% | 0% | 0 | 0 | 0 | 0 | 2030 | 13 | 13 | SWH roadmap; California Center for Sustainable Energy Solar Water Heating Pilot Program 3/2011; Cold Climate Solar Domestic Water Heating Systems: Cost/Benefit Analysis and Opportunities for Improvements (Burch et. Al.) Primary Source: Itron, Inc.; "California Center for Sustainable Energy Solar Water Heating Pilot Program" (3/2011) Federal Energy Management Program, "Solar Water Heating with Low-Cost Plastic Systems" (1/2012) Other Supporting Sources: Hudon, Burch "Solar Water Heating Roadmap" (in preperation)
520 | Accelerate retirement of home water heaters from 16 to 12 years | R: Early Retirement of Inefficient WH Units | 4 | Residential | Water Heating | All types of residential water heaters older than 10 years | Energy Factor | 0.17 | 0 | 890 | 678.9767 | 890 | 678.9767 | 211.0233 | 13 | 13 | Average of 517-519
521 | Increase usage of low-temperature detergent in residential dishwashers | R: DW Low Temperature Detergent | 3 | Residential | Dishwashing | Total residential water heating for dishwashing energy consumption | Energy Savings (%) | 20% | 0% | 57.5962 | 46.7969 | 57.5962 | 46.7969 | 10.7993 | 19 | 19 | Chemical and Engineering News, Vol. 85 #5, Jan. 2007; Other Primary Source: Tables 8-24 and 8-25 Navigant Consulting; "Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances" (2009) Other Supporting Sources: Chemical and Engineering News, Vol. 85 #5, Jan. 2007
524 | Deploy heat pump water heaters to replace all electric water heaters in commercial buildings (no fuel switching) | C: HPWH (COP 4) | 3 | Commercial | Water Heating | Total energy consumption by all commercial electric storage water heaters | Energy Savings (%) | 68% | 0% | 0 | 0 | 0 | 0 | 10411 | 13 | 13 | 1) Energy savings from first principles and pg. 194 Tables 6-11, 6-21, and 6-24 in Goetzler, W., Zogg, R., Ahlfeldt, J., Hiraiwa, H., Sathe & Sutherland. Energy Savings Potential and RD & D Opportunities for Commercial Building Appliances. December 21, 2009. 2) Installed cost estimates obtained for a typical unit with input capacity of 54kW and storage of 120 gal for a standard electric resistance WH, and equivalent HPWH of input capacity of 10-16kW. Source: AO Smith quote. *Heat pump water heaters are not sold with a tank; however, HPWH can be added to an existing WH system and can use an existing tank. The cost of the tank is not included in the incremental cost calculation.
525 | Demonstrate and deploy advanced CO2 heat pump water heaters with COP of 5.1 (no fuel switching). EcoCute. | R: Adv. HPWH (COP 5.1, EF 3.6) | 3 | Residential | Water Heating | Total electric water heating energy consumption | Energy Factor (converted from 5.1 COP) | 3.5581 | 0.92 | 5400 | 615 | 5400 | 615 | 4785 | 13 | 13 | 1) Baseline unit cost: Total installed cost is $566 ($2008) (2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses) Cost adjusted from $2008 to $2014 (http://data.bls.gov/cgi-bin/cpicalc.pl) 2) Efficient unit cost: '-This is a target cost for US manufacturers, assuming a 50% cost compression for large scale manufacturing. Unit cost is 814,643 yen in October 2011 (Source: http://www.r744.com/articles/150420111031.php). Yen to US dollar conversion rate from October 2011 is 1 USD = 78.3331 JPY (Source: http://www.exchangerates.org.uk/USD-JPY-31_10_2011-exchange-rate-history.html). Cost adjusted from $2011 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl) 3) Efficiency target: This is a target for EF for US HPWH manufacturers. Panasonic released CO2 HPWH with COP of 5.1 (Source: r744.com, "Eco Cute Update: new line-up with 5.1 COP by Panasonic, upgrades by Hitachi and domestic statistics in Japan" (2011)) 5.1 COP converted to 3.56 EF, using a 0.697 conversion factor which accounts for differences between lab rating and typical field performance (Source: Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007)) 4) Base performance: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment -EIA AEO 2014 Early Release, http://www.eia.gov/forecasts/aeo/er/index.cfm -r744.com, "Eco Cute Update: new line-up with 5.1 COP by Panasonic, upgrades by Hitachi and domestic statistics in Japan" (2011) -Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007) -2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses -http://data.bls.gov/cgi-bin/cpicalc.pl - http://www.exchangerates.org.uk/USD-JPY-31_10_2011-exchange-rate-history.html
526 | Deploy highest efficiency heat pump water heaters in homes (no fuel switching) | R: HPWH (EF 2.4) | 4 | Residential | Water Heating | Total electric water heating energy consumption | Energy Factor | 2.4 | 0.92 | 1299 | 615 | 1299 | 615 | 684 | 13 | 13 | 1) Baseline unit cost: Total installed cost is $566 ($2008) (2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses) Cost adjusted from $2008 to $2014 (http://data.bls.gov/cgi-bin/cpicalc.pl) 2) Efficent unit cost: GE listed MRSP, http://products.geappliances.com/ApplProducts/Dispatcher?REQUEST=SpecPage&Sku=GEH50DEEDSR -2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment -EIA AEO 2014 Early Release, http://www.eia.gov/forecasts/aeo/er/index.cfm -2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 5 - Engineering Analysis -http://products.geappliances.com/ApplProducts/Dispatcher?REQUEST=SpecPage&Sku=GEH50DEEDSR DOE TSD (2010), Table 5.7.4, 5.13.4 (MSP); Tables 6-11 and 6-24, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances; EPA ENERGY STAR doc Primary Source: Fitzpatrick, S, Murray, M; "GE Heat Pump Water Heater Report", Advanced Energy (2011) Other Supporting Sources: Navigant Consulting Research and Development Roadmap for Water Heating. Department of Energy (2011).
527 | Replace gas water heaters with tankless gas water heaters with improved heat exchangers and condensate mgmt (Level 5) | R: Tankless With Improved Heat Exchanger Area | 3 | Residential | Water Heating | Total gas water heating energy consumption | Energy Factor | 0.84 | 0.59 | 2935 | 1021.72 | 2935 | 1021.72 | 1913.28 | 13 | 13 | DOE TSD (2010), http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr.html
528 | Increase insulation standard in residential tank H2O heaters: gas | R: Gas storage WH - more insulation | 5 | Residential | Water Heating | Total residential storage natural gas water heaters | Energy Factor | 0.63 | 0.59 | 1244 | 1079 | 1244 | 1079 | 165 | 13 | 13 | DOE TSD (2010), http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr.html
529 | Increase insulation standard in residential tank H2O heaters: electric | R: Elec. storage WH - more insulation | 5 | Residential | Water Heating | Total electric water heating energy consumption | Energy Factor | 0.95 | 0.9 | 0 | 0 | 0 | 0 | 408 | 13 | 13 | DOE TSD (2010), http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr.html
530 | Increase insulation standard in residential tank H2O heaters: oil | R: Oil storage WH - more insulation | 5 | Residential | Water Heating | Total residential water heating by LPG and distillate fuel oil | Energy Factor | 0.58 | 0.53 | 0 | 0 | 0 | 0 | 1333 | 13 | 13 | DOE TSD (2010), http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr.html
531 | Increase deployment of insulating blankets on residential water heaters | R: WH Insulation Blankets | 4 | Residential | Water Heating | Total residential storage water heater (with no blanket installed) energy consumption | Energy Savings (%) | 50% | 0% | 0 | 0 | 0 | 0 | 20 | 13 | 13 | EERE Water Heater Final Rule Analytical Spreadsheet (consistent with the TSD) (http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html) Primary Source: U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy (EERE). (2011, March 30). Residential Heating Products Final Rule Analytical Tools. Retrieved from Appliance & Equipment Standards: http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html
532 | Increase deployment of insulating blankets on commercial WH | C: WH insulation blankets | 4 | Commercial | Water Heating | Total commercial water heater standby energy losses | Energy Savings (%) | 40% | 0% | 0 | 0 | 0 | 0 | 20 | 13 | 13 | Tables 6-11 and 6-18, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Standby losses estimated based on Federal Standard (329 Btu/hr), combined with CBECS water heater energy assuming one water heater per building on average (3%). Primary Source: Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy (EERE). (2011, March 30). Residential Heating Products Final Rule Analytical Tools. Retrieved from Appliance & Equipment Standards: http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html
534 | Deploy timers for existing water heaters | R: Install night time timers on water heaters | 4 | Residential | Water Heating | Total residential storage electric and natural gas water heaters | Energy Savings (%) | 7.5% | 0% | 0 | 0 | 0 | 0 | 40 | 13 | 13 | Original source: http://michaelbluejay.com/electricity/waterheaters.html. New sources used for cost & savings data: Energy Efficiency & Environmental News: 1) Water Heater Timers s insulated Jackets. Florida Energy Extension Service and Gary Cook. January 1993. http://www.greatlakeshomeperformance.com/elibrary/Water%20Heater%20Timers%20&%20Jackets.pdf; 2) Exclusion of timers for gas water heaters due to: Energy Efficient Water Heating. LBNL. January 1995. http://www.ces.ncsu.edu/depts/fcs/pdfs/energy_efficient.pdf)
536 | Develop max tech option for residential oil water heaters | R: Multiple Flue Design, Insulation for oil WH | 3 | Residential | Water Heating | Total residential water heating by LPG and distillate fuel oil | Energy Factor | 0.68 | 0.53 | 955 | 795 | 955 | 795 | 160 | 13 | 13 | http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr.html Primary Source: Table 5.13.3, U.S. Department of Energy, Technical Support Document (2010)
541 | Replace residential gas storage with whole-home gas tankless water heaters (Tankless Level 3) | R: Replace Tank w/ Tankless Gas (Level 3) | 4 | Residential | Water Heating | Total residential storage natural gas water heaters | Energy Factor | 0.8 | 0.59 | 2303 | 1079 | 2303 | 1079 | 1224 | 13 | 13 | EERE Water Heater Final Rule Analytical Spreadsheet (consistent with the TSD) (http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html)
543 | Replace standing pilot in new gas WH with electronic ignitions | R: Gas water heater electronic ignition | 5 | Residential | Water Heating | All residential gas water heaters with pilot lights | Energy Factor | 0.64 | 0.59 | 1523 | 1079 | 1523 | 1079 | 444 | 13 | 13 | EERE Water Heater Final Rule Analytical Spreadsheet (consistent with the TSD) (http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html) Primary Source: U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy (EERE). (2011, March 30). Residential Heating Products Final Rule Analytical Tools. Retrieved from Appliance & Equipment Standards: http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html
544 | Replace residential gas storage with whole-home gas tankless water heaters (Tankless Level 4) | R: Replace Tank w/ Tankless Gas (Level 4) | 3 | Residential | Water Heating | Total residential storage natural gas water heaters | Energy Factor | 0.82 | 0.59 | 2377 | 1079 | 2377 | 1079 | 1298 | 13 | 13 | EERE Water Heater Final Rule Analytical Spreadsheet (consistent with the TSD) (http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html)
548 | Decrease cost and deploy Forced circulation (indirect active) SWH (El. to El. back up) TARGET | R: Solar WH elec. BU - indirect active (no FS)* | 0 | Residential | Water Heating | Total electric water heating energy consumption | Energy Savings (%) | 37.5% | 0% | 1200 | 0 | 1200 | 0 | 1200 | 13 | 13 | SWH roadmap; Primary Source: Itron, Inc.; "California Center for Sustainable Energy Solar Water Heating Pilot Program" (3/2011) Federal Energy Management Program, "Solar Water Heating with Low-Cost Plastic Systems" (1/2012) Other Supporting Sources: Hudon, Burch "Solar Water Heating Roadmap" (in preperation)
549 | Decrease cost and deploy Forced circulation (indirect active) SWH (gas to gas back up) TARGET | R: Solar WH gas BU - indirect active (no FS)* | 0 | Residential | Water Heating | Total gas water heating energy consumption | Energy Savings (%) | 37.5% | 0% | 1200 | 0 | 1200 | 0 | 1200 | 13 | 13 | SWH roadmap; Primary Source: Itron, Inc.; "California Center for Sustainable Energy Solar Water Heating Pilot Program" (3/2011) Federal Energy Management Program, "Solar Water Heating with Low-Cost Plastic Systems" (1/2012) Other Supporting Sources: Hudon, Burch "Solar Water Heating Roadmap" (in preperation)
553 | Deploy ground source heat pumps to all single family homes, no fuel switching | R: Single Family GSHP | 4 | Residential | Heating/Cooling/Water | Total electric heating, electric hot water, and proportion of electric cooling in homes with electric heating | Energy Savings (%) | 64.8% | 0% | 20319 | 5919 | 20319 | 5919 | 14400 | 15 | 15 | ORNL Residential Retrofti Tech potential Primary Source: Liu, X. Assessment of National Benefits from Retrofitting Existing Single-Family Homes with Ground Source Heat Pump Systems. Oak Ridge National Laboratory (2010) Hughes, P.J. Geothermal ( Ground-Source ) Heat Pumps: Market Status , Barriers to Adoption , and Actions to Overcome Barriers. Oak Ridge National Laboratory (2008) Other Supporting Sources: Office of the Deputy Under Secretary of Defense Report to Congress: Ground-Source Heat Pumps at Department of Defense Facilities. (2007) Hughes, P.J. & Shonder, J.A. The Evaluation of a 4000-Home Geothermal Heat Pump Retrofit at Fort Polk , Louisiana: Final Report. Oak Ridge National Laboratory (1998)
557 | Commercialize, demonstrate, and deploy comprehensive home automation system | R: Home Automation | 3 | Residential | HVAC/Lighting | Total residential energy consumption in all single-family homes | Energy Savings (%) | 6% | 0% | 600 | 0 | 600 | 0 | 600 | 20 | 20 | 1) Cost as found $1000 (without PC, assume most homes have a PC); cost compressed to $600: Williams, Matthews, Breton, and Brady; "Use of a Computer-Based System to Measure and Manage Energy Consumption in the Home" IEEE 2006 Other Supporting Sources: Wireless home automation networks: A survey of architectures and technologies 2) Energy savings: Effectiveness of Displaying Energy Consumption Data in residential buildings: To Know is to Change. Tsuyoshi Ueno, Centeral Research Institute of Electric Power Industry (CRIEPI). Kiichiro Tsuji, Osaka University. Yukio Nakano, CRIEPI.
558 | Research, demonstrate, and deploy spray-cooled condenser for rooftop AC units in commercial buildings | C: Spray-cooled Condenser | 4 | Commercial | Cooling | Total commercial electric load of rooftop AC units (residential style) | COP | 3.53 | 3.04 | 0.525 | 0 | 0.525 | 0 | 0.525 | 15 | 15 | Friterm document pg. 4/13 Primary Source: Acul, H. Air Cooled Condensers And Their Effect On Energy. 1-13 (2008)
561 | Research, demonstrate, and deploy climate optimized hot-dry A/C in homes. (To assure adequate dehumidification in most climates, the evaporator provides extra cooling which is unnecessary in hot-dry climates.) | R: Hot-dry AC | 2 | Residential | Cooling | Total cooling in mixed-dry and hot-dry climates | Energy Savings (%) | 20% | 0% | 0 | 0 | 0 | 0 | 246 | 16 | 16 | Primary Source: Desroches, L.-B. et al. Max Tech and Beyond (2011) & Sachs, Lin, Lowenberger. Emergin Energy-Saving HVAC Technologies and Practices for the Buildings Sector, AEEE (2009)
562 | Research, demonstrate, and deploy climate optimized hot-dry A/C in commercial buildings. (To assure adequate dehumidification in most climates, the evaporator provides extra cooling which is unnecessary in hot-dry climates.) | C: Hot-dry AC | 2 | Commercial | Cooling | Total cooling in hot, dry climates in all commercial buildings | Energy Savings (%) | 20% | 0% | 0 | 0 | 0 | 0 | 0.10933 | 15 | 15 | Primary Source: Desroches, L.-B. et al. Max Tech and Beyond (2011) & Sachs, Lin, Lowenberger. Emergin Energy-Saving HVAC Technologies and Practices for the Buildings Sector, AEEE (2009)
563 | Demonstrate and deploy pre-dehumidification multiple-small plate dehumidifiers in commercial buildings in hot, humid climates | C: MSP Dehumidifier | 1 | Commercial | Cooling | Total cooling in hot, humid climates in all commercial buildings | Energy Savings (%) | 32% | 0% | 0.5 | 0 | 0.5 | 0 | 0.5 | 15 | 15 | MTAB, nauticadehumid.com Primary Source: MSP Technology, "Dehumidification Equipment for Recirculated Air and Dedicated Outside Air Systems (DOAS)" Desroches, L.-B. et al. Max Tech and Beyond (2011)
564 | Demonstrate and deploy magnetic bearing variable speed centrifugal chillers | C: Magnetic Bearing Variable Speed Centrifugal Chiller | 3 | Commercial | Cooling | All commercial centrifugal chillers | kW/ton cooling | 0.5 | 0.9 | 3.4 | 2.1 | 3.4 | 2.1 | 1.3 | 25 | 25 | MTAB, turbocor_chiller.pdf Primary Source: U.S. Navy Technology Validation, FEMP: "Evaluation of a Variable-speed Centrifugal Compressor with Magnetic Bearings". Pg 3. Fig 4 & 5. http://www1.eere.energy.gov/femp/pdfs/etcs_vscompressor.pdf Desroches, L.-B. et al. Max Tech and Beyond (2011)
566 | CBI high efficiency RTU specification challenge | C: Adv. RTU (IEER 18) | 4 | Commercial | Cooling | Total commercial cooling by rooftop AC units (RTUs) | IEER | 18 | 11.4 | 1.984 | 0.8525 | 1.984 | 0.8525 | 1.1315 | 15 | 15 | 1) Base and efficient unit costs: Base cost from EIA Tech Forecast 2013; efficient cost intrapolated based on EIA Tech Forecast data for IEER 20.8 unit. 2) Performance estimated from Challenge specifications. DOE and PrivateSector Partners Introduce a New Money-Saving Specification for Commercial Air Conditioners", 2011. Daikon McQuay Rebel RTU Specifications
567 | Improve scroll compressor performance - TARGET (COP) | C: Improved scroll compressor* | 0 | Commercial | Cooling | Commercial cooling: Scroll | Compressor COP | 4.7 | 3.4 | 1.05 | 1.8133 | 1.05 | 1.8133 | 0.76333 | 20 | 20 | 28% savings from Bouza. Baseline efficiency estimated from multiple references: http://www.hitachi-ap.com/products/business/compressor/scroll/aircon_spec.html, http://www.emersoncanada.ca/pages/energy/presentations/Scroll_Compressor_Technology_Optimizing_Efficiency_Feb08.pdf) Primary Source: Personal communication: Bouza, DOE Other Supporting Sources: Manufacturer presentation (http://www.emersoncanada.ca/pages/energy/presentations/Scroll_Compressor_Technology_Optimizing_Efficiency_Feb08.pdf) and specifications: Hitachi EU Series DC Inverter controlled series, Mitsubishi R407C & 410A
574 | Natural ventilation cooling system in all new homes (single/multi/mobile) | R: Nat. Ventilation Cooling (N, exc. Hot-humid CZ) | 2 | Residential | Building | Total cooling in new homes in all but hot-humid climates | Energy Savings (%) | 30% | 0% | 0 | 0 | 0 | 0 | 2400 | 30 | 30 | Cardinale, et. Al. (http://www.sciencedirect.com/science/article/pii/S0378778802000245), WBDG (http://www.wbdg.org/resources/naturalventilation.php)
575 | Demonstrate and deploy insulating and reflective attachments to homes | R: Window Attachments | 3 | Residential | HVAC | Total cooling lost due to solar gain through residential windows that can benefit from attachments (assuming 50% of homes have windows that can benefit from advanced attachments (beyond typical blinds or curtains which may not be properly utilized for greater savings) | Energy Savings (%) | 48.15% | 0% | 2367 | 720 | 2367 | 720 | 1647 | 30 | 30 | DOE-EPA Attachments industry presentation; http://www.solar-components.com/comfortex.htm Primary Source: Savings: first principles calculation from R- and SHGC- impacts of product Price: Comfortex. Manufacturer & expert interviews Other Supporting Sources: Kotey, N.A., Wright, J.L., Barnaby, C.S., Collins, M.R., "Solar Gain Through Windows with Shading Devices: Simulation versus Measurement," ASHRAE Transactions, Vol. 115, Pt. 2, (2009)
576 | Demonstrate and deploy insulating and reflective attachments to pre-2010 commercial buildings | C: Window Attachments [E] | 3 | Commercial | HVAC | All commercial windows that can benefit from attachments in pre-2010 buildings | Energy Savings (%) | 51.26% | 0% | 4.68 | 1.44 | 4.68 | 1.44 | 3.24 | 40 | 40 | DOE-EPA Attachmentsindustry presentation; http://www.solar-components.com/comfortex.htm Primary Source: Savings: first principles calculation from R- and SHGC- impacts of product Price: Comfortex Manufacturer & expert interviews Other Supporting Sources: Kotey, N.A., Wright, J.L., Barnaby, C.S., Collins, M.R., "Solar Gain Through Windows with Shading Devices: Simulation versus Measurement," ASHRAE Transactions, Vol. 115, Pt. 2, (2009)
585 | Increase adoption of standard storm windows on existing 1-pane metal framed windows in single and multi family homes | R: Standard storms on single pane windows [E] | 4 | Residential | HVAC | Total energy losses due to conduction for single pane glass windows for all homes built before 2010 | Energy Savings (%) | 45.79% | 0% | 2250 | 0 | 2250 | 0 | 2250 | 30 | 30 | 1) Costs were adjusted based on PNNL RFI response: $150 per 30"x60" window, uninstalled from http://www.efficientwindowcoverings.org/understanding-window-coverings/storm-window/ 2) Kohler, C Letter report for low-e storm window retrofits, 2006
586 | Increase adoption of low-e standard storm windows on existing 1-pane metal framed windows in homes | R: Low-e Storms [E] | 4 | Residential | Building | Total energy losses due to conduction and radiation for single pane glass windows for all homes built before 2010 | Energy Savings (%) | 54.63% | 0% | 2250 | 0 | 2250 | 0 | 2250 | 30 | 30 | 1) Costs were adjusted based on PNNL RFI response: $150 per 30"x60" window, uninstalled from http://www.efficientwindowcoverings.org/understanding-window-coverings/storm-window/ 2) Kohler, C Letter report for low-e storm window retrofits, 2006
587 | Increase adoption of low-e standard storm windows on existing 1-pane metal framed windows in commercial buildings | C: Low-e Storms [E] | 4 | Commercial | Building | Total commercial radiative and conductive window load for pre-2010 buildings with single pane windows (includes solar heat gain loss during cooling season as well as solar heat gain benefit during heating season) | Energy Savings (%) | 54.63% | 0% | 4.32 | 0 | 4.32 | 0 | 4.32 | 40 | 40 | 1) Costs were adjusted based on PNNL RFI response: $150 per 30"x60" window, uninstalled from http://www.efficientwindowcoverings.org/understanding-window-coverings/storm-window/ 2) Kohler, C Letter report for low-e storm window retrofits, 2006
590 | Deploy advanced walls in new residential buildings (offset frame with spray foam) | R: R-30 Walls (N) | 2 | Residential | Building | Total heating and cooling lost through walls in new single/multi/mobile homes | R-value | 37.1 | 11.1 | 962 | 0 | 962 | 0 | 962 | 30 | 30 | Building Science, research report 0903, LaFrance Primary Source: Straube, J. and Smegal, J.; Building America Special Research Project: High-R Walls Case Study Analysis; Building Science Corporation 2009 (updated 2011)
591 | Deploy advanced walls in existing residential buildings, i.e., exterior insulation finishing systems (EIFS) | R: R-30 Walls (E) | 2 | Residential | Building | Total heating and cooling lost through walls in single-family homes built before 2010 | R-value | 36.2 | 6 | 20800 | 0 | 20800 | 0 | 20800 | 30 | 30 | Building Science, research report 0903, LaFrance Primary Source: Straube, J. and Smegal, J.; Building America Special Research Project: High-R Walls Case Study Analysis; Building Science Corporation 2009 (updated 2011)
593 | Deploy advanced walls in new commercial buildings (offset frame with spray foam) | C: EIFS R-30 Walls (N) | 1 | Commercial | Building | Total heating and cooling energy lost through wall in all new commercial buildings | R-value | 37.1 | 17 | 0 | 0 | 0 | 0 | 2.7 | 40 | 40 | Building Science, research report 0903, LaFrance and LBNL "Overview of US Building Stock", http://eetd.lbl.gov/ie/pdf/LBNL-43640.pdf
594 | Deploy advanced walls in existing commercial buildings, i.e., exterior insulation finishing systems (EIFS) | C: EIFS R-30 Walls (E) | 1 | Commercial | Building | Total heating and cooling load due to energy loss through walls in all commercial buildings built before 2010 | R-value | 36.2 | 11.1 | 0 | 0 | 0 | 0 | 4.32 | 40 | 40 | Building Science, research report 0903, LaFrance and LBNL "Overview of US Building Stock", http://eetd.lbl.gov/ie/pdf/LBNL-43640.pdf
600 | Develop integrated roofing package for existing homes in non-hot climates using phase change materials (PCM) for R-75 equivalent | R: R-75 PCM Roofs, non-hot CZ (E) | 2 | Residential | Building | Total heating and cooling energy lost through attics in all existing homes in all non-hot climates | R-value | 75 | 23.1875 | 3186.9735 | 0 | 3186.9735 | 0 | 3186.9735 | 30 | 30 | Miller, W. & Kosny, J. Next-Generation Roofs and Attics for Homes. ACEEE Summer Study on Energy Efficiency in Buildings 180-195 (2008)
605 | Demonstration and deployment assistance to advanced (CO2) HPWH w COP of 5.1 (no fuel switching) | C: Adv. HPWH (COP 5.1, EF 3.6) (no FS) | 2 | Commercial | Water Heating | Total energy consumption by all commercial electric storage water heaters | EF (converted from 5.1 COP) | 3.5581 | 1 | 30830 | 2799 | 30830 | 2799 | 28031 | 13 | 13 | Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances Primary Source: r744.com, "Eco Cute Update: new line-up with 5.1 COP by Panasonic, upgrades by Hitachi and domestic statistics in Japan" (2011) Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007) Other Supporting Sources: Navigant Consulting Research and Development Roadmap for Water Heating. Department of Energy (2011).
608 | Deploy highest efficiency heat pump water heaters commercial buildings w small WH needs (no FS) | C: HPWH (no FS) | 4 | Commercial | Water Heating | All commercial electric small water heaters | Energy Factor | 2.27 | 0.81 | 2097 | 1022 | 2097 | 1022 | 1075 | 13 | 13 | $150 premium for 120 gallon tank vs 50 gallon tank, (consistent with the TSD). U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy (EERE). (2011, March 30). Residential Heating Products Final Rule Analytical Tools. Retrieved from Appliance & Equipment Standards: http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html
613 | Replace all commercial and industrial lighting with LEDs - TARGET | C/I: LEDs, SSL Program Goal (2020)* | 0 | Commercial/Industrial | Lighting | All lighting in all types of commercial and industrial buildings | lumens/watt | 210 | 67 | 85 | 97.5 | 85 | 97.5 | -97.5 | 26 | 5 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
614 | Replace all residential lighting with LEDs - TARGET | R: LEDs, SSL Program Goal (2020)* | 0 | Residential | Lighting | Total lighting energy consumption in all homes | lumens/watt | 210 | 26 | 4 | 1.2 | 4 | 1.2 | -17.2 | 86 | 5 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
615 | Deploy max tech compressor racks | C: Remote condensing units for refrigeration | 2 | Commercial | Refrigeration | All supermarket compressor racks | Energy Savings (%) | 9% | 0% | 38016 | 0 | 38016 | 0 | 38016 | 15 | 15 | Table 5-9, Navigant CRE
616 | Deploy max tech walk-in coolers and freezers | C: Max Tech Walk-In Refrigerator | 2 | Commercial | Refrigeration | All walk-in coolers and freezers | Energy Savings (%) | 54% | 0% | 1554 | 0 | 1554 | 0 | 1554 | 11 | 11 | Table 5-13, 5-14, Navigant CRE
617 | Deploy and standardize max tech refrigerated food service equipment | C: Max Tech food service equipment | 2 | Commercial | Refrigeration | Food Prep Equipment | Energy Savings (%) | 56% | 0% | 379 | 0 | 379 | 0 | 379 | 12 | 12 | Table 5-17, Navigant CRE
619 | Deploy max tech beverage merchandisers | C: Max Tech Refrig. Beverage Merchandisers | 2 | Commercial | Refrigeration | All commercial beverage merchandisers | Energy Savings (%) | 55% | 0% | 620 | 0 | 620 | 0 | 620 | 15 | 15 | Table 5-22, Navigant CRE
621 | Deploy and standardize max tech supermarket display cases | C: Max Tech Supermarket Display Case | 2 | Commercial | Refrigeration | Display Cases, Supermarkets | Energy Savings (%) | 36% | 0% | 1592 | 0 | 1592 | 0 | 1592 | 10 | 10 | Table 5-6,5-7,5-8 Navigant CRE
622 | Incentives or campaign to build max tech supermarkets | C: Max Tech Supermarket | 2 | Commercial | Refrigeration | All supermarket refrigeration systems (cond, comp, walk-ins, & display) | Energy Savings (%) | 28.4% | 0% | 228536 | 0 | 228536 | 0 | 228536 | 12 | 12 | Table 5-12, 4-3, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment (http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_refrig_report_10-09.pdf)
624 | Resi code: 30% lower than today, starting in 2017 | R: Code target: 30%* | 0 | Residential | Building | Total heating and cooling in all new single-family homes | Energy Savings (%) | 30% | 0% | 0 | 0 | 0 | 0 | 0 | 30 | 30 | Program goal
625 | Resi code: 50% lower than today, starting in 2023 | R: Code target: 50%* | 0 | Residential | Building | Total heating and cooling in all new single-family homes | Energy Savings (%) | 50% | 0% | 0 | 0 | 0 | 0 | 0 | 30 | 30 | Program goal
628 | Develop, demonstrate, and deploy integrated heat pumps (No fuel switching) | R: IHP | 2 | Residential | Heating/Cooling/Water | Total electric heating, electric hot water, and proportion of electric cooling in homes with electric heating | Energy Savings (%) | 50% | 0% | 8184 | 5207 | 8184 | 5207 | 2977 | 15 | 15 | 1) Baxter, V.; Murphy, R; Rice, K; Craddick, B; "Development of a Small Integrated Heat Pump (IHP) for Net Zero Energy Homes" 9th International IEA Heat Pump Conference (2008): a. Standard unit cost: Estimated based on average between installed cost estimates of $5,408 and $6,013, minus $503 for the cost of the WH b. Efficient unit cost: Estimated based on average between installed cost estimates of $7,582 and $8,786 c. Used 50% as conservative estimate for total energy savings based on 46-67% range: "For the air source IHP version, the simulation results showed ~46-67% energy savings depending upon location. For the ground-source IHP version, the simulation showed over 50% savings in all locations" 2) 2008 ORNL paper "DEVELOPMENT OF A SMALL INTEGRATED HEAT PUMP (IHP) FOR NET ZERO ENERGY HOMES"
629 | Max Tech Level ASHP | R: Max Tech ASHP | 0 | Residential | Heating & Cooling | All electric heating, proportion of cooling in homes with electric heating | Energy Savings (%) | 40.77% | 0% | 4508 | 4680 | 4508 | 4680 | -172 | 15 | 15 | Personal communication: Bouza, DOE. Hewitt, N.J., Huang, M.J., Anderson, M. & Quinn, M. Advanced air source heat pumps for UK and European domestic buildings. Applied Thermal Engineering 31, 3713-3719 (2011); Res CAC, HP, and Furnace TSD, June 2011.
630 | Residential absorption gas heat pump water heaters (no fuel switching) - TARGET | R: Absorption Gas HPWH* | 0 | Residential | Water Heating | Total gas water heating energy consumption | Energy Factor | 1.3 | 0.59 | 1800 | 1116 | 1800 | 1116 | 684 | 13 | 13 | 1) Efficiency: target EF for manufacturers: M. Garrabrant, Stone Mountain Technologies Inc, Development & Validation of a Gas-Fired Residential Heat Pump Water Heater, January 2013, Report DE-EE0003985, http://www.osti.gov/scitech/servlets/purl/1060285 2) Total installed cost is $1027 ($2008) (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses) Cost adjusted from $2008 to $2014 (Source: Baseline cost from EERE Water Heater Final Rule Analytical Spreadsheet (http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html). 3) This is a target installed cost for 2030 (Source: M. Garrabrant, Stone Mountain Technologies Inc, Development & Validation of a Gas-Fired Residential Heat Pump Water Heater, January 2013, Report DE-EE0003985, http://www.osti.gov/scitech/servlets/purl/1060285)
634 | Develop, demonstrate, and deploy integrated heat pumps: fuel switching only | R: IHP (FS) | 2 | Residential | Heating/Cooling/Water | All non-electric heating and water heating plus cac | Energy Savings (%) | 42.5% | 0% | 8184 | 3919 | 8184 | 3919 | 4265 | 15 | 15 | 2008 ORNL paper "DEVELOPMENT OF A SMALL INTEGRATED HEAT PUMP (IHP) FOR NET ZERO ENERGY HOMES" Primary Source: Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy., http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf
635 | Develop, demonstrate, and deploy integrated heat pumps: fuel switching only (commercial) | C: IHP (FS) | 2 | Commercial | Heating/Cooling/Water | Non-electric space heating, proportion of cooling and hot water | Energy Savings (%) | 42.5% | 0% | 31530 | 21830 | 31530 | 21830 | 0.64667 | 15 | 15 | Tables 6-11, 6-21, and 6-23, Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy., http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Murphy,R; Rice, C; Baxter, V; Craddick, W. "Air-Source Integrated Heat Pump for NetZero-Energy Houses: Technology Status Report". Oak Ridge National Laboratory ORNL/TM-2007/112 Baxter, V.; Murphy, R; Rice, K; Craddick, B; "Development of a Small Integrated Heat Pump (IHP) for Net Zero Energy Homes" 9th International IEA Heat Pump Conference (2008)
638 | Develop, demonstrate, and deploy integrated heat pumps: no fuel switching (commercial) | C: IHP | 2 | Commercial | Heating/Cooling/Water | Electric space heating (ASHP, GSHP, screw &other) and proportion of cooling and hot water in building with electric space heating (assumption) | Energy Savings (%) | 50% | 0% | 6.6667 | 3.1833 | 6.6667 | 3.1833 | 3.4833 | 15 | 15 | 1) Assuming 50% total energy savings as used in the residential IHP measure (# 628) (Baxter, V.; Murphy, R; Rice, K; Craddick, B; "Development of a Small Integrated Heat Pump (IHP) for Net Zero Energy Homes" 9th International IEA Heat Pump Conference (2008), "For the air source IHP version, the simulation results showed ~46-67% energy savings depending upon location. For the ground-source IHP version, the simulation showed over 50% savings in all locations") 2) Standard unit cost estimated based on the cost typical of a commercial rooftop heat pump ($5,850) and commercial electric storage WH ($3,700) (EIA - Technology Forecast Updates – Residential and Commercial Building Technologies, September 2013) 3) Efficient unit cost estimated based on the list price of 15,015 euros for a 90kBtu/Hr IHP (with integrated electric WH), which is equal to roughly $20,000 (ORIGEN COMPLETE PRICELIST 2013) 4) Incremental cost calculated based on the cost difference for two 90kBTU/Hr (7.5 Tons) systems for a 3,000 square foot building, assuming a typical ratio of 40 tons per 15,000 sq ft building.
642 | Increase adoption of R-5 replacement windows in new homes or at retrofit | R: R-5 Windows | 4 | Residential | Building | Total heating and cooling lost through windows due to conduction in all homes | R-value | 5 | 1.8612 | Confidential | Confidential | Confidential | Confidential | Confidential | 30 | 30 | 1) Costs and energy savings from PNNL 2013 Highly Insulating Windows Volume Purchase Program Final Report. February 2013.
643 | Increase adoption of R-5 replacement windows in commercial buildings | C: R-5 Windows | 4 | Commercial | Building | Total window conductive loss in all commercial buildings | R-value | 5 | 1.6129 | Confidential | Confidential | Confidential | Confidential | Confidential | 40 | 40 | Program Primary Source: 6. Apte, J. & Arasteh, D. Window-Related Energy Consumption in the US Residential and Commercial Building Stock. Buildings 1-38 (Berkeley, CA, 2006).
646 | Demonstrate and deploy radiative barrier in attics (above ducts) in new homes in hot climates | R: Attic Rad. Barrier (Ducts), Hot CZ (N) | 5 | Residential | Building | Total cooling in all new homes in hot climates | Energy Savings (%) | 11.6% | 0% | 221.7025 | 0 | 221.7025 | 0 | 221.7025 | 30 | 30 | Primary Source: Medina, M; "On the performance of radiant barriers in combination with different attic insulation levels"; Energy and Buildings 33 (2000) 31-40 Other Supporting Sources: http://www.reflectixinc.com/basepage.asp?PageIndex=390; Adjusted for heating penalty and average national load as pwer cool roof calculations
647 | Demonstrate and deploy radiative barrier in attics (above ducts) in existing homes in hot climates | R: Attic Rad. Barrier (Ducts), Hot CZ (E) | 5 | Residential | Building | Total cooling in all existing (pre-2010) homes in hot climates | Energy Savings (%) | 11.6% | 0% | 263.2717 | 0 | 263.2717 | 0 | 263.2717 | 30 | 30 | Primary Source: Medina, M; "On the performance of radiant barriers in combination with different attic insulation levels"; Energy and Buildings 33 (2000) 31-40 Other Supporting Sources: http://www.reflectixinc.com/basepage.asp?PageIndex=390; Adjusted for heating penalty and average national load as pwer cool roof calculations
648 | Demonstrate and deploy cool roofs in existing homes in the hottest climates | R: Cool roofs, hot CZ [E] | 4 | Residential | Building | Total cooling in all existing (pre-2010) homes in hot climates | Energy Savings (%) | 4.5% | 0% | 692.8203 | 0 | 692.8203 | 0 | 692.8203 | 30 | 30 | Page 8 of: http://www.ornl.gov/sci/buildings/2012/B11%20papers/64_Miller.pdf ;NREL measure database, BTP website. Primary Source: Konopacki, S., Akbari, H., Pomerantz, M., Gabersek, S. & Gartland, L. Cooling Energy Savings of Light-Colored Roofs for Residential and Commercial Buildings in 11 U.S. Metropolitan Areas. 117 (1997).
649 | Develop integrated roofing package for all homes in hot climates (with duct benefits) using phase change materials (PCM) for R-75 equivalent | R: R-75 PCM Roof, hot CZ (N) | 2 | Residential | Building | Central cooling in new single-family homes in hottest two climates | Energy Savings (%) | 11.7% | 0% | 1953.7533 | 0 | 1953.7533 | 0 | 1953.7533 | 30 | 30 | Miller, W. & Kosny, J. Next-Generation Roofs and Attics for Homes. ACEEE Summer Study on Energy Efficiency in Buildings 180-195 (2008)
650 | Demonstate, deploy, and increase adoption of dynamic window films in homes in the hottest climates | R: Dynamic Films [hot CZ] (MYP2025)* | 0 | Residential | Building | Total cooling in all homes in hot climates | SHGF, 50% of the time | 0.07 | 0.47 | 444 | 0 | 444 | 0 | 444 | 30 | 30 | R&D Roadmap for Emerging Window and Building Envelope Technologies 2014.
651 | Demonstate, deploy, and increase adoption of dynamic window films in homes | R: Dynamic Films (MYP2025)* | 0 | Residential | Building | Total cooling energy losses through windows due to solar radiation in all homes | SHGF, 50% of the time | 0.07 | 0.47 | 444 | 0 | 444 | 0 | 444 | 30 | 30 | R&D Roadmap for Emerging Window and Building Envelope Technologies 2014.
652 | Demonstate, deploy, and increase adoption of dynamic window films in commercial buildings | C: Dynamic Films (MYP2025)* | 0 | Commercial | Building | Total cooling energy lost through windows due to solar heat gain in all commercial buildings | SHGF, 50% of the time | 0.07 | 0.47 | 0.72 | 0 | 0.72 | 0 | 0.72 | 40 | 40 | R&D Roadmap for Emerging Window and Building Envelope Technologies 2014.
654 | Research, demonstrate, and deploy phase change materials for existing home attics in all climates (cost reduction target) | R: PCM Attics [E]* | 0 | Residential | Building | Attic generated electric cooling in single family homes in hottest 2 climates in existing homes | Energy Savings (%) | 54% | 0% | 0 | 0 | 0 | 0 | 1566 | 30 | 30 | Cost Analysis of Simple PCM-Enhanced Building Envelopes in Southern U.S. Climates Jan Kośny, Nitin Shukla, and Ali Fallahi
655 | Research, demonstrate, and deploy phase change materials for new home attics (cost reduction target) | R: PCM Attics (N)* | 0 | Residential | Building | Attic generated electric cooling in single family homes in hottest 2 climates in new homes | Energy Savings (%) | 54% | 0% | 0 | 0 | 0 | 0 | 1044 | 30 | 30 | Cost Analysis of Simple PCM-Enhanced Building Envelopes in Southern U.S. Climates Jan Kośny, Nitin Shukla, and Ali Fallahi
656 | Research, demonstrate, and deploy phase change materials for new home walls (cost reduction target) | R: PCM Walls (N)* | 0 | Residential | Building | Wall generated electric cooling in single family homes in hottest 2 climates in new homes | Energy Savings (%) | 22% | 0% | 0 | 0 | 0 | 0 | 406 | 30 | 30 | Cost Analysis of Simple PCM-Enhanced Building Envelopes in Southern U.S. Climates Jan Kośny, Nitin Shukla, and Ali Fallahi
657 | Deploy advanced walls in existing residential buildings (EIFS with sealing benefit) | R: EIFS w/ Sealing (E) | 2 | Residential | Building | Total heating and cooling lost through walls in homes built before 2010 | Energy Savings (%) | 68% | 0% | 15600 | 1820 | 15600 | 1820 | 13780 | 30 | 30 | Jan Kośny, Nitin Shukla, and Ali Fallahi
658 | Deploy R-6 insulation to homes when replacing siding | R: R-6 Sheathing [E] | 3 | Residential | Building | Total heating and cooling lost through walls in homes built before 2010 | R-value | 17.1 | 11.1 | 2548 | 0 | 2548 | 0 | 2548 | 30 | 30 | Building Science, research report 0903, LaFrance Primary Source: Straube, J. and Smegal, J.; Building America Special Research Project: High-R Walls Case Study Analysis; Building Science Corporation 2009 (updated 2011)
659 | Deploy R-6 insulation to homes when replacing siding (with sealing benefit) | R: R-6 Sheathing w/ Sealing [E] | 3 | Residential | Building | Total energy loss through walls and infiltration (siding based) in all existing homes | Energy Savings (%) | 50.7% | 0% | 2548 | 0 | 2548 | 0 | 2548 | 30 | 30 | Building Science, research report 0903, LaFrance Primary Source: Straube, J. and Smegal, J.; Building America Special Research Project: High-R Walls Case Study Analysis; Building Science Corporation 2009 (updated 2011)
660 | Move from R-6 to EIFS when replacing siding (no sealing benefit; applies on both scenarios) | R: Sheathing to EIFS Upgrade [E] | 2 | Residential | Building | Total heating and cooling lost through walls in single-family homes built before 2010 | R-value | 36.2 | 17.1 | 15600 | 2548 | 15600 | 2548 | 13052 | 30 | 30 | Building Science, research report 0903, LaFrance Primary Source: Straube, J. and Smegal, J.; Building America Special Research Project: High-R Walls Case Study Analysis; Building Science Corporation 2009 (updated 2011)
661 | Insulate slab edges in existing homes to R-10 (exterior) | R: R-10 Slab Edge (E) | 4 | Residential | Building | Total heating and cooling energy lost through slab foundation in all existing homes | Energy Savings (%) | 85% | 0% | 1437.2222 | 0 | 1437.2222 | 0 | 1437.2222 | 30 | 30 | Kanasas: buildersguide.pdf; slab insulation technology factsheet.pdf Primary Source: "A Builder’s Guide to Residential Foundation Insulation" King, J.; Meyer, G Other Supporting Sources: FEMP Technology Fact Sheet: Slab Insulation", Southface Energy Institute, Oak Ridge National Laboratory
662 | Insulate slab edges in new homes to R-5 (exterior) | R: R-5 Slab Edge (N) | 4 | Residential | Building | Total heating and cooling energy lost through slab foundation in all new homes | Energy Savings (%) | 70% | 0% | 715 | 0 | 715 | 0 | 715 | 30 | 30 | Kanasas: buildersguide.pdf; slab insulation technology factsheet.pdf Primary Source: "A Builder’s Guide to Residential Foundation Insulation" King, J.; Meyer, G Other Supporting Sources: FEMP Technology Fact Sheet: Slab Insulation", Southface Energy Institute, Oak Ridge National Laboratory
667 | Vacuum Insulated Panels (VIPs) in walls in all homes | R: VIP in Walls (+R-24) | 3 | Residential | Building | Total residential heating and cooling lost through walls in all homes | R-value | 35 | 11.1 | 48976 | 0 | 48976 | 0 | 48976 | 30 | 30 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf
668 | Vacuum Insulated Panels (VIPs) in walls in existing commercial buildings | C: VIP in Walls (+R-24) (E) | 3 | Commercial | Building | Total heating and cooling load due to energy loss through walls in all commercial buildings | R-value | 35 | 11.1 | 8.64 | 0 | 8.64 | 0 | 8.64 | 40 | 40 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf
676 | Demonstrate and deploy dual source heat pumps in homes in non-coldest climates, FS | R: Dual Source HP (FS) | 4 | Residential | Heating & Cooling | Non-electric heating, proportion of cooling not in coldest 2 climates | Energy Savings (%) | 79% heating, 15% cooling | 0% | 7560 | 4680 | 7560 | 4680 | 2880 | 15 | 15 | FEMP Technology alert DOE/E-0220; savings and costs relative to furnace and A/C. Ground loop from Navigant 2009 (Ground‐Source Heat Pumps: Overview of Market Status, Barriers to Adoption, and Options for Overcoming Barriers) $3000/ton for residential retrofit. Baseline cost from NREL Retrofit Measures Database. Primary Source: Hadley, D., Collins, T., Parkerk, S., Cornett, G. & Cavedo, F. Energy Savings from Dual-Source Heat Pump Technology Federal Energy Management Program E-0220 (2000)
678 | Research, demonstrate, and deploy advanced liquid desiccant A/C (e.g., DeVAP, DuCool) in commercial buildings in dry climates | C: DEVAP, dry CZ | 1 | Commercial | Cooling | Total cooling in dry climates by all commercial RTUs | Energy Savings (%) | 76.2% | 0% | 19000 | 9300 | 19000 | 9300 | 2.0867 | 15 | 15 | http://www.nrel.gov/features/20100611_ac.html Primary Source: Eric Kozubal, Jason Woods, Jay Burch, Aaron Boranian, and Tim Merrigan. Desiccant Enhanced Evaporative Air-Conditioning (DEVap): Evaluation of a New Concept in Ultra Efficient Air Conditioning http://www.nrel.gov/docs/fy11osti/49722.pdf; NCI Internal DeVAP Report Cost (listed value is not consistent with this source: "Rooftop units using DEVAP design are initially expected to cost ~30% more than competing models." Kozubal. NREL. July 2 2012. http://www.nrel.gov/docs/fy12osti/55740.pdf
679 | Research, demonstrate, and deploy advanced liquid desiccant A/C (e.g., DeVAP, DuCool) in homes in dry climates | R: DEVAP, dry CZ | 1 | Residential | Cooling | Total residential central cooling in dry climates | Energy Savings (%) | 39.5% | 0% | 9235 | 3200 | 9235 | 3200 | 6035 | 17 | 17 | http://www.nrel.gov/features/20100611_ac.html Primary Source: Eric Kozubal, Jason Woods, Jay Burch, Aaron Boranian, and Tim Merrigan. Desiccant Enhanced Evaporative Air-Conditioning (DEVap): Evaluation of a New Concept in Ultra Efficient Air Conditioning http://www.nrel.gov/docs/fy11osti/49722.pdf NREL Residential Efficiency Measures Database. http://www.nrel.gov/ap/retrofits/measures.cfm?gId=2&ctId=16; NCI Internal DeVAP Report Cost (listed value is not consistent with this source: "Rooftop units using DEVAP design are initially expected to cost ~30% more than competing models." Kozubal. NREL. July 2 2012. http://www.nrel.gov/docs/fy12osti/55740.pdf
680 | Engine Driven Heat Pump, commercial buildings | C: Engine Driven HP (FS to gas) | 3 | Commercial | Heating & Cooling | Total commercial electric heating and proportion of cooling in buildings with electric heating | Energy Savings (%) | -24.63% | 0% | 18.8 | 9.4 | 18.8 | 9.4 | 9.4 | 15 | 15 | Discussion with Omar Abdelaziz. Baseline cost from RS Means Assemblies Cost Data, 33rd Edition ($9.4/ft2 for twenty single-zone RTUs, 2 tons each, including ductwork and controls) Primary Source: Omar Abdelaziz. Oak Ridge National Laboratory. 2011. Personal communication RS Means. 2012. Assemblies Cost Data, 33rd Edition
681 | Demonstrate and deploy Energy Recovery Ventilation (ERV) in new commercial buildings | C: Energy Recovery Vent (N) | 4 | Commercial | Building | Total HVAC load in new commercial buildings | Energy Savings (%) | 10% | 0% | 0.17 | 0 | 0.17 | 0 | 0.17 | 20 | 20 | 1) pg. 10-11 of Emerging Energy-Saving HVAC Technologies and Practices for the Building Sector (2009) by Sachs, Lin, Lowenberger. ACEEE. December 2009. 2) pg. 4-33, 34 of Energy Consumption Characteristics of Commercial Building HVAC Systems Volume III: Energy Savings Potential. Roth, Westphalen, dieckmann, Hamilton, Goetzler. TIAX. 2002. 3) p.3 of Energy Recovery Ventilation. FPL Technical Paper. 4) Paper cites incremental cost per unit as $1,150 (pg 11) for a building of 6600 sq.ft., 561 cfm, 8.5 tons RTU (pg 10). Dividing this incremental cost by the building square footage gives an incremental cost of $0.17/sqft of Emerging Energy-Saving HVAC Technologies and Practices for the Building Sector (2009) by Sachs, Lin, Lowenberger. ACEEE. December 2009.
682 | Demonstrate and deploy dual source heat pumps in commercial buildings in non-coldest climates (FS only) | C: Dual source HP (FS) | 4 | Commercial | Heating & Cooling | Non-electric space heating, proportion of cooling, excluding coldest climate | Energy Savings (%) | 79% heating, 15% cooling | 0% | 11.1542 | 9.4 | 11.1542 | 9.4 | 1.7542 | 15 | 15 | FEMP Technology alert DOE/E-0220; savings relative to ASHP. Savings adjusted for gas reference case. Baseline costs for gas and electric based on RS Means Assemblies Cost Data, 33rd Edition ($9.4/ft2 for twenty single-zone RTUs, 2 tons each, including ductwork and controls; $8.65/ft2 for a rooftop electric heat pump, including ductwork and controls, scaled by 75% because 25% of load is met by ground loop) Ground loop cost from ORNL Residential Retrofti Tech potential ($7000/ton for commercial retrofit), assumes precent savings similar to residential. Primary Source: Hadley, D., Collins, T., Parkerk, S., Cornett, G. & Cavedo, F. Energy Savings from Dual-Source Heat Pump Technology Federal Energy Management Program E-0220 (2000)
685 | Deploy ground source heat pumps (GSHP) to all commercial buildings, no fuel switching | C: GSHP | 3 | Commercial | Heating/Cooling/Water | Electric space heating (ASHP, GSHP, screw &other) and proportion of cooling and hot water in building with electric space heating (assumption) | Energy Savings (%) | 64.8% | 0% | 28.5714 | 9.4 | 28.5714 | 9.4 | 19.1714 | 25 | 16 | 1) Cost from pg. 8, energy savings from pg. 22 (assumes similar to the residential sector) of Liu, Xiaobing. Energy and Transportation Science Division, Oak Ridge National Laboratory. Assessment of National Benefits from Retrofitting Existing Single-Family Homes with Ground Source Heat Pump Systems. August 2010. 2) Cost estimate confirmed by data internal to NCI. 3) Baseline cost from RS Means Assemblies Cost Data, 33rd Edition ($9.4/ft2 for twenty single-zone RTUs, 2 tons each, including ductwork and controls) Hughes, P.J. & Shonder, J.A. The Evaluation of a 4000-Home Geothermal Heat Pump Retrofit at Fort Polk , Louisiana: Final Report. Oak Ridge National Laboratory (1998)
686 | Thermoelectric (TE) devices cooling in commercial | C: TE subcooling RTU | 2 | Commercial | Cooling | Total commercial cooling by rooftop AC units (RTUs) | Energy Savings (%) | 9% | 0% | 0 | 0 | 0 | 0 | 0 | 15 | 15 | Akei et al. 2007. “Vapor Compression Circuit and Method Including a Thermoelectric Device.” U.S. Patent No: US 7,240,494 B2. July 10, 2007. Radermacher et al. 2007. “Integrated Alternative and Conventional Cooling Technologies”. ASHRAE Journal. October, 2007. p 28-35. Radermacher, Reinhard. 2011. Personal Communication. June 2011. Radhakrishnan et al. 2009. “Thermoelectric Device Based Refrigerant Subcooling.” U.S. Patent Application Publication. Pub. No: US 2009/0266084 A1. Oct. 29, 2009. Schoenfeld, Jonathan. 2008. “Integration of a Thermoelectric Subcooler into a Carbon Dioxide Transcritical Vapor Compression Cycle Refrigeration System.” University of Maryland. Yang et al. 2008. “Thermoelectric Technology Assessment: Application to Air Conditioning and Refrigeration.” HVAC&R Research. Volume 14, Number 5. September 2008. Primary Source: Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. 289 (2011).
689 | Thermotunneling cooling systems - TARGET | C: Thermotunneling cooling systems* | 0 | Commercial | Cooling | Commercial Cooling (HP and RTU), 100% new and 50% old | Energy Savings (%) | 10% | 0% | 9375 | 7500 | 9375 | 7500 | 1.3393 | 15 | 15 | Brown, DR. et al. “The Prospects of Alternatives to Vapor Compression Technology for Space Cooling and Food Refrigeration Applications.” PNNL-19259. PNNL. March 2010. Prepared for the U.S. DOE under contract DE-AC05-76RL01830. Sachs, H. et al. “Emerging Energy-Saving Technologies and Practices for the Building Sector as of 2004.” October 2004. Report Number A042. ACEEE. Weaver, Stan et al. “Thermotunneling Based Cooling Systems for High Efficiency Buildings.” Final Technical Report. GE Global Research. DE-FC26-04NT42324. Cool Chips PLC, Presentation. “Cool Chips – Technical Overview.” http://www.coolchips.gi/technology/Coolchipstech3Jan06.pdf Cool Chips PLC, Website. http://www.coolchips.gi/about.shtml Primary Source: Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. 289 (2011). (pg. 78, Cost and % energy savings.)
690 | Magnetic Cooling | C: RTU: magnetic cooling | 2 | Commercial | Cooling | All commercial cooling by RTUs and chillers, 100% new and 50% old | Energy Savings (%) | 25% | 0% | 0 | 0 | 0 | 0 | 2.7306 | 17 | 17 | Boeder, A., and Zimm, C., 2006. “Magnetic Refrigeration Technology for High Efficiency Air Conditioning.” Report prepared by Astronautics Corporation of America for the U.S. Department of Energy. December. Chubu Electric, 2006. “Development of Room Temperature Magnetic Refrigeration System - World leading performance a big step forward in achieving practical systems –“. Press Release. November 7. Retrieved July 6, 2011 from http://www.chuden.co.jp/english/corporate/press2006/1107_1.html. Dieckmann, J., Roth, K., and Brodrick, J., 2007. “Emerging Technologies – Magnetic Refrigeration.” ASHRAE Journal. pp. 74-76. August. Goetzler, W., Goffri, S., Jasinski, S., Legett, R., Lisle, H., Marantan, A., Millard, M., Pinault, D., Westphalen, D., and Zogg, R., 2009. “Energy Savings Potential and RD&D Opportunities for Commercial Refrigeration.” Report prepared by Navigant Consulting, Inc. for the U.S. Department of Energy Building Technologies Program. September. Gorman, S., 2009. “As hybrid cars gobble rare metals, shortage looms”. Reuter. Retrieved July 7, 2011 from http://www.reuters.com/article/2009/08/31/us-mining-toyota-idUSTRE57U02B20090831. Gschneider, K. A., and Pecharsky, V. K., 2008. “Thirty years of near room temperature magnetic cooling: Where we are today and future prospects.” International Journal of Refrigeration. Vol. 31, pp. 945-961. January 25. Liu, D., Yue, M., Zhang, J., McQueen, T.M., Lynn, J., Wang, X., Chen, Y., Li, J., Cava, R.J., Liu, X., Altounian, Z., and Huang, Q., 2009. “Origin and tuning of the magnetocaloric effect for the magnetic refrigerant Mn1.1Fe0.9(P0.80Ge0.20).” January. Shen, J., 2011. “Pressure to be lifted on rare earth element pricing, says Information Network “. Digitimes. Retrieved July 7, 2011 from http://www.digitimes.com/news/a20110707PR201.html. Primary Source: Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. 289 (2011).
692 | Decrease cost & deploy indirect, active SWH w/ elec. BU to commercial (no FS) | C: Solar WH indirect active, elec. BU (no FS) | 2 | Commercial | Water Heating | Total energy consumption by all commercial electric storage water heaters | Energy Savings (%) | 61% | 0% | 24710.985 | 0 | 24710.985 | 0 | 24710.985 | 13 | 13 | SWH roadmap; California Center for Sustainable Energy Solar Water Heating Pilot Program 3/2011 Primary Source: Itron, Inc.; "California Center for Sustainable Energy Solar Water Heating Pilot Program" (3/2011) Federal Energy Management Program, "Solar Water Heating with Low-Cost Plastic Systems" (1/2012) Other Supporting Sources: Hudon, Burch "Solar Water Heating Roadmap" (in preperation)
694 | R&D Residential Solar assisted ASHPWH, tech limit (no FS) | R: Solar assisted ASHPWH (no FS) | 1 | Residential | Water Heating | Total electric water heating energy consumption | COP | 5.25 | 1 | 2682 | 552 | 2682 | 552 | 2130 | 13 | 13 | Li. Et.al, "Experimental performance analysis on a direct-expansion solar-assisted heat pump water heater"; Applied Thermal Engineering 27 (2007) 2858–2868 Other Supporting Sources: Guoying, X; Ziaosong, Z; Lei, Y; Shiming, D.; "Performance of a solar-air source heat pump system for water heating on different weather conditions" IEEE (2009)
696 | R&D Commercial Solar assisted ASHPWH, tech limit (no FS) | C: Solar assisted ASHPWH (no FS) | 1 | Commercial | Water Heating | Total energy consumption by all commercial electric storage water heaters | COP | 5.25 | 1 | 0 | 2799 | 0 | 2799 | -2799 | 13 | 13 | Li. Et.al, "Experimental performance analysis on a direct-expansion solar-assisted heat pump water heater"; Applied Thermal Engineering 27 (2007) 2858–2868 Other Supporting Sources: Guoying, X; Ziaosong, Z; Lei, Y; Shiming, D.; "Performance of a solar-air source heat pump system for water heating on different weather conditions" IEEE (2009)
698 | R&D Residential Air-source HPWH, High Performance Target (no FS) | R: ASHPWH, Target (no FS) | 0 | Residential | Water Heating | Total electric water heating energy consumption | COP | 4.8 | 0.9 | 4134 | 0 | 4134 | 0 | 4134 | 13 | 13 | Zhang, J., Wang, R.Z. & Wu, J.Y. System optimization and experimental research on air source heat pump water heater. Applied Thermal Engineering 27, 1029-1035 (2007). Other Supporting Sources: Xu, G., Zhang, X. & Deng, S. A simulation study on the operating performance of a solar–air source heat pump water heater. Applied Thermal Engineering 26, 1257-1265 (2006). measures 698 and 700 are based on a 2007 paper not the TSD. The TSD maximum system efficiency is at EF of 2.35 with an installed cost premium of only $1703 - $569 = 1134; --> The 2007 paper refer to R22 which is no longer in use and depend on an external evaporator. Remove "Tech Limit" from title and use 4.8 as the target EF and target cost as 3* the cost of the TSD
700 | R&D Commercial Air-source HPWH, High Performance Target (no FS) | C: ASHPWH* | 0 | Commercial | Water Heating | Total energy consumption by all commercial electric storage water heaters | COP | 4.8 | 0.9 | 18536 | 2799 | 18536 | 2799 | 15737 | 13 | 13 | Zhang, J., Wang, R.Z. & Wu, J.Y. System optimization and experimental research on air source heat pump water heater. Applied Thermal Engineering 27, 1029-1035 (2007). Other Supporting Sources: Xu, G., Zhang, X. & Deng, S. A simulation study on the operating performance of a solar–air source heat pump water heater. Applied Thermal Engineering 26, 1257-1265 (2006). measures 698 and 700 are based on a 2007 paper not the TSD. The TSD maximum system efficiency is at EF of 2.35 with an installed cost premium of only $1703 - $569 = 1134; --> The 2007 paper refer to R22 which is no longer in use and depend on an external evaporator. Remove "Tech Limit" from title and use 4.8 as the target EF and target cost as 3* the cost of the TSD
702 | R&D Residential engine driven/absorption HPWH, Max Tech (no FS) | R: Gas HPWH, tech limit (no FS) | 1 | Residential | Water Heating | Total gas water heating energy consumption | COP | 1.6577 | 0.59 | 2880 | 1079 | 2880 | 1079 | 1801 | 13 | 13 | HepBasli et. Al, Sanyae Primary Source: Zhang et. al. "Analysis on the heating performance of a gas engine driven air to water heat pump based on a steady-state model", Energy Conversion and Management 46 (2005) 1714–1730 Other Supporting Sources: Hepbasli, A. & Kalinci, Y. A review of heat pump water heating systems. Renewable and Sustainable Energy Reviews 13, 1211-1229 (2009).
704 | R&D Commercial engine driven/absorption HPWH, Max Tech (no FS) | C: Gas HPWH, tech limit (no FS) | 1 | Commercial | Water Heating | Total energy consumption by all commercial gas storage water heaters | COP | 1.6577 | 0.59 | 35580.9524 | 4606 | 35580.9524 | 4606 | 30974.9524 | 13 | 13 | HepBasli et. Al, Sanyae Primary Source: Zhang et. al. "Analysis on the heating performance of a gas engine driven air to water heat pump based on a steady-state model", Energy Conversion and Management 46 (2005) 1714–1730 Other Supporting Sources: Hepbasli, A. & Kalinci, Y. A review of heat pump water heating systems. Renewable and Sustainable Energy Reviews 13, 1211-1229 (2009).
707 | Replace gas water heaters with tankless gas water heaters w/improved HX, direct vent, low NOx (Level 6) | R: Tankless water heater, level 6 (No FS) | 4 | Residential | Water Heating | Total residential storage natural gas water heaters | Energy Factor | 0.85 | 0.59 | 3034 | 1079 | 3034 | 1079 | 1955 | 13 | 13 | DOE TSD (2010), http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr.html
708 | Replace gas water heaters with tankless gas water heaters with direct vent, condensing (Standard Level 7) | R: Tankless Water Heater, Level 7 | 3 | Residential | Water Heating | Total residential storage natural gas water heaters | Energy Factor | 0.92 | 0.59 | 2884 | 1079 | 2884 | 1079 | 1805 | 13 | 13 | DOE TSD (2010), http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr.html Primary Source: U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy (EERE). (2011, March 30). Residential Heating Products Final Rule Analytical Tools. Retrieved from Appliance & Equipment Standards: http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html
718 | A heat pump coupled washer is devised such that a single heat pump is designed to provide heating for the dry cycle and for generating hot water. The device will include an internal heat exchanger and storage component capable of recovering waste heat between the wash and dry cycles. | R: Adv Washer-Dryer Pair | 2 | Residential | Washing & Drying | Total residential clothes washing, drying, and water heating energy consumption | Energy Savings (%) | 40% | 0% | 3000 | 1200 | 3000 | 1200 | 1800 | 12 | 12 | Confidential White Paper and confidential discussion with ORNL CRADA partner Primary Source: Personal communication: Bouza, DOE (1/2012)
719 | Optimize whole-building control system (new software) that controls the operation of multiple systems to minimize costs based on a variety of inputs, such as occupancy, weather, fuel prices, etc. This measure is applicable to systems in large buildings (>100,000 sq.ft.) with poorly performing control systems. It also includes retro-commissioning (adjustment of thermostats, schedules, set points, calibration. It does not include equipment replacement (bad sensors, frozen dampers, etc.)) - will be an extra cost. | C: Bldg Control Opt. (>100,000SF) | 3 | Commercial | HVAC/Lighting | All HVAC and Lighting in commercial buildings >100,000 ft2 | Energy Savings (%) | 20% | 0% | 2.36 | 0 | 2.36 | 0 | 2.36 | 10 | 10 | 1) Savings and costs from pg. 9-91,93,95,139 of TIAX. Energy Impact of Commercial Building Controls and Performance Diagnostics: Market Characterization, Energy Impact of Building Faults and Energy Savings Potential. November 2005. “Overall, it would appear that the first cost of an OWBCS associated with an EMCS would be similar to the cost of a higher-end Whole Building Diagnostics implementation less the cost of additional sensors, i.e. on the order of $100,000.” Adding the costs of the EMCS, which is assumed to be similar to EIS of $1.36/sq.ft (pg. 9-136), and the OWBCS for a 100,000 sq.ft. building gives a cost of $2.36/sq.ft.
720 | Outside air damper automated fault detection and diagnostics (AFDD) | C: Outside-Air Damper AFDD | 3 | Commercial | Heating & Cooling | Total commercial cooling by rooftop AC units (RTUs) | Energy Savings (%) | 10% | 0% | 0.014286 | 0 | 0.014286 | 0 | 0.014286 | 15 | 15 | TIAX. Energy Impact of Commercial Building Controls and Performance Diagnostics?: Market Characterization , Energy Impact of Building Faults and Energy Savings Potential. Construction 413 (2005).
721 | Rooftop Unit (RTU) fault detection and diagnostics | C: RTU AFDD | 2 | Commercial | Heating & Cooling | Total commercial cooling by rooftop AC units (RTUs) | Energy Savings (%) | 9% | 0% | 0.038095 | 0 | 0.038095 | 0 | 0.038095 | 15 | 15 | TIAX. Energy Impact of Commercial Building Controls and Performance Diagnostics: Market Characterization , Energy Impact of Building Faults and Energy Savings Potential. Construction 413 (2005).
722 | Automated whole-building diagnostics (AWBD) | C: Automated whole building diagnostics | 2 | Commercial | HVAC/Lighting | HVAC, lighting, and half of refrigeration | Energy Savings (%) | 12.5% | 0% | 2.04 | 0 | 2.04 | 0 | 2.04 | 20 | 20 | TIAX. Energy Impact of Commercial Building Controls and Performance Diagnostics?: Market Characterization , Energy Impact of Building Faults and Energy Savings Potential. Construction 413 (2005).
723 | Packaged HVAC controls for existing buildings (economizer, multi-speed fan and capacity control, demand control ventilation) | C: Packaged HVAC Controls (Retrofit) | 3 | Commercial | Heating & Cooling | Total commercial HVAC (HP and RTU) in all existing buildings | Energy Savings (%) | 30% | 0% | 1.32 | 0 | 1.32 | 0 | 1.32 | 15 | 15 | W Wang, Y Huang, S Katipamula, MR Brambley. 2011. Advanced Controls for Existing Packaged A/C with gas heating. PNNL 20995. http://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20955.pdf
724 | Improve duct sealing in new small commercial buildings beyond code | C: Duct Sealing beyond code (S) | 3 | Commercial | Building | Commercial heating and cooling in small new buildings (<10,000 ft2) | Energy Savings (%) | 5% | 0% | 0 | 0 | 0 | 0 | 0.33 | 20 | 20 | Aeroseal website: http://www.aeroseal.com/commercial_duct_sealing.html; Modera 2005: Fixing Duct Leaks, ASHRAE Journal; Primary Source: Modera, M Fixing Duct Leaks in Commercial Buildings ASHRAE Journal June 2005 ASHRAE. 2010. Energy Standard for Buildings Except Low-Rise Residential Buildings. ASHRAE 90.1 2010.
725 | Duct sealing in small existing commercial buildings | C: Duct Sealing (E,S) | 3 | Commercial | Building | Commercial heating and cooling in small existing buildings (<10,000 ft2) | Energy Savings (%) | 5% | 0% | 0 | 0 | 0 | 0 | 0.33 | 20 | 20 | Aeroseal website: http://www.aeroseal.com/commercial_duct_sealing.html; Modera 2005: Fixing Duct Leaks, ASHRAE Journal; Primary Source: Modera, M Fixing Duct Leaks in Commercial Buildings ASHRAE Journal June 2005
726 | Duct sealing in large existing commercial buildings | C: Duct Sealing (E,L) | 3 | Commercial | Building | Commercial heating and cooling in large existing buildings (>10,000 ft2) | Energy Savings (%) | 16% | 0% | 0 | 0 | 0 | 0 | 0.33 | 20 | 20 | Aeroseal website: http://www.aeroseal.com/commercial_duct_sealing.html; Modera 2005: Fixing Duct Leaks, ASHRAE Journal; Primary Source: Modera, M Fixing Duct Leaks in Commercial Buildings ASHRAE Journal June 2005. Other Supporting Sources: Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. 289 (2011).
727 | Low lift chiller system | C: Low lift cooling system (N) | 2 | Commercial | Cooling | Total electric cooling and ventilation in new office buildings | Energy Savings (%) | 40% | 0% | 0 | 0 | 0 | 0 | 0.7 | 15 | 15 | Katipamula, S. Pacific Northwest National Laboratory. "Cost-Effective Integration of Efficient Low-Lift Baseload Cooling Equipment: FY08 Final Report", PNNL-19114 (http://www.pnl.gov/main/publications/external/technical_reports/PNNL-19114.pdf)
732 | Tasklighting | C: Tasklighting | 4 | Commercial | Lighting | Total task lighting in all commercial buildings | Energy Savings (%) | 50% | 0% | 0 | 0 | 0 | 0 | 1.96 | 5 | 5 | http://www.etcc-ca.com/images/pge0820.pdf, http://cltc.ucdavis.edu/content/view/673/359/ Primary Source: California Lighting Technology Center. (n.d.). Integrated Office Lighting System (IOLS) . Retrieved from Demonstration: http://cltc.ucdavis.edu/content/view/673/359/ Other Supporting Sources: Heschong Mahone Group, Inc. (2009). Small Office ("Encon" Building) Site Report. Pacific Gas and Electric Company.
738 | Conventional commercial Liquid Desiccant Air Conditioner (LDAC) | C: Conventional LDAC | 4 | Commercial | Cooling | Total cooling in humid climates by all commercial RTUs | Energy Savings (%) | 40% | 0% | 15000 | 12000 | 15000 | 12000 | 0.5 | 15 | 15 | http://www.nrel.gov/features/20100611_ac.html Primary Source: Sachs, H..; Lin, W.; Lowenberger, A.; "Emerging Energy Savings HVACTechnologies and Practices for the Buildings Sector"; ACEEE, 2009 DuCool Case Studies, Advantix Company presentations (publically available, 2011) Other Supporting Sources: Choi-Granade et. Al.; "Unlocking Energy Efficiency in the U.S. Economy"; McKinsey & Company (2009)
739 | Conventional residential Liquid Desiccant Air Conditioner (LDAC) | R: Conventional LDAC | 3 | Residential | Cooling | Total residential central cooling in humid climates | Energy Savings (%) | 40% | 0% | 5780 | 4680 | 5780 | 4680 | 1100 | 17 | 17 | http://www.nrel.gov/features/20100611_ac.html Primary Source: Sachs, H..; Lin, W.; Lowenberger, A.; "Emerging Energy Savings HVACTechnologies and Practices for the Buildings Sector"; ACEEE, 2009 DuCool Case Studies, Advantix Company presentations (publically available, 2011) Other Supporting Sources: Choi-Granade et. Al.; "Unlocking Energy Efficiency in the U.S. Economy"; McKinsey & Company (2009)
741 | Increase roof insulation to R-30 continuous or R-49 cavity for new commercial buildings | C: Highly Insulating Roofs (N) (MYP2025)* | 0 | Commercial | Building | Total heating and cooling loads through attics in new commercial buildings | R-value | 30 | 15 | 1.15 | 0.81667 | 1.15 | 0.81667 | 0.33333 | 40 | 40 | 50% Grocery Store TSD (http://www.nrel.gov/docs/fy09osti/46101.pdf), 50% Large Office TSD (http://www.nrel.gov/docs/fy10osti/49213.pdf), 50% Medium Box Retail (http://www.nrel.gov/docs/fy08osti/42828.pdf) Primary Source: Leech, M. et. al.; "Grocery Store 50% Energy Savings Technical Support Document", National Renewable Energy Laboratory (2009) Leech, M. et. al.; "Technical Support Document: Strategies for 50% Energy Savings in Large Office Buildings", National Renewable Energy Laboratory (2010) Hale E. et. al.; "Technical Support Document: Development of the Advanced Energy Design Guide for Medium Box Retail—50% Energy Savings", National Renewable Energy Laboratory (2008)
742 | Optimize window placement, orientation, and properties for daylighting | C: Optimize Windows for Daylight (N) | 4 | Commercial | Lighting | All fluorescents, new commercial | Energy Savings (%) | 8% | 0% | 0.15 | 0 | 0.15 | 0 | 0.15 | 40 | 40 | Estimate based on experience of NREL Commercial Buildings Group (both energy savings and modeling costs) Primary Source: Hendron, R. Senior Engineer - National Renewable Energy Laboratory Commercial Buildings Group. Personal communications.
743 | Install skylights to enhance daylighting | C: Add skylights (N) | 4 | Commercial | Lighting | All fluorescents, new commercial | Energy Savings (%) | 7.6% | 0% | 1.374 | 0 | 1.374 | 0 | 1.374 | 40 | 40 | Leach, M., Hale, E., Hirsch, A. & Tocellini, P. Grocery Store 50 % Energy Savings Technical Support Document Grocery Store (2009). http://www.nrel.gov/docs/fy09osti/46101.pdf
744 | Require use of controllable power outlets that are turned off during unoccupied hours using timer control | C: Controllable power outlets (N) | 4 | Commercial | MELs | All plug loads in new commercial buildings | Energy Savings (%) | 19% | 0% | 1.75 | 0 | 1.75 | 0 | 1.75 | 20 | 20 | E.T. Hale, D.L. Macumber, N.L. Long, B.T. Griffith, K.S. Benne, S.D. Pless, and P.A. Torcellini. 2008. Technical Support Document: Development of the Advanced Energy Design Guide for Medium Box Retail—50% Energy Savings. (http://www.nrel.gov/docs/fy08osti/42828.pdf)
746 | Add R-10 continuous roof insulation to existing commercial buildings | C: R-10 Roof Insulation (E) | 4 | Commercial | Building | Total heating and cooling loads through attics in all existing commercial buildings | R-value | 24 | 14 | 1082915 | 1023057 | 1082915 | 1023057 | 0.28396 | 40 | 40 | AERG for K-12 Schools (unpublished) Primary Source: NREL. 2011. Advanced Energy Retrofit Guide for K-12 Schools (Draft). EERE Report DOE/GO-102011-3467. Project Lead: Robert Hendron
747 | Install tubular daylighting devices for interior spaces, and add photosensor controls and dimming ballasts | C: TDDs and Controls (E) | 4 | Commercial | Lighting | All fluorescents, existing commercial | Energy Savings (%) | 21% | 0% | 8.5025 | 0 | 8.5025 | 0 | 8.5025 | 40 | 40 | AERG for K-12 Schools (unpublished) Primary Source: NREL. 2011. Advanced Energy Retrofit Guide for K-12 Schools (Draft). EERE Report DOE/GO-102011-3467. Project Lead: Robert Hendron
748 | Use a stack economizer to recover waste heat from flue gases | C: Stack economizer [E] | 4 | Commercial | Heating | Space heating using boiler in all existing commercial buildings | Energy Savings (%) | 5% | 0% | 0.76202 | 0 | 0.76202 | 0 | 0.76202 | 30 | 30 | Energy savings from AERG for Healthcare Facilities (unpublished), cost estimated from Kemco case study (http://www.kemcosystems.com/Case-Studies/Food-Stack.html) Primary Source: NREL. 2011. Advanced Energy Retrofit Guide for Healthcare Facilities (Draft). Project Lead: Robert Hendron Kemco case study. Boiler Stack Economizer - Provides A 3 ½ Month ROI. (http://www.kemcosystems.com/Case-Studies/Food-Stack.html)
753 | Distribution Transformers - Dry, Low efficiency improvement | C: Dry distribution transformers, Low | 4 | Commercial | MELs | All dry distribution transformers (mmBTUs, site) | Energy Savings (%) | 31.91% | 0% | 0 | 0 | 0 | 0 | 0 | 32 | 32 | 0
754 | Distribution Transformers - Dry, Medium-Low efficiency improvement | C: Dry distribution transformers, Medium-Low | 4 | Commercial | MELs | All dry distribution transformers (mmBTUs, site) | Energy Savings (%) | 44.6% | 0% | 0 | 0 | 0 | 0 | 0 | 32 | 32 | 0
756 | Dry type distribution transformers (1- & 3-phase; design levels 6-13b, TSD 2013) efficiency improvement to TSL 5 of 6 total levels (44%-70% or 61% weighted average reduction in losses compared to a baseline transformer established prior to 2013 DT standard; OR ~39% reduction in losses compared to 2013 DT standard (weighted average of 22% over baseline) (TSL 1)) | C: High Eff. Dry Distr. Transformers (TSL 5 of 6) | 4 | Commercial | MELs | All dry distribution transformers (mmBTUs, site) | Energy Savings (%) | 60.95% | 0% | 43756.4972 | 25313.5028 | 43756.4972 | 25313.5028 | 18442.9944 | 32 | 32 | 1) Energy saving were obtained from weighted average of % savings from TSL levels set in 2013 Standards. The Excel file was saved in supporting documents. 2) The weighted average for incremental cost was obtained from 2013 Standard TSD: Table 10.3.1 First Cost of DT by Trial Standard Level and Product Class (2006$/kVA, Baseline and TSL 1 - TSL 6) located on page 10-17. 3) Shipment data to obtain weighted averages for costs and savings is from 2012 NOPR presentation by James Raba during 2013 standard rulemaking. The PPT file was saved in supporting documents.
759 | Reduce/increase temperature set-point 1 F in heating/cooling season | R: Change inside temp 1F | 4 | Residential | HVAC | Total residential heating and cooling in all homes | Energy Savings (%) | 5% | 0% | 0 | 0 | 0 | 0 | 0 | 1 | 1 | EIA Brief (1997): Winter Energy Savings from Lower Thermostat Settings Primary Source: Berry, C; Swenson, A; "Winter Energy Savings from Lower Thermostat Settings", EIA Brief (2000)
760 | Reduce/increase temperature set-point 1 F in heating/cooling season | C: Change inside temp 1F | 4 | Commercial | HVAC | All commercial HVAC energy use | Energy Savings (%) | 5% | 0% | 0 | 0 | 0 | 0 | 0 | 1 | 1 | EIA Brief (1997): Winter Energy Savings from Lower Thermostat Settings Primary Source: Berry, C; Swenson, A; "Winter Energy Savings from Lower Thermostat Settings", EIA Brief (2000)
765 | Advanced RTU (CRADA) | C: RTU (IEER 20) | 3 | Commercial | Cooling | Total commercial cooling by rooftop AC units (RTUs) | IEER | 20 | 11.4 | 2.35 | 0.8525 | 2.35 | 0.8525 | 1.4975 | 15 | 15 | 1) IEER=20 units available from McQuay and Carrier, although not for all capacity ranges. http://www.go.mcquay.com/rebel, http://www.carrierweatherexpert.com/downloads/6-10-tons/catc_10003_brochure_weatherexpert_rtus_hirez_spreads.pdf 2) Cost assumes a typical RTU size of 7.5 tons: from EIA Tech Forecast 2013. Also, DOE funded target: $9-10,000 for highest IEER unit. (Bouza) & pg. 28 of Advanced RTU Campaign. Webinar. Better Buildings. US DOE. June 17, 2013. 3) )
766 | Demonstrate, deploy, and develop tools for designing cost effective high performance commercial buildings | C: 50% building, modeling cost only | 3 | Commercial | All End Uses | All energy consumption in new buildings | Energy Savings (%) | 50% | 0% | 0.14286 | 0 | 0.14286 | 0 | 0.14286 | 40 | 40 | "General Merchandise 50% Energy Savings Technical Support Document" (http://www.nrel.gov/docs/fy09osti/46100.pdf) and "Technical Support Document: Strategies for 50% Energy Savings in Large Office Buildings" (http://www.nrel.gov/docs/fy10osti/49213.pdf)
767 | Thermotunneling cooling systems - TARGET | R: Thermotunneling cooling systems* | 0 | Residential | Cooling | Residential Cooling (HP & RTU), 100% New, 50% Old | Energy Savings (%) | 10% | 0% | 5000 | 4167 | 5000 | 4167 | 833 | 16 | 16 | Brown, DR. et al. “The Prospects of Alternatives to Vapor Compression Technology for Space Cooling and Food Refrigeration Applications.” PNNL-19259. PNNL. March 2010. Prepared for the U.S. DOE under contract DE-AC05-76RL01830. Sachs, H. et al. “Emerging Energy-Saving Technologies and Practices for the Building Sector as of 2004.” October 2004. Report Number A042. ACEEE. Weaver, Stan et al. “Thermotunneling Based Cooling Systems for High Efficiency Buildings.” Final Technical Report. GE Global Research. DE-FC26-04NT42324. Cool Chips PLC, Presentation. “Cool Chips – Technical Overview.” http://www.coolchips.gi/technology/Coolchipstech3Jan06.pdf Cool Chips PLC, Website. http://www.coolchips.gi/about.shtml Primary Source: Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. 289 (2011). (pg. 78, cost and % savings)
768 | Install heat-resistant radiator reflectors between exterior walls and radiators | R: Install radiator reflectors | 4 | Residential | Heating | Total residential cooling by CAC and ASHPs as well as ASHP heating | Energy Savings (%) | 10% | 0% | 0 | 250 | 0 | 250 | 250 | 15 | 15 | Novitherm website, calculation, and cost estimation tools
775 | Close blinds/curtains/drapes/shades during the day when cooling your home especially on south and west-facing windows | R: Close blinds | 3 | Residential | HVAC | Total cooling lost due to solar gain through residential windows that can benefit from attachments (assuming 50% of homes have windows that can benefit from advanced attachments (beyond typical blinds or curtains which may not be properly utilized for greater savings) | Energy Savings (%) | 16% | 0% | 0 | 0 | 0 | 0 | 440 | 1 | 1 | Cho, S.-hwan, Shin, K.-S. & Zaheer-Uddin, M. The Effect of Slat Angle of Windows With Venetian Blinds on Heating and Cooling Loads in South Korea. Energy 20, 1225-1236 (1995)
776 | Close blinds in commercial buildings | C: Close blinds | 3 | Commercial | HVAC | All commercial windows that can benefit from attachments in pre-2010 buildings | Energy Savings (%) | 16% | 0% | 0 | 0 | 0 | 0 | 0.1375 | 10 | 10 | Cho, S.-hwan, Shin, K.-S. & Zaheer-Uddin, M. The Effect of Slat Angle of Windows With Venetian Blinds on Heating and Cooling Loads in South Korea. Energy 20, 1225-1236 (1995)
777 | Develop integrated roofing package for existing homes in hot climates (with duct benefits) using phase change material (PCM) for R-75 equivalent (DOE FOA Target) | R: R-75 PCM Roof, hot CZ [E]* | 2 | Residential | Building | Total central cooling in all existing single-family homes in hottest two climates | Energy Savings (%) | 35% | 0% | 4156.9219 | 0 | 4156.9219 | 0 | 4156.9219 | 30 | 30 | Miller, W. & Kosny, J. Next-Generation Roofs and Attics for Homes. ACEEE Summer Study on Energy Efficiency in Buildings 180-195 (2008); FOA TARGET
782 | Commercial CHP, serving all heating load using a CHP system and displacing some of the electrical end use | C: CHP, EPA (2), 47% heat, 24.6% electricity | 4 | Commercial | Heating | CHP Commercial Buildings | Energy Savings (%) | 71.6% | 55.47% | 0 | 0 | 0 | 0 | 56.5377 | 20 | 20 | EPA Technology Characterization: Microturbines. Prepared for EPA by ICF International. 2008.
785 | Install PVT Collectors on Commercial Roofs to Meet Hot Water Demand and Supply Site Renewable Energy | C: PVT Collectors | 4 | Commercial | Water Heating | Total energy consumption by all commercial storage water heaters | Energy Savings (%) | 79.4% | 0% | 26453.7776 | 0 | 26453.7776 | 0 | 26453.7776 | 13 | 13 | J. Paidipati, L. Frantzis, H. Sawyer, and A. Kurrasch, Rooftop Photovoltaics Market Penetration Scenarios, Navigant Consulting, Inc. Burlington, Mass, 2008 - NREL Report NREL/SR-581-42306; Masters Thesis from U. Michigan (http://deepblue.lib.umich.edu/bitstream/2027.42/83664/3/The_Green_Brewery_Project-updated.pdf) pages 56-60 and attached brochure from manufacturing company.
786 | Create and deploy technology for direct use of local DC renewable supply in DC-powered products | R: Use of DC Renewable Supply | 2 | Residential | Building | Total residential energy consumption in all single-family homes | Energy Savings (%) | 0.884% | 0% | 20000 | 0 | 20000 | 0 | 20000 | 10 | 10 | Garbesi, K., Vossos, V., Sanstad, A., and G. Burch, "Optimizing Energy Savings from Direct DC in US Residential Buildings," LBNL-5193E, 2011.
792 | Low cost solar water heater, gas back up with no fuel switching to replace all gas water heater | R: NREL Solar WH, Gas BU, $1200 | 2 | Residential | Water Heating | Total gas water heating energy consumption | Energy Savings (%) | 32% | 0% | 0 | 0 | 0 | 0 | 1200 | 13 | 13 | Bahman Habibzadeh
793 | Low cost solar water heater, gas BU with no FS to replace all gas water heater | R: NREL Solar WH, Gas BU, $3000 | 2 | Residential | Water Heating | Total gas water heating energy consumption | Energy Savings (%) | 32% | 0% | 0 | 0 | 0 | 0 | 3000 | 13 | 13 | Bahman Habibzadeh
794 | Low cost solar water heater, gas back up with no fuel switching to replace gas storage water heater in all except hottest climate | R: NREL Solar WH, Gas BU, $1200 (Exc. Hot CZ) | 2 | Residential | Water Heating | All residential gas storage water heaters in all except hottest climates | Energy Savings (%) | 32% | 0% | 0 | 0 | 0 | 0 | 1200 | 13 | 13 | Bahman Habibzadeh
795 | Low cost solar water heater, gas BU with no FS to replace gas storage water heater in all except hottest climate | R: NREL Solar WH, Gas BU, $3000 (Exc. Hot CZ) | 2 | Residential | Water Heating | All residential gas storage water heaters in all except hottest climates | Energy Savings (%) | 32% | 0% | 0 | 0 | 0 | 0 | 3000 | 13 | 13 | Bahman Habibzadeh
796 | Demonstrate and deploy NG Adsorption Heat Pump WHs in commercial buildings - TARGET | C: Gas Adsorption HPWH* | 0 | Commercial | Water Heating | Total energy consumption by all commercial gas storage water heaters | Energy Factor | 1.5 | 0.6 | 13250 | 4900 | 13250 | 4900 | 8350 | 13 | 13 | 1) Baseline operation: Estimated based on typical energy factors for residential gas-fired WH (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) 2) Target EF is based on max heating COP listed for SorTech adsorption chiller in heat pump mode (Source: http://www.kpwsolutions.com.au/global/brochures/KPW-Solutions-Cooling-Data-Sheets.pdf) 3) Baseline cost: Average cost (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) 4) Target price assumes a 50% cost reduction from current price (Source: http://www.r718.com/news/view/3745). Current price for a 200,000 Btu/Hr adsorption heat pump (~$26,500) extrapolated based on prices for 25 and 50 kw adsorption chillers in heat pump mode (Equipment Performance Source: http://www.kpwsolutions.com.au/global/brochures/KPW-Solutions-Cooling-Data-Sheets.pdf) (Pricing Sources: http://www.sortech.de/uploads/media/SorTech_Prices_Information_ACS08.pdf http://www.sortech.de/uploads/media/SorTech_Prices_Information_ACS15.pdf) Prices converted from euros to dollars using the 2013 annual average conversion rate of 1.27 (Source: http://www.irs.gov/Individuals/International-Taxpayers/Yearly-Average-Currency-Exchange-Rates)
797 | Engine Driven Heat Pump, residential buildings - TARGET | R: Engine Driven HP (FS to gas)* | 0 | Residential | Heating & Cooling | All electric heating, proportion of cooling in homes with electric heating | Energy Factor | 1.295 | 2.8949 | 9000 | 3075 | 9000 | 3075 | 5925 | 15 | 15 | 1) Efficient unit performance: Heating primary EF of 1.4; cooling primary EF of 1.1. Total Primary EF based on 65-35 average of heating and cooling primary EF, average EF can be adjusted for specific building types by weighting based on relative heating /cooling loads (65-35 split of heating and cooling energy consumption based on average residential building primary energy use for space heating and cooling in Buildings Energy Data Book). Heating and cooling primary EF based on typical COPs for Commercial Gas-Fired Engine-Driven Rooftop Air Conditioners (Source: EIA - Technology Forecast Updates – Residential and Commercial Building Technologies, September 2013) 2) Base unit performance: 0.75 heating primary EF; 1.2 cooling primary EF. Total Primary EF based on 65-35 average of heating and cooling primary EF, average EF can be adjusted for specific building types by weighting based on relative heating /cooling loads (65-35 split of heating and cooling energy consumption based on average residential building primary energy use for space heating and cooling in Buildings Energy Data Book). Heating: 8 HSPF (Source: EIA - Technology Forecast Updates – Residential and Commercial Building Technologies, September 2013), Converted to 2.34 COP (via COP = 0.293*HSPF), Converted to Primary EF assuming a site-to-source conversion factor of 3.1 (Source: Buildings Energy Data Book). Cooling: converted 14 SEER to roughly 3.7 COP, converted to 1.2 primary EF. 3) Standard unit average cost for a residential air source heat pump. (EIA - Technology Forecast Updates – Residential and Commercial Building Technologies, September 2013) 4) Efficient unit cost for Commercial Gas-Fired Engine-Driven Rooftop Air Conditioners (Source: EIA - Technology Forecast Updates – Residential and Commercial Building Technologies, September 2013)
802 | Research and demonstrate R-10 windows in homes (DOE Roadmap 2025 Cost Target) | R: R-10 Windows*(2025, $6/SF) | 0 | Residential | Building | Total heating and cooling lost through windows due to conduction in all homes | R-value | 10 | 1.8612 | 1332 | 0 | 1332 | 0 | 1332 | 30 | 30 | Cost target: Windows Roadmap Goals provided by Karma. Southwall, Alpeninc, PNNL Lost Opportunities Primary Source: 6. Apte, J. & Arasteh, D. Window-Related Energy Consumption in the US Residential and Commercial Building Stock. Buildings 1-38 (Berkeley, CA, 2006). Personal communication: various window experts Other Supporting Sources: Arasteh, Dariush; Selkowitz, Steve; Apte, Josh; LaFrance, Marc. Energy Impacts of Today’ s Window Stock ; FOA TARGET
803 | Research and demonstrate R-10 windows in commercial buildings (DOE Roadmap 2025 Cost Target) | C: R-10 Windows* (2025, $6/SF) | 0 | Commercial | Building | Total window conductive loss in all commercial buildings | R-value | 10 | 1.6129 | 2.16 | 0 | 2.16 | 0 | 2.16 | 40 | 40 | Cost target: Windows Roadmap Goals provided by Karma. Southwall, Alpeninc, PNNL Lost Opportunities Primary Source: 6. Apte, J. & Arasteh, D. Window-Related Energy Consumption in the US Residential and Commercial Building Stock. Buildings 1-38 (Berkeley, CA, 2006). Personal communication: various window experts Other Supporting Sources: Arasteh, Dariush; Selkowitz, Steve; Apte, Josh; LaFrance, Marc. Energy Impacts of Today’ s Window Stock ; FOA TARGET
804 | Develop and Deploy Cold Climate Heat Pumps - Target based on UTRC project | C: Cold Climate HP* | 0 | Commercial | Heating/Cooling/Water | Total commercial electric heating and proportion of cooling in buildings with electric heating in 2 coldest climates | Energy Savings (%) | 51.79% | 0% | 0 | 0 | 0 | 0 | 0.095 | 15 | 15 | Program Goal
805 | Develop and Deploy Low-Cost Gas Heat Pump for Building Space Heating (DOE FOA Target) | R: Low-Cost Gas HP* | 0 | Residential | Building | Total residential heating energy use by natural gas furnaces in all homes. | Energy Savings (%) | 30% | 0% | 0 | 0 | 0 | 0 | 1000 | 15 | 15 | Program goal
806 | Reduce air infiltration due to windows with better flashing at EOL or New Construction | R: Improved Window Flashing | 4 | Residential | Building | Total heating and cooling lost through infiltration in all homes | Energy Savings (%) | 7% | 0% | 296 | 0 | 296 | 0 | 296 | 30 | 30 | Window Area: BED Table 2.1.15; Energy Savings: BED Table 2.1.15; ASHRAE 2007, ORNL Study "An Exploration of Wall Retrofit Best Practices". Cost: Need a source!
807 | Vacuum Insulated Panels (VIPs) in walls in new homes | R: VIP in Walls (N) | 3 | Residential | Building | Total heating and cooling lost through walls in new single/multi/mobile homes | R-value | 35 | 11.1 | 48976 | 3364 | 48976 | 3364 | 45612 | 30 | 30 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf
808 | Vacuum Insulated Panels (VIPs) in walls in new commercial buildings | C: VIP in Walls (N) | 3 | Commercial | Building | Total heating and cooling energy lost through wall in all new commercial buildings | R-value | 35 | 17 | 8.64 | 0.5886 | 8.64 | 0.5886 | 8.0514 | 40 | 40 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf
812 | Retrofit using aerogel in walls in pre-2010 single-family homes (interior insulation (R-4)). TARGET- cost | R: Aerogel in walls, interior R-4 [E]* | 0 | Residential | Building | Total heating and cooling lost through walls in single-family homes built before 2010 | R-value | 15.1 | 11.1 | 5096.565 | 0 | 5096.565 | 0 | 5096.565 | 30 | 30 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf
813 | Aerogel in walls in all commercial buildings, interior insulation (R-4). TARGET - cost | C: Aerogel in walls, int R-4* | 0 | Commercial | Building | Total heating and cooling load due to energy loss through walls in all commercial buildings | R-value | 15.1 | 11.1 | 0.8991 | 0 | 0.8991 | 0 | 0.8991 | 40 | 40 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf
814 | Advanced Rooftop Unit (RTU) (DOE CRADA TARGET) | C: Adv. RTU (IEER 22)* | 0 | Commercial | Cooling | Total commercial cooling by rooftop AC units (RTUs) | IEER | 22 | 11.2 | 2.3 | 1.3333 | 2.3 | 1.3333 | 0.96667 | 15 | 15 | CRADA with BTP, Primary Source: Personal communication: Bouza
815 | Retrofit walls with blown-in aerogel in pre-2010 homes. TARGET (R-value & cost) | R: Blown-in Aerogel, Walls* [E] | 0 | Residential | Building | Total heating and cooling lost through walls in homes built before 2010 | R-value | 31.1 | 11.1 | 39793 | 0 | 39793 | 0 | 39793 | 30 | 30 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf
816 | Research, develop and demonstrate lighting energy savings of improved daylighting over 50 foot floor plate in commercial buildings | C: Perimeter Zone Daylighting (MYP2020)* | 0 | Commercial | Lighting | All commercial fluorescents in a perimeter zone | Energy Savings (%) | 35% | 0% | 195 | 0 | 195 | 0 | 195 | 20 | 20 | Source: Karma Sawyer: Windows Roadmap Goals (May 30, 2013)
817 | Replace metal halide parking lot lighting with LEDs, and install timer and motion sensor controls | O: Parking Lot LEDs + Cntrls | 4 | Outdoor | Lighting | All metal halide lighting in parking lots | lumens/watt | 112.88 | 60 | 573.46 | 240 | 573.46 | 240 | 90.4 | 11 | 4 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
818 | LEDs for residential general use lighting in place of incandescents | R: LEDs to replace Incandescents | 4 | Residential | Lighting | Total incandescent (MSB, reflectors, and other) lighting energy consumption all homes | lumens/watt | 73 | 13 | 25.34 | 1.2 | 25.34 | 1.2 | -24.36 | 43 | 2 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization 4) Daily operating hours from the PNNL: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/2012_residential-lighting-study.pdf
819 | Vacuum Insulated Panels (VIPs) in walls in existing commercial buildings | C: VIP in Walls [E]* | 0 | Commercial | Building | Total heating and cooling load due to energy loss through walls in all commercial buildings | R-value | 35 | 11.1 | 4.32 | 0 | 4.32 | 0 | 4.32 | 40 | 40 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf
820 | Vacuum Insulated Panels (VIPs) in walls in new commercial buildings | C: VIP in Walls [N]* | 0 | Commercial | Building | Total heating and cooling energy lost through wall in all new commercial buildings | R-value | 35 | 17 | 4.32 | 0.5886 | 4.32 | 0.5886 | 3.7314 | 40 | 40 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf
824 | Replace all outdoor lighting with LEDs | O: LED, General Illumination | 4 | Outdoor | Lighting | All lighting, Outdoor | lumens/watt | 83 | 63 | 477.56 | 240 | 477.56 | 240 | 62.46 | 15 | 8 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
825 | Replace all outdoor lighting with LEDs - TARGET | O: LEDs, SSL Program Goal (2020)* | 0 | Outdoor | Lighting | All lighting, Outdoor | lumens/watt | 210 | 63 | 170 | 240 | 170 | 240 | -420 | 30 | 8 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
826 | Replace all commercial, residential and industrial downlighting (incandescent, screw base CFL or pin base CFL) with LEDs | C/R/I: Replace Downlight w/ LEDs | 4 | Commercial/Residential/Industrial | Lighting | All downlighting in all commercial, residential and industrial buildings | lumens/watt | 64 | 20 | 41.82 | 3.6 | 41.82 | 3.6 | -41.58 | 46 | 3 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
827 | Replace all MR16s with LEDs | R/C: Replace MR16s w/ LEDs | 4 | Residential and Commercial | Lighting | All commercial and residential MR16s | lumens/watt | 62 | 17 | 34.05 | 2.25 | 34.05 | 2.25 | 13.24 | 9 | 1 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
828 | Replace metal halide streetlighting with LEDs | O: LED Streetlights | 4 | Outdoor | Lighting | All metal halide street lighting | lumens/watt | 83 | 60 | 716.19 | 250 | 716.19 | 250 | 101.61 | 11 | 4 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
829 | Replace metal halide streetlighting with LEDs with controls | O: LED Streetlights + Controls | 4 | Outdoor | Lighting | All metal halide street lighting | lumens/watt | 106 | 60 | 812.19 | 250 | 812.19 | 250 | 197.61 | 11 | 4 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
830 | Replace metal halide parking garage lights with LEDs | O: Parking Garage LEDs | 4 | Outdoor | Lighting | All metal halide lighting in parking garages | lumens/watt | 78 | 60 | 238.73 | 97.5 | 238.73 | 97.5 | 19.7 | 8 | 3 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
831 | Replace metal halide parking garage lights with LEDs with controls | O: Parking Garage LEDs + Cntrls | 4 | Outdoor | Lighting | All metal halide lighting in parking garages | lumens/watt | 106 | 60 | 334.73 | 97.5 | 334.73 | 97.5 | 115.7 | 8 | 3 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
832 | LEDs to replace high bay | C: High Bay LEDs | 4 | Commercial | Lighting | All high bay lighting in all commercial and industrial buildings | lumens/watt | 80 | 65 | 1494.15 | 225 | 1494.15 | 225 | 1146.15 | 8 | 3 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization
833 | OLED Tasklighting target for 2020 to partially (50%) replace linear fluorescent ceiling lighting in new construction | C: OLED Tasklighting* (N) | 0 | Commercial | Lighting | All fluorescents, new commercial | Energy Savings (%) | 25% | 0% | 60 | 42 | 60 | 42 | 18 | 5 | 5 | Cost and efficiency data is from Internal Solid State Program White Papers: 1) Cost Competitiveness of Solid State Lighting. (2013,not published). 2) Energy Savings Potential of OLEDs in Office Buildings (July 2013). OLED cost source: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_manuf-roadmap_sept2013.pdf Flourescent lamp and ballast cost: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_mypp2013_web.pdf Google search for cost of linear fluorescent fixtures.
834 | Wireless temperature sensors | C: Wireless Temperature Sensors | 4 | Commercial | HVAC | Total heating and cooling in all commercial buildings | Energy Savings (%) | 10% | 0% | 0.077778 | 0 | 0.077778 | 0 | 0.077778 | 10 | 10 | FEMP Technology Installation Review: Wireless Temperature Sensors for Improved HVAC Control (DOE/EE-0319); Navigant Report: Energy Savings Potential and RD&D Opportunities for Residential HVAC Technologies, September 2012.
843 | Deploy advanced walls using EIFS with VIPs in all commercial buildings. DOE DE-EE0003915 project lead by Dow Corning, Dryvit, Inc., and Fraunhofer CSE. | C: EIFS+VIP R-30 Walls | 3 | Commercial | Building | Total heating and cooling load due to energy loss through walls in all commercial buildings | R-value | 31.8 | 11.1 | 18.9 | 10.8 | 18.9 | 10.8 | 8.1 | 40 | 40 | Data obtained from RFI Measure Addition Form submitted by Lawrence Carbary from Dow Corning in 2013. He specified that the data is obtianed from the PI of this project (DOE DE-EE0003915) funded by DOE ($1,241,120 USD/3years from saved report).
844 | Research, demonstrate and deploy Sandia rotating heat exchangers in residential refrigerators and freezers | R: Rotary Cooler in Refrigerators and Freezers* | 0 | Residential | Refrigeration | All residential refrigerators and freezers | Energy Savings (%) | 10% | 0% | 22.4971 | 0 | 22.4971 | 0 | 22.4971 | 17 | 17 | Market Assessment and Commercialization Strategy for the Radia Sandia Cooler. 2014. BTO. DOE. Not published yet.
846 | Research, demonstrate and deploy Sandia rotating heat exchangers in residential central air conditioners, room air conditioners, and ASHPs. | R: Rotary Cooler in CAC, room ACs, and HPs* | 0 | Residential | Heating & Cooling | Total residential CAC, room AC, and electric heat pump heating and cooling | Energy Savings (%) | 10% | 0% | 57.4655 | 0 | 57.4655 | 0 | 57.4655 | 20 | 20 | Market Assessment and Commercialization Strategy for the Radia Sandia Cooler. 2014. BTO. DOE. Not published yet.
848 | Research and demonstrate R-10 windows in homes at a 2025 DOE Roadmap target premium cost (2014) | R: R-10 Windows (MYP2020, $10/SF)* | 0 | Residential | Building | Total heating and cooling lost through windows due to conduction in all homes | R-value | 10 | 1.61 | 4440 | 2220 | 4440 | 2220 | 2220 | 30 | 30 | Cost Targets from Windows and Envelope Roadmap Report 2014
849 | Research and demonstrate R-7 windows in commercial buildings a 2025 DOE Roadmap target premium cost (2014) | C: R-7 Windows (MYP2020, $8/SF)* | 0 | Commercial | Building | Total window conductive loss in all commercial buildings | R-value | 7 | 1.86 | 6.48 | 3.6 | 6.48 | 3.6 | 2.88 | 40 | 40 | Cost Targets from Windows and Envelope Roadmap Report 2014
850 | Increase adoption of low-e interior panel storm windows on existing 1-pane metal framed windows in homes | R: Interior Low-e Panels [E] | 4 | Residential | Building | Total energy losses due to conduction and radiation for single pane glass windows for all homes built before 2010 | Energy Savings (%) | 54.63% | 0% | 1800 | 0 | 1800 | 0 | 1800 | 30 | 30 | Kohler, C Letter report for low-e storm window retrofits, 2006
851 | Increase adoption of low-e interior panel storm windows on existing 1-pane metal framed windows in commercial buildings | C: Interior Low-e Panels [E] | 4 | Commercial | Building | Total commercial radiative and conductive window load for pre-2010 buildings with single pane windows (includes solar heat gain loss during cooling season as well as solar heat gain benefit during heating season) | Energy Savings (%) | 54.63% | 0% | 3.6 | 0 | 3.6 | 0 | 3.6 | 40 | 40 | Kohler, C Letter report for low-e storm window retrofits, 2006
870 | Develop and deploy a controller pack to RTU accomponied by a gas furnace for demand controlled ventilation and upgrade to a digital economizer with differential high limit control. In the process reduce excess baseline ventilation with acceptance testing on setup. | C: RTU Control Retrofit (DCV+Economizer) | 3 | Commercial | Heating & Cooling | Total Furnace gas heating and electric RTU AC in all commercial buildings | Energy Savings (%) | 20% | 0% | 1 | 0 | 1 | 0 | 1 | 15 | 15 | 1) Costs and energy savings obtained from pg. 60-61, RTU Premium Ventilation: Proof of Concept Field Test. May 2012. Bonneville Power Administration. http://www.bpa.gov/energy/n/emerging_technology/pdf/38702_RTU_Premium_Ventilation_Proof_Of_Concept_FINAL.pdf a. Baseline: Energy intensity of NEMSConsFcast3!$L$3792/EquipStockTable3!$L$3792 = 0.039 mmBTU/sq.ft per year. b. Savings in electricity of 0.00117 mmBTU/sq.ft. per year; and 0.006 mmBTU/sq.ft. in gas. 2) Other supporting sources confirming the data: Tables ES 1, 2, 3, etc. PNNL 2011. Wang, Katipamula. Huang. Brambley. Enegy Savings and Economics of Advanced Control Strategies for Packaged Air-Conditioning Units with Gas Heat.
871 | Develop and deploy a controller pack to RTU accomponied by a gas furnace for demand controlled ventilation and upgrade to a digital economizer with differential high limit control. In the process reduce excess baseline ventilation with acceptance testing on setup. Add fan control, either VSD or fan cycling to reduce fan energy use. | C: RTU Control Retrofit (DCV+Econ+VSD) | 3 | Commercial | Heating & Cooling | Total Furnace gas heating and electric RTU AC in all commercial buildings | Energy Savings (%) | 24% | 0% | 3.04 | 0 | 3.04 | 0 | 3.04 | 15 | 15 | 1) Costs and energy savings obtained from pg. 60-61, RTU Premium Ventilation: Proof of Concept Field Test. May 2012. Bonneville Power Administration. http://www.bpa.gov/energy/n/emerging_technology/pdf/38702_RTU_Premium_Ventilation_Proof_Of_Concept_FINAL.pdf a. Baseline: Energy intensity of NEMSConsFcast3!$L$3792/EquipStockTable3!$L$3792 = 0.039 mmBTU/sq.ft per year. b. Savings in electricity of 0.00317 mmBTU/sq.ft. per year; and 0.00562 mmBTU/sq.ft. in gas. =(NEMSConsFcast3!$L$3806/EquipStockTable3!$L$3806-0.00562)+(NEMSConsFcast3!$F$3807/EquipStockTable3!$F$3807-0.00317) 2) Other supporting sources confirming the data: Tables ES 1, 2, 3, etc. PNNL 2011. Wang, Katipamula. Huang. Brambley. Enegy Savings and Economics of Advanced Control Strategies for Packaged Air-Conditioning Units with Gas Heat.
872 | Develop and deploy a controller pack to RTU accomponied by a gas furnace for demand controlled ventilation and upgrade to a digital economizer with differential high limit control. In the process reduce excess baseline ventilation with acceptance testing on setup. Add fan control, either VSD or fan cycling to reduce fan energy use, as well as robust optimum start, ventilation lockout during warmup, occupancy sensor standby, and temperature setpoint limits. | C: RTU Control Retrofit (DCV+Econ+VSD+prem) | 3 | Commercial | Heating & Cooling | Total Furnace gas heating and electric RTU AC in all commercial buildings | Energy Savings (%) | 34% | 0% | 2.21 | 0 | 2.21 | 0 | 2.21 | 15 | 15 | 1) Costs and energy savings obtained from pg. 60-61, RTU Premium Ventilation: Proof of Concept Field Test. May 2012. Bonneville Power Administration. http://www.bpa.gov/energy/n/emerging_technology/pdf/38702_RTU_Premium_Ventilation_Proof_Of_Concept_FINAL.pdf a. Baseline: Energy intensity of NEMSConsFcast3!$L$3792/EquipStockTable3!$L$3792 = 0.039 mmBTU/sq.ft per year. b. Savings in electricity of 0.00355 mmBTU/sq.ft. per year; and 0.00919 mmBTU/sq.ft. in gas. =(NEMSConsFcast3!$L$3806/EquipStockTable3!$L$3806-0.00919)+(NEMSConsFcast3!$F$3807/EquipStockTable3!$F$3807-0.00355) 2) Other supporting sources confirming the data: Tables ES 1, 2, 3, etc. PNNL 2011. Wang, Katipamula. Huang. Brambley. Enegy Savings and Economics of Advanced Control Strategies for Packaged Air-Conditioning Units with Gas Heat.
876 | Goal for 2030: deploy a suite of energy saving technologies to accomplish the Building America goal of 30% energy savings in existing homes | R: Building America, 2030 (E)* | 0 | Residential | All End Uses | Total Energy Consumption for all single and multi-family homes built pre-2010 | Energy Savings (%) | 30% | 0% | 1628.8415 | 0 | 1628.8415 | 0 | 1628.8415 | 30 | 30 | 0
877 | Goal for 2030: deploy a suite of energy saving technologies to accomplish the Building America goal of 50% energy savings in new homes | R: Building America, 2030 (N)* | 0 | Residential | All End Uses | Total Energy Consumption for all single and multi-family homes built after 2010 | Energy Savings (%) | 50% | 0% | 2615.6318 | 0 | 2615.6318 | 0 | 2615.6318 | 30 | 30 | 0
878 | Improving Buildings Energy Performance by Integrating EnergyPlus Energy Modeling in the Design Stage, New Buildings | C: EnergyPlus Integration in Building Design (N) | 3 | Commercial | All End Uses | Total HVAC load in new commercial buildings | Energy Savings (%) | 20% | 0% | 0 | 0 | 0 | 0 | 0.32984 | 40 | 40 | Source: Amir Roth and AIA data 1) No good incremental cost data available, costs were estimated; 2) The energy savings estimates are for architectural firms that are participating in the AIA 2030 Commitment. These are generally large architecture firms that we consider to be aggressive in pursuing energy efficiency (i.e. data is not from a random or representative sample) 3) The energy savings estimate is for the marginal energy savings improvement of simulation/integrative design measures on building designs that already meet “beyond-code prescriptive” performance levels 4) Modeling improves all areas of building consumption, although currently savings were only applied to HVAC because that's the largest active component and because we don't have good data at this point to partition the savings at a finer granularity.
879 | Improving Buildings Energy Performance by Integrating EnergyPlus Energy Modeling in the Design Stage, Existing Buildings | C: EnergyPlus Integration in Building Retrofit (E) | 3 | Commercial | All End Uses | Total HVAC load in existing commercial buildings | Energy Savings (%) | 10% | 0% | 0 | 0 | 0 | 0 | 0.32984 | 40 | 40 | Source: Amir Roth 1) This measure is based on #878, but due to retrofit applications was estimated to be half the benefit of new construction. 2) Modeling improves all areas of building consumption, although currently savings were only applied to HVAC because that's the largest active component and because we don't have good data at this point to partition the savings at a finer granularity.
880 | Deploy a suite of energy saving technologies to accomplish the Better Buildings Challenge goal of 20% energy savings in new buildings | C: Better Buildings Challenge (N)* | 0 | Commercial | All End Uses | All energy consumption in new buildings | Energy Savings (%) | 20% | 0% | 2.2409 | 0 | 2.2409 | 0 | 2.2409 | 40 | 40 | 0
881 | Deploy a suite of energy saving technologies to accomplish the Better Buildings Challenge goal of 20% energy savings in Existing buildings | C: Better Buildings Challenge (E)* | 0 | Commercial | All End Uses | All energy consumption in Existing buildings | Energy Savings (%) | 20% | 0% | 2.2409 | 0 | 2.2409 | 0 | 2.2409 | 40 | 40 | 0
882 | Integrating "smart controls" into residential WH systems giving them the capability to learn and adapt to building WH usage patterns, raising or lowering the temp accordingly, and activating re-circulation loops as needed. Smart WH controls can also incorporate FDD capabilities, intuitive interfaces, adaptive algorithms, and integrate seamlessly with other smart building systems. This system is intended to replace the baseline residential gas/oil-fired and electric WH without a smart control system or programmable thermostat. | R: WH Smart Controls* | 0 | Residential | Water Heating | Total residential storage electric and natural gas water heaters | Energy Savings (%) | 15% | 0% | 370 | 0 | 370 | 0 | 370 | 13 | 13 | DOE WH R&D Roadmap Initiative "Expand smart controls for water heating and integrate WH into smart building control systems" 1) % savings: target, NREL has developed a predictive control system for electric heat pump water heaters and gas fired WH. Simulations estimate this technology can reduce energy consumption by up to 20% for a HPWH, therefore we are using 15% energy savings as a target for this technology when applied to all WH (source: http://techportal.eere.energy.gov/technology.do/techID=1181) 2) Cost: target, assumed same as measure 122, "Demonstrate and deploy predictive control thermostats in all homes" ($250 per thermostat plus $120 for NEST installation). Assuming no smart control system or programmable thermostat for a baseline cost. 3) Lifetime of 13 years: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment
883 | Integrating "smart controls" into commercial WH systems giving them the capability to learn and adapt to building WH usage patterns, raising or lowering the temp accordingly, and activating re-circulation loops as needed. Smart WH controls can also incorporate FDD capabilities, intuitive interfaces, adaptive algorithms, and integrate seamlessly with other smart building systems. This system is intended to replace the baseline commercial gas/oil-fired and electric WH without a smart control system or programmable thermostat. | C: WH Smart Controls* | 0 | Commercial | Water Heating | Total energy consumption by all commercial storage water heaters | Energy Savings (%) | 15% | 0% | 2800 | 0 | 2800 | 0 | 2800 | 13 | 13 | 1) % savings: NREL has developed a predictive control system for electric heat pump water heaters and gas fired WH. Simulations estimate this technology can reduce energy consumption by up to 20% for a HPWH, therefore we are using 15% energy savings as a target for this technology when applied to all WH (source: http://techportal.eere.energy.gov/technology.do/techID=1181) 2) Costs: Assuming $250 per thermostat and $300 for control system. Based on measure 122, "Demonstrate and deploy predictive control thermostats in all homes" 3) Lifetime: Assumes smart control system has no impact on WH life. Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013
884 | Residential absorption cycle heat pumps (including ammonia-water and LiBr systems) replacing gas-fired storage water heaters. | R: Gas-fired Absorption HPWH* | 0 | Residential | Water Heating | Total residential storage natural gas water heaters | Energy Factor | 1.5 | 0.59 | 1800 | 1116 | 1800 | 1116 | 684 | 13 | 13 | 1) % Savings: Standard unit: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment; Efficient unit with EF of 1.5 is a target EF for manufacturers, based on ammonia-water system (Source: M. Garrabrant, Stone Mountain Technologies Inc, Development & Validation of a Gas-Fired Residential Heat Pump Water Heater, January 2013, Report DE-EE0003985) 2) Cost of standard unit: Total installed cost is $1027 ($2008) (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses). Cost adjusted from $2008 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl). 3) Cost of efficient unit: target installed cost for 2030, based on ammonia-water absorption system (Source: M. Garrabrant, Stone Mountain Technologies Inc, Development & Validation of a Gas-Fired Residential Heat Pump Water Heater, January 2013, Report DE-EE0003985, http://www.osti.gov/scitech/servlets/purl/1060285 http://techportal.eere.energy.gov/technology.do/techID=1181)
885 | Commercial absorption cycle heat pumps (including ammonia-water and LiBr systems) replacing gas-fired storage water heaters. Assume no impact on space heating and cooling of this measure. | C: Gas-fired Absorption HPWH* | 0 | Commercial | Water Heating | Total energy consumption by all commercial gas storage water heaters | Energy Factor | 1.5 | 0.6 | 7900 | 5430 | 7900 | 5430 | 2470 | 13 | 13 | 1) % savings: Assuming roughly the same EF as a residential gas-fired storage WH for standard unit (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment); for efficient unit, EF of 1.5 is a target EF for manufacturers, based on ammonia-water system (Source: M. Garrabrant, Stone Mountain Technologies Inc, Development & Validation of a Gas-Fired Residential Heat Pump Water Heater, January 2013, Report DE-EE0003985). Standard unit performance: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment. 2) Cost of standard unit: Average installed cost for a 200kBtu/Hr gas storage WH is $5,430 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) 3) Cost of efficient unit: target installed cost for 2030 is $7,900, based on incremental cost ratio for residential units of 1.6 times the cost of a baseline unit - See "Residential gas-fired absorption HPWH" measure
886 | Thermally driven heat pump water heater which is targeted to replace residential gas-fired storage WH (typical capacity of 40 gallons and EF of 0.59). Not analyzing benefits of space heating or cooling. Assume no impact on space heating and cooling of this measure. | R: Non-sorption Gas-fired HPWH* | 0 | Residential | Water Heating | Total residential storage natural gas water heaters | Energy Factor | 1.5 | 0.59 | 2630 | 1116 | 2630 | 1116 | 1514 | 13 | 13 | 1) % savings: 1.5 EF; target COP of 2.2, based on ThermoLift Vuilleumier cycle heat pump (Source: Comparative Analysis of Current Thermally-Driven Refrigeration Devices, ThermoLift, Inc.) Converted to 1.5 using a 0.698 conversion factor which accounts for differences between lab rating and typical field performance (Source: Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007)) 2) Costs: This is a target installed cost, based on the fact that ThermoLift aims to design a product that is cost competitive with state-of-the-art HPWH (Source: Comparative Analysis of Current Thermally-Driven Refrigeration Devices, ThermoLift, Inc.)
887 | Thermally driven heat pump water heater, targeting to replace commercial gas-fired storage water heaters with 200kBtu/hr capacity, and EF of ~0.6. Not analyzing benefits of space heating or cooling. Assume no impact on space heating and cooling of this measure. | C: Non-sorption Gas-fired HPWH* | 0 | Commercial | Water Heating | Total energy consumption by all commercial gas storage water heaters | Energy Factor | 1.5 | 0.6 | 12760.5 | 5430 | 12760.5 | 5430 | 7330.5 | 13 | 13 | 1) % savings: Assuming roughly the same EF as a residential gas-fired storage WH for standard unit (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment); for efficient unit, 2.2 is a target COP, based on ThermoLift Vuilleumier cycle heat pump (Source: Comparative Analysis of Current Thermally-Driven Refrigeration Devices, ThermoLift, Inc.) Converted to EF 1.5 using a 0.698 conversion factor which accounts for differences between lab rating and typical field performance (Source: Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007)) 2) Cost of standard unit: Average installed cost for a 200kBtu/Hr gas storage WH is $5,430 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) 3) Cost of efficient unit: Assumes the same incremental cost ratio of 2.35 as between residential baseline and state-of-the-art HPWH (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) The residentail cost is a target installed cost, based on the fact that ThermoLift aims to design a product that is cost competitive with state-of-the-art HPWH (Source: Comparative Analysis of Current Thermally-Driven Refrigeration Devices, ThermoLift, Inc.)
888 | Residential thermoelectric HPWH will likely not exceed the efficiency of conventional high-efficiency HPWH, they do have the potential to be significantly cheaper while still providing better performance than a traditional electric resistance WH. The system intends to replace a residential baseline 50 gal, 0.92 EF electric storage WH unit. Assume no impact on space heating and cooling of this measure. | R: Thermoelectric HPWH* | 0 | Residential | Water Heating | Total residential storage electric water heaters | Energy Factor | 1.6 | 0.92 | 1035 | 615 | 1035 | 615 | 420 | 13 | 13 | 1) Baseline unit performance: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment; 2) Efficient unit performance: Assuming TE HPWH with a 1.6 EF (Low Cost Heat Pump Water Heaters, Oct 5, 2013, http://aceee.org/files/pdf/conferences/hwf/2013/7A-pokharna.pdf) 3) Baseline unit cost: Total installed cost is $566 ($2008) (2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses) Cost adjusted from $2008 to $2014 (http://data.bls.gov/cgi-bin/cpicalc.pl) 4) Efficient unit cost: TARGET Installed Cost -Assuming $200 increase in retail price for TE HP (Source: Low Cost Heat Pump Water Heaters, Oct 5, 2013, http://aceee.org/files/pdf/conferences/hwf/2013/7A-pokharna.pdf) -Assuming $344 for product cost of baseline electric WH (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses), Cost adjusted from $2008 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl) -Assuming $491 for installation cost, based on installation cost for typical HPWH (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses), Cost adjusted from $2008 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl)
890 | A grey-water-source heat pump water heater can greatly reduce WH energy consumption when replacing a standard electric stoarage WH with 54kW capacity and thermal efficiency of 98%, especially in commercial buildings that have high WH loads (restaurants, laundromats, hotels, etc.) by recovering heat in grey water replacing electric storage WH via a water-to-water heat pump. Assume no impact on space heating and cooling of this measure. | C: Grey-Water HPWH* | 0 | Commercial | Water Heating | Total energy consumption by all commercial electric storage water heaters | Energy Factor | 2.4 | 0.92 | 9200 | 5430 | 9200 | 5430 | 3770 | 13 | 13 | 1) Baseline unit performance: Assuming roughly the same EF as a residential gas-fired storage WH for standard unit (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment) 2) Efficient unit performance: Assuming roughly the same performance as a ground-source heat pump, 3.5 COP (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) -Converting to 2.4 EF using a 0.698 conversion factor which accounts for differences between lab rating and typical field performance (Source: Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007)) 3) Baseline unit cost: Average installed cost for a 54 kW electric storage WH is $5,430 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) 4) Efficient unit cost: TARGET Installed Cost -Assuming a 48kBtu/Hr ground-source heat pump has a retail equipment cost of $7,000 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) -Assuming roughly 30% of that cost represents the water-to-air heat pump gives a cost of $2,100 (Source: COST CONTAINMENT FOR GROUND-SOURCE HEAT PUMPS, S. Kavanaugh, http://geoheat.oit.edu/pdf/tp72.pdf) -Assuming that the water-to-air heat pump is a reasonable proxy for a water-to-water heat pump and scaling this cost up to 200,000 kBtu/Hr capacity gives a cost of $8,750, and adding 40% for installation gives $12,250 -Assuming a 25% cost reduction for improved design results in a target installed cost of roughly $9,200
891 | Heat pump water heater connected directly to a PV array (i.e., without grid interconnection). It may utilize DC compressor and other components to avoid need for DC-AC converter. Baseline technology is assumed to be a typical residential electric storage WH with 50 gal tank and 0.92 EF. Assume no impact on space heating and cooling of this measure. | R: PV-assisted HPWH* | 0 | Residential | Water Heating | Total residential electric storage water heaters energy consumption in homes suitable for PV installations (35% of homes) | Energy Usage, kWh/yr | 340 | 2250 | 4590 | 615 | 4590 | 615 | 3975 | 13 | 13 | DOE WH R&D Roadmap Initiative "Develop optimal configurations for PV assisted HPWH by supporting lab testing and product development efforts " 1) Baseline unit performance: Assuming an average electric water heater consumes 2550 kwh/yr (2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 7 - Energy Use Chara) 2) Efficient unit performance: Average water heating energy use of HPWH (COP of 2.4) is 1830 kWh/yr (www.geappliances.com/heat-pump-hot-water-heater/water-heater-features.htm) -Using a PV Array with (4) 300W panels for a total of 1.2kW installed on a home in Boston MA would produce ~1490 kWh/Yr (usable), (PVWatts) In a best case scenario, 100% of the electricity output can all be used for water heating. The system will use 340 kWh/yr of site electricity. 3) Baseline unit cost: Total installed cost is $566 ($2008) (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses) Cost adjusted from $2008 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl) 4) Efficient unit cost: TARGET Installed Cost 5$/Watt Installed cost of PV; 1.2 kW of PV for $6,000 -Total installed cost for a HPWH is $1,517 ($2008) (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses), Cost adjusted to $1,654, from $2008 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl) -Assumes 40% achievable price reduction for 2030 target - including PV reduction to $3/W or less and additional HPWH reductions. -Added costs for PV to HPWH control module offset by no need for grid interconnection
893 | Integrating advanced thermal storage tanks into residential gas and electric storage water heaters, thereby reducing tank losses and extending equipment lifetimes. Baseline technology is assumed to be gas-fired and electric storage WH with conventional storage tanks. | R: Adv. Thermal Storage WH* | 0 | Residential | Water Heating | Total residential storage electric and natural gas water heaters | Energy Factor | 0.805 | 0.755 | N/A | N/A | N/A | N/A | 185 | 20 | 13 | DOE WH R&D Roadmap Initiative "Develop advanced thermal storage tanks" 1) Baseline unit performance: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment 2) Efficient unit performance: Estimated target increase 3) Incremental cost: TARGET Increase in Installed Cost based on $145 installed cost associated with increasing the insulation in a storage WH to improve 5 EF points (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses), cost adjusted from $2008 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl) Including $40 premium for longer lasting tank materials.
894 | Integrating advanced thermal storage tanks into commercial gas and electric storage water heaters, thereby reducing tank losses and extending equipment lifetimes. | C: Adv. Thermal Storage WH* | 0 | Commercial | Water Heating | Total energy consumption by all commercial storage water heaters | Energy Factor | 0.805 | 0.755 | N/A | N/A | N/A | N/A | 1850 | 20 | 13 | DOE WH R&D Roadmap Initiative "Develop advanced thermal storage tanks" 1) Baseline unit performance: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment 2) Efficient unit performance: Estimated target increase 3) Incremental cost: TARGET Increase in Installed Cost based on $145 installed cost associated with increasing the insulation in a storage WH to improve 5 EF points (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses), cost adjusted from $2008 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl). Including $40 premium for longer lasting tank materials.
896 | Improved commercial HPWHs with variable capacity to meet demands of commercial building environments, particularly those with large water heating loads. Not analyzing benefits of space cooling. Baseline technology: commercial electric storage WH 54kW, TE 98%. Assume no impact on space heating and cooling of this measure. | C: Variable Capacity HPWH* | 0 | Commercial | Water Heating | Total energy consumption by all commercial electric storage water heaters | Energy Factor | 2.8 | 0.92 | 16000 | 5430 | 16000 | 5430 | 10570 | 13 | 13 | DOE WH R&D Roadmap Initiative "Develop commercial HPWH with flexibility to meet base load demands, peak demands, and recovery time requirements" 1) Baseline unit performance: Assuming similar EF to residential electric storage WH (2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment) 2) Efficient unit performance: Assuming max performance, 4.0 COP (A.O. Smith AWH-170 Spec Sheet, http://www.hotwater.com/lit/spec/com_hp/aosze15000.pdf) -Converting to 2.8 EF using a 0.698 conversion factor which accounts for differences between lab rating and typical field performance (Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007)) 3) Baseline unit cost: Average installed cost for a 54 kW electric storage WH is $5,430 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013 4) Efficient unit cost: TARGET Installed Cost estimated using commercial rooftop heat pump as a proxy for commercial HPWH. Average equipment cost for a 90 kBtu/H rooftop heat pump is $7,325, scaling up to 200 kBtu/H equals roughly $16,000 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013)
898 | Develop more cost-effective compressors to make residential HPWH more cost competitive with conventional WH. Assume no impact on space heating and cooling of this measure. | R: Imp. HPWH Compressors* | 0 | Residential | Water Heating | Total residential storage electric water heaters | Energy Factor | 2.45 | 0.92 | 1500 | 615 | 1500 | 615 | 885 | 13 | 13 | DOE WH R&D Roadmap Initiative "Improve compressor technologies for HPWH" 1) Baseline performance: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment 2) Efficient unit performance: Assuming 2.45 EF (Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) Primary EF is 0.9, Assuming 3.1 site-to-source conversion factor (DOE Buildings Energy Data Book) 3) Base unit cost: Total installed cost is $566 ($2008) (2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses) -Cost adjusted from $2008 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl) 4) Efficient unit cost: This is a target installed cost, assuming a 10% reduction in the total installed cost due to reduction in cost of the compressor. Low installed cost estimate for a 50 gal, 2.45 EF HPWH is $1,710 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013)
900 | Develop more cost-effective compressors to make commercial HPWH more cost competitive with conventional WH. Not analyzing benefits of space cooling. Assume no impact on space heating and cooling of this measure. | C: Imp. HPWH Compressors* | 0 | Commercial | Water Heating | Total energy consumption by all commercial electric storage water heaters | Energy Factor | 2.5 | 0.92 | 14400 | 5430 | 14400 | 5430 | 8970 | 13 | 13 | DOE WH R&D Roadmap Initiative "Improve compressor technologies for HPWH" 1) Baseline performance: Assuming similar EF to residential electric storage WH (2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment) 2) Efficient unit performance: Assuming average performance of 3.6 COP (Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013 , and A.O. Smith AWH-170 Spec Sheet, http://www.hotwater.com/lit/spec/com_hp/aosze15000.pdf) Converting to 2.5 EF using a 0.698 conversion factor which accounts for differences between lab rating and typical field performance (Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007)) 3) Base unit cost: Average installed cost for a 54 kW electric storage WH is $5,430 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) 4) Efficient unit cost: $14,400, this is a target installed cost, assuming a 10% reduction in the total installed cost due to reduction in cost of the compressor -Estimated using commercial rooftop heat pump as a proxy for commercial HPWH. Average equipment cost for a 90 kBtu/H rooftop heat pump is $7,325, scaling up to 200 kBtu/H equals roughly $16,000 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) Based on a 15,000 sq ft commercial building, assuming 200 kBtu/H water heater is appropriate for a 15,000 sq ft building
902 | ≥R-12/in building envelope thermal insulation material that can be added to walls to retrofit existing buildings and can also be applicable to other portions of the building enclosure (e.g., reduce the impact of thermal bridging between building components). The material must meet durability requirements and minimize occupant disturbance. | R: Envelope Insulation (MYP2025)* | 0 | Residential | Building | Total residential heating and cooling lost through walls in all homes | R-value | 23.1 | 11.1 | 765.25 | 0 | 765.25 | 0 | 765.25 | 30 | 30 | R&D Roadmap for Emerging Window and Building Envelope Technologies 2014.
903 | ≥R-12/in building envelope thermal insulation material that can be added to walls to retrofit existing buildings and can also be applicable to other portions of the building enclosure (e.g., reduce the impact of thermal bridging between building components). The material must meet durability requirements and minimize occupant disturbance. | C: Envelope Insulation (MYP2025)* | 0 | Commercial | Building | Total heating and cooling load due to energy loss through walls in all commercial buildings | R-value | 29 | 17 | 0.135 | 0 | 0.135 | 0 | 0.135 | 40 | 40 | R&D Roadmap for Emerging Window and Building Envelope Technologies 2014.
904 | A system capable of concurrently regulating heat, air, and moisture flow to achieve the following performance specifications: <1 ACH50 | R: Air-Sealing, (MYP2025)* (N) | 0 | Residential | Building | Total heating and cooling in all new single-family homes | Energy savings (%) | 67% | 0% | 1136 | 0 | 1136 | 0 | 1136 | 30 | 30 | R&D Roadmap for Emerging Window and Building Envelope Technologies 2014.
905 | A system capable of concurrently regulating heat, air, and moisture flow to achieve the following performance specifications: <1 ACH51 | R: Air-Sealing, (MYP2025)* (E) | 0 | Residential | Building | Pre-2010 homes heating and cooling: Single family | Energy savings (%) | 90% | 0% | 1136 | 0 | 1136 | 0 | 1136 | 30 | 30 | R&D Roadmap for Emerging Window and Building Envelope Technologies 2014.
906 | A system capable of concurrently regulating heat, air, and moisture flow to achieve the following performance specifications: <0.25 CFM75/ft2 (5-sided envelope) | C: Air-Sealing (MYP2025)* | 0 | Commercial | Building | All commercial heating and cooling lost due to infiltration | CFM/ft2@75 Pa | 0.25 | 1.38 | 0.5 | 0 | 0.5 | 0 | 0.5 | 40 | 40 | R&D Roadmap for Emerging Window and Building Envelope Technologies 2014.
907 | Residential Advanced Vapor Compression Technologies (MYP 2020) | R: Adv. Vapor Compression (MYP2020)* | 0 | Residential | HVAC | Remainder of all residential and commercial electric heating and cooling | Energy Savings (%) | 34% | 0% | 0 | 0 | 0 | 0 | 0.45 | 15 | 15 | Tony Bouza
908 | Residential Target Air Source Integrated Heat Pump (2-speed and variable speed, electric) | R: Air-Source IHP (MYP2020)* | 0 | Residential | HVAC | 30% of Residential and Commercial IHP market (30% of electric heating, electric WH, and proportion of cooling) | Energy Savings (%) | 46% | 0% | 0 | 0 | 0 | 0 | 1.53 | 15 | 15 | Tony Bouza
909 | Residential Target Air Source Cold Climate Heat Pump | R: Air-Source Cold Climate HP (MYP2020)* | 0 | Residential | HVAC | Residential and Commercial Electric Heating + proportion of cooling in buildings with electric heating in CZ 1&2 | Energy Savings (%) | 46% | 0% | 0 | 0 | 0 | 0 | 2.08 | 15 | 15 | Tony Bouza
910 | Residential Target Non-Vapor Compression HVAC systems (magnetocaloric, electrocaloric and others) | R: Non-vapor Compr. HVAC (MYP2020)* | 0 | Residential | HVAC | Commercial and residential NIK gradual market entry for all electric heating and cooling | Energy Savings (%) | 40% | 0% | 0 | 0 | 0 | 0 | 0.4 | 15 | 15 | Tony Bouza
911 | Residential Target Gas Engine Driven HP | R: Gas Engine HP (MYP2020)* | 0 | Residential | HVAC | Residential and Commercial Gas Heating and Gas Cooling | Energy Savings (%) | 42% | 0% | 0 | 0 | 0 | 0 | 1.03 | 15 | 15 | Tony Bouza
912 | Target Gas Heat Pump Heating | R+C: Gas Heat Pump (MYP2020)* | 0 | Residential and Commercial | HVAC | Residential and Commercial Gas Heating and Gas Cooling | Energy Savings (%) | 40% | 0% | 0 | 0 | 0 | 0 | 0.98 | 15 | 15 | Tony Bouza
913 | Target Residential heat pump clothes dryers | R: HP Clothes Dryer (MYP2020)* | 0 | Residential | Washing & Drying | Total energy use by all electric clothes dryers | Energy Savings (%) | 50% | 0% | 0 | 0 | 0 | 0 | 500 | 12 | 12 | Tony Bouza
914 | Target residential advanced compressor for refrigeration | R: Compressor Refrig.(MYP2020)* | 0 | Residential | Refrigeration | Residential Refrigerators and Freezers (excluding non-vapor compression refrigeration, assuming its entrance into market in 2016 with 20% market share by 2030 | Energy Savings (%) | 20% | 0% | 0 | 0 | 0 | 0 | 100 | 17 | 17 | Program goal
915 | Target Advanced Refrigeration | R: Adv Refrigerator (MYP2020)* | 0 | Residential | Refrigeration | Residential Refrigerators and Freezers (excluding non-vapor compression refrigeration, assuming its entrance into market in 2016 with 20% market share by 2030 | Energy Savings (%) | 50% | 0% | 0 | 0 | 0 | 0 | 250 | 17 | 17 | Program goal
916 | Target Non-Vapor Compression Refrigeration (magnetocaloric) | R: Non-Vapor Compr. Refrig.(MYP2020)* | 0 | Residential | Refrigeration | Residential Non Vapor Compression Refrigeration (assuming its entrance into market in 2016 with 20% market share by 2030) | Energy Savings (%) | 60% | 0% | 0 | 0 | 0 | 0 | 300 | 17 | 17 | Program goal
917 | Target commercial advanced compressor for refrigeration | C: Compressor Refrig.(MYP2020)* | 0 | Commercial | Refrigeration | All commercial compressors (DC) | Energy Savings (%) | 10% | 0% | 0 | 0 | 0 | 0 | 1000 | 15 | 15 | 0
918 | Target Advanced Refrigeration | C: Adv Refrigerator (MYP2020)* | 0 | Commercial | Refrigeration | All commercial refrigeration equipment (including compressors, excluding condensers and non-vapor compression refrigeration, assuming its entrance into market in 2016 with 20% market share by 2030) | Energy Savings (%) | 10% | 0% | 0 | 0 | 0 | 0 | 1000 | 12 | 12 | 0
919 | Target Non-Vapor Compression Refrigeration (magnetocaloric) | C: Non-Vapor Compr. Refrig.(MYP2020)* | 0 | Commercial | Refrigeration | Commercial Non-vapor Compression Refrigeration | Energy Savings (%) | 10% | 0% | 0 | 0 | 0 | 0 | 1000 | 12 | 12 | 0
920 | Target for non-CO2 vapor compression HPWH (MYP 2020). Similar to measure #526. Assume no impact on space heating and cooling of this measure. | R: Non-CO2 Vap-Comp HPWH (MYP2020)* | 0 | Residential | Water Heating | Total residential storage electric water heaters | Energy Factor | 2.5815 | 0.92 | 1046.5 | 640 | 1046.5 | 640 | 406.5 | 13 | 13 | 1) Performance and cost targets from MYP 2014 Report; 2) Baseline cost and performance from EIA- Technology Forecast Updates - Residential and Commercial Building Technologies- Reference Case. September 2013.
921 | Target for CO2 vapor compression HPWH (MYP 2020). Similar to measure #525. Assume no impact on space heating and cooling of this measure. | R: CO2 Vap-Comp HPWH (MYP2020)* | 0 | Residential | Water Heating | Total residential storage electric water heaters | Energy Factor | 2.9958 | 0.92 | 1237 | 640 | 1237 | 640 | 597 | 13 | 13 | 1) Performance and cost targets from MYP 2014 Report; 2) Baseline cost and performance from EIA- Technology Forecast Updates - Residential and Commercial Building Technologies- Reference Case. September 2013.
922 | Target for non-vapor compression HPWH (MYP 2020). Similar to measure #798. Assume no impact on space heating and cooling of this measure. | R:Non-Vap-comp HPWH (MYP2020)* | 0 | Residential | Water Heating | Total residential storage electric water heaters | Energy Factor | 1.6572 | 0.92 | 840 | 640 | 840 | 640 | 150 | 13 | 13 | 1) Performance and cost targets from MYP 2014 Report; 2) Baseline cost and performance from EIA- Technology Forecast Updates - Residential and Commercial Building Technologies- Reference Case. September 2013.
923 | Target for gas-fired absorption or adsorption HPWH (MYP 2020). Assume no impact on space heating and cooling of this measure. | R: Ab/Ad-sorption Gas HPWH (MYP2020)* | 0 | Residential | Water Heating | Total residential storage natural gas water heaters | Energy Factor | 1.2 | 0.59 | 1285.6 | 1000 | 1285.6 | 1000 | 285.6 | 13 | 13 | 1) Performance and cost targets from MYP 2014 Report; 2) Baseline cost and performance from EIA- Technology Forecast Updates - Residential and Commercial Building Technologies- Reference Case. September 2013.
925 | Optimize whole-building control system (new software) that controls the operation of multiple systems to minimize costs based on a variety of inputs, such as occupancy, weather, fuel prices, etc. This measure is applicable to systems in large buildings (>100,000 sq.ft.) with poorly performing control systems. It also includes retro-commissioning (adjustment of thermostats, schedules, set points, calibration. It does not include equipment replacement (bad sensors, frozen dampers, etc.)) - will be an extra cost. | C: Bldg Control Opt. (all bldgs)* | 0 | Commercial | HVAC/Lighting | All HVAC and Lighting energy use in commercial buildings | Energy Savings (%) | 20% | 0% | 2.36 | 0 | 2.36 | 0 | 2.36 | 15 | 15 | 1) Savings and costs from pg. 9-91,93,95,139 of TIAX. Energy Impact of Commercial Building Controls and Performance Diagnostics: Market Characterization, Energy Impact of Building Faults and Energy Savings Potential. November 2005. “Overall, it would appear that the first cost of an OWBCS associated with an EMCS would be similar to the cost of a higher-end Whole Building Diagnostics implementation less the cost of additional sensors, i.e. on the order of $100,000.” Adding the costs of the EMCS, which is assumed to be similar to EIS of $1.36/sq.ft (pg. 9-136), and the OWBCS for a 100,000 sq.ft. building gives a cost of $2.36/sq.ft.
937 | Upgrade medium or small sized office buildings (<100,000SF) from standalone thermostat control design to a building automation system control design (HVAC benefit only), which includes new thermostats that communicate with BAS head-end; wireless temperature sensors to cover 50% of the office spaces; communications network which allows for sharing and configuration of common data points like ouside air temp, occupancy and holiday scheduling, trend logs and historical data; whole building electrical metering system that provides real-time and historical data naalysis of the building; holiday scheduling, optimal start capability, schedules tightened, auto night low and high limits set, 4F dead band gap created, and auto air low temp override added. The buildings had rooftop heat pump units, and were located in Richland, Washington. | C: Bldg Auto System (<100,000SF) | 3 | Commercial | HVAC | All HVAC energy use in small and medium commercial buildings <100,000 sq.ft. | Energy Savings (%) | 22% | 0% | 1 | 0 | 1 | 0 | 1 | 15 | 15 | Cost and energy savings from Small- and Medium Sized Commercial Building Monitoring and Controls Needs: A Scoping Study. Katipamula, Underhill, Goddard, Taasevigen, Piette, Granderson, et al. PNNL 22169. October 2012. pg. 48-54.
938 | Demonstrate and deploy smart thermostat that uses occupancy sensors to automatically turn off the HVAC system when the occupants are sleeping or away from home. The wireless motion and door sensors cost ~$5 each off the shelf and can be installed in minutes using double-sided tape. The smart thermostat has a fast reaction algorithm with a probabilistic model that uses these sensors and processes the sensor data to quickly estimate whether occupants are active, sleeping, or away. This algorithm can typically respond within minutes of the occupants leaving the house, without introducing false vacancy detections. Second, the system combines historical occupancy patterns with on-line sensor data to decide whether to preheat the home or to heat after the occupants arrive. Finally, the system saves additional energy by using deep setback, allowing the temperature to drift further from the setpoint temperature when it is confident that the home is unoccupied. | R: Smart Thermostats (UVA) | 2 | Residential | Building | Total residential central AC and heating energy consumption | Energy Savings (%) | 28% | 0% | 25 | 0 | 25 | 0 | 25 | 35 | 35 | Energy savings and cost - pg. 1 of The Smart Thermostat: Using Occupancy Sensors to Save Energy in Homes. Jiakang Lu, Tamim Sookoor, et al. University of Virginia. SenSys November 305, 2010.
940 | Demonstrate and deploy demand control ventilation with an a cheaper metal-oxide indoor air quality sensor that will enable demand control ventilation in compliance with the ASHRAE standard 61-1989. | C: DCV, VOC metal-oxide sensors | 1 | Commercial | Ventilation | All commercial HVAC energy use | Energy Savings (%) | 15% | 0% | 0.15622 | 0 | 0.15622 | 0 | 0.15622 | 15 | 15 | 1) Measures is based on #141, which showed 20% savings for DCV, however, because VOC/metal oxide sensors seems more sensitive/will do more ventilation work, potential savings were reduced by 25%. This is based on Figures 6 & 7 of Beyond CO2: Sensing VOCs in Indoor Air Protects Health, Saves Energy. Applied Sensor White Paper. https://www.appliedsensor.com/pdfs/IndoorAirQuality_WhitePaper_0609.pdf) 2) Cost was based on a form submitted by ORNL and email confirmation from Teja Kuruganti that claimed $50/metal oxide sensor cost. Hence cost of #141 C: DCV was taken and reduced by $50 (derivation explanation can be found in notes). Final cost per sq.ft. was not significantly affected.
943 | Develop and evaluate techniques for separate sensible and latent control for residential central A/Cs. Air-conditioning systems remove both sensible heat (temperature) and latent heat (the energy required to evaporate or condense water) from supply air to create comfortable conditions for building occupants. Many options for latent control exist, but typically as an add-on component and may increase energy consumption. Incorporating these technologies into packaged solutions can lower the installation cost/ complexity, especially for retrofit applications, and better coordinate the control of sensible and latent cooling mechanisms. | R: Latent Heat Controls Package to replace CAC and ASHP cooling (HVAC RM)* | 0 | Residential | Cooling | Total residential cooling (CAC & ASHP) other than room A/Cs | Energy Savings (%) | 30% | 0% | 5300 | 2300 | 5300 | 2300 | 3000 | 16 | 16 | 1. Savings estimated from Ling et al. 2010 "Enhancement of the Separate Sensible and Latent Cooling Air-Conditioning Systems" and similar research papers 2. Cost premium: Assumes cost premium equal to residential high efficiency central A/Cs from EIA Technology Forecast Update 3. Lifetime: Median of Residential central A/C from EIA Technology Forecast Update
944 | Develop and evaluate techniques for separate sensible and latent control for residential room A/Cs. Air-conditioning systems remove both sensible heat (temperature) and latent heat (the energy required to evaporate or condense water) from supply air to create comfortable conditions for building occupants. Many options for latent control exist, but typically as an add-on component and may increase energy consumption. Incorporating these technologies into packaged solutions can lower the installation cost/ complexity, especially for retrofit applications, and better coordinate the control of sensible and latent cooling mechanisms. | R: Latent Heat Controls Package for Room A/C (HVAC RM)* | 0 | Residential | Cooling | All residential cooling using room A/Cs | Energy Savings (%) | 30% | 0% | 600 | 440 | 600 | 440 | 160 | 10 | 10 | 1. Savings estimated from Ling et al. 2010 "Enhancement of the Separate Sensible and Latent Cooling Air-Conditioning Systems" and similar research papers 2. Cost premium: Assumes cost premium equal to residential high efficiency room A/Cs from EIA Technology Forecast Update 3. Lifetime: Median of Residential room A/C from EIA Technology Forecast Update
945 | Develop and evaluate techniques for separate sensible and latent control for rooftop A/C units and ASHPs. Air-conditioning systems remove both sensible heat (temperature) and latent heat (the energy required to evaporate or condense water) from supply air to create comfortable conditions for building occupants. Many options for latent control exist, but typically as an add-on component and may increase energy consumption. Incorporating these technologies into packaged solutions can lower the installation cost/ complexity, especially for retrofit applications, and better coordinate the control of sensible and latent cooling mechanisms. | C: Latent Heat Controls Package (HVAC RM)* | 0 | Commercial | Cooling | Total commercial cooling by RTUs and ASHPs | Energy Savings (%) | 30% | 0% | 12.1429 | 4.3095 | 12.1429 | 4.3095 | 7.8333 | 15 | 15 | 1. Savings estimated from Ling et al. 2010 "Enhancement of the Separate Sensible and Latent Cooling Air-Conditioning Systems" and similar research papers 2. Cost premium: Assumes cost premium equal to commercial high efficiency Rooftop unit from EIA Technology Forecast Update 3. Lifetime: Commercial Rooftop Unit AC from EIA Technology Forecast Update
946 | Develop electrochemical compression systems to replace residential central AC and ASHP heating. Electrochemical compressors raise the pressure of a hydrogen working fluid using a proton exchange membrane and electricity source, and replace motor-driven compressors for a heat pump system. Additional development is needed to develop the technology, working fluids, and system aspects to drive a vapor-compression cycle. | R: Electrochemical Compressors to replace CAC & ASHP* | 0 | Residential | Heating & Cooling | Total residential cooling by CAC and ASHPs as well as ASHP heating | Energy Savings (%) | 20% | 0% | 165 | 0 | 165 | 0 | 165 | 18 | 18 | 1. Savings estimates from Xergy presentation 2013 http://aceee.org/files/pdf/conferences/hwf/2013/7A-bahar.pdf 2. Cost premium: Xergy estimates $55 incremental cost for 1-ton compressor, assumes other costs are equal, Xergy presentation 2013 http://aceee.org/files/pdf/conferences/hwf/2013/7A-bahar.pdf 3. Lifetime: Median of Residential central A/C from EIA Technology Forecast Update
947 | Develop electrochemical compression systems to replace room ACs. Electrochemical compressors raise the pressure of a hydrogen working fluid using a proton exchange membrane and electricity source and replace motor-driven compressors for a heat pump system. Additional development is needed to develop the technology, working fluids, and system aspects to drive a vapor-compression cycle. | R: Electrochemical Compressors to replace room AC* | 0 | Residential | Heating & Cooling | All residential cooling using room A/Cs | Energy Savings (%) | 20% | 0% | 55 | 0 | 55 | 0 | 55 | 9 | 9 | 1. Savings estimates from Xergy presentation 2013 http://aceee.org/files/pdf/conferences/hwf/2013/7A-bahar.pdf 2. Cost premium: Xergy estimates $55 incremental cost for 1-ton compressor, assumes other costs are equal, Xergy presentation 2013 http://aceee.org/files/pdf/conferences/hwf/2013/7A-bahar.pdf 3. Lifetime: Median of Residential room A/C from EIA Technology Forecast Update
948 | Develop electrochemical compression systems to replace rooftop AC units (RTUs) and ASHP's cooling and heating. Electrochemical compressors raise the pressure of a hydrogen working fluid using a proton exchange membrane and electricity source and replace motor-driven compressors for a heat pump system. Additional development is needed to develop the technology, working fluids, and system aspects to drive a vapor-compression cycle. | C: Electrochemical Compressors to replace RTUs & ASHPs* | 0 | Commercial | Heating & Cooling | All commercial cooling by ASHPs and RTUs; and heating by ASHPs | Energy Savings (%) | 20% | 0% | 0.19643 | 0 | 0.19643 | 0 | 0.19643 | 15 | 15 | 1. Savings estimates from Xergy presentation 2013 http://aceee.org/files/pdf/conferences/hwf/2013/7A-bahar.pdf 2. Cost premium: Xergy estimates $55 incremental cost for 1-ton compressor, assumes other costs are equal, Xergy presentation 2013 http://aceee.org/files/pdf/conferences/hwf/2013/7A-bahar.pdf 3. Lifetime: Commercial Rooftop Unit AC from EIA Technology Forecast Update
949 | Develop techniques to raise heat pump performance at low-ambient temperature; consider elimination of defrost (or frost buildup) and backup heat sources to improve the application of cold-climate heat pumps. Traditionally, vapor-compression heat pumps have had limited use in colder climates due to decreasing heating capacity and COP as outdoor temperatures decrease because of the increased temperature lift across the compressor. Several technologies could improve heat pump performance at low-ambient conditions and improve electric or gas heat pump efficiency in colder climates. | R: Cold Climate HP to replace ASHP* | 0 | Residential | Heating | Total residential electric heating using ASHP | Energy Savings (%) | 25% | 0% | 3000 | 0 | 3000 | 0 | 3000 | 15 | 15 | 1. Savings estimated from Navigant Residential HVAC Report 2. Cost premium: Navigant assumption of $3000 premium from Residential HVAC Report 3. Lifetime: Median of residential central ASHPs, from EIA Technology Forecast Update
950 | Develop techniques to raise heat pump performance at low-ambient temperature; consider elimination of defrost (or frost buildup) and backup heat sources to improve the application of cold-climate heat pumps. Traditionally, vapor-compression heat pumps have had limited use in colder climates due to decreasing heating capacity and COP as outdoor temperatures decrease because of the increased temperature lift across the compressor. Several technologies could improve heat pump performance at low-ambient conditions and improve electric or gas heat pump efficiency in colder climates. | R: Cold Climate Gas HP to replace gas heating* | 0 | Residential | Heating | Total residential heating using natural gas furnaces and boilers | Energy Savings (%) | 40% | 0% | 3000 | 0 | 3000 | 0 | 3000 | 15 | 15 | 1. Savings estimated from Navigant Residential HVAC Report 2. Cost premium: Navigant assumption of $3000 premium from Residential HVAC Report 3. Lifetime: Residential gas-fired heat pump from EIA Technology Forecast Update
951 | Develop techniques to raise heat pump performance at low-ambient temperature; consider elimination of defrost (or frost buildup) and backup heat sources to improve the application of cold-climate heat pumps. Traditionally, vapor-compression heat pumps have had limited use in colder climates due to decreasing heating capacity and COP as outdoor temperatures decrease because of the increased temperature lift across the compressor. Several technologies could improve heat pump performance at low-ambient conditions and improve electric or gas heat pump efficiency in colder climates. | C: Cold Climate HP to replace ASHP* | 0 | Commercial | Heating | Total commercial ASHP heating | Energy Savings (%) | 25% | 0% | 1.9 | 0 | 1.9 | 0 | 1.9048 | 15 | 15 | 1. Savings estimated from Navigant Commercial HVAC Report 2. Cost premium: Navigant assumption of $4000 premium Residential and Commercial HVAC Report 3. Lifetime: Commercial central ASHPs, from EIA Technology Forecast Update
952 | Develop techniques to raise heat pump performance at low-ambient temperature; consider elimination of defrost (or frost buildup) and backup heat sources to improve the application of cold-climate heat pumps. Traditionally, vapor-compression heat pumps have had limited use in colder climates due to decreasing heating capacity and COP as outdoor temperatures decrease because of the increased temperature lift across the compressor. Several technologies could improve heat pump performance at low-ambient conditions and improve electric or gas heat pump efficiency in colder climates. | C: Cold Climate Gas HP to replace gas heating* | 0 | Commercial | Heating | Total natural gas heating | Energy Savings (%) | 40% | 0% | 1.9 | 0 | 1.9 | 0 | 1.9048 | 15 | 15 | 1. Savings estimated from Navigant Residential HVAC Report, because systems will use modular units of similar technology to residential 2. Cost premium: Navigant assumption of $4000 premium Residential and Commercial HVAC Report 3. Lifetime: Commercial Gas-Fired Engine-Driven Rooftop Air Conditioners from EIA Technology Forecast Update
953 | Develop non-VC cooling systems (Thermoelectric, magnetic, etc.) to replace residential ASHP heating with suitable efficiency, cost, and performance compared to next generation HVAC equipment. This measure intends to replace residential ASHP heating. Various non-vapor compression cooling cycles exist that offer the potential for significant energy savings over current and future vapor-compression systems, but require additional development before wide commercialization for HVAC systems. | R: Non-VC System to replace ASHP for heating* | 0 | Residential | Heating | Total residential electric heating using ASHP | Energy Savings (%) | 25% | 0% | 4500 | 3300 | 4500 | 3300 | 1200 | 15 | 15 | 1. Savings estimated from Navigant Non-Vapor-Compression Report, vuilleumier and magnetocaloric heating 2. Cost premium: Assumes cost premium equal to residential high efficiency central ASHPs from EIA Technology Forecast Update 3. Lifetime: Median of residential central ASHPs, from EIA Technology Forecast Update
954 | Develop non-VC cooling systems (Thermoelectric, magnetic, etc.) to replace commercial ASHP heating with suitable efficiency, cost, and performance compared to next generation HVAC equipment. Various non-vapor compression cooling cycles exist that offer the potential for significant energy savings over current and future vapor-compression systems, but require additional development before wide commercialization for HVAC systems. | C: Non-VC System to replace ASHP for heating* | 0 | Commercial | Heating | Total commercial ASHP heating | Energy Savings (%) | 25% | 0% | 12.1667 | 4.3095 | 12.1667 | 4.3095 | 7.8571 | 15 | 15 | 1. Savings estimated from Navigant Non-Vapor-Compression Report, vuilleumier and magnetocaloric heating 2. Cost premium: Assumes cost premium equal to commercial high efficiency Rooftop unit from EIA Technology Forecast Update 3. Lifetime: Commercial central ASHPs, from EIA Technology Forecast Update
955 | Develop non-VC cooling systems (Thermoelectric, magnetic, etc.) to replace all residential cooling other than room ACs with suitable efficiency, cost, and performance compared to next generation HVAC equipment. Various non-vapor compression cooling cycles exist that offer the potential for significant energy savings over current and future vapor-compression systems, but require additional development before wide commercialization for HVAC systems. | R: Non-VC System to replace CAC* | 0 | Residential | Cooling | Total residential cooling (CAC & ASHP) other than room A/Cs | Energy Savings (%) | 40% | 0% | 5300 | 2300 | 5300 | 2300 | 3000 | 16 | 16 | 1. Savings estimated from Navigant Non-Vapor-Compression Report, thermoelastic and membrane cooling 2. Cost premium: Assumes cost premium equal to residential high efficiency central A/Cs from EIA Technology Forecast Update 3. Lifetime: Median of Residential central A/C from EIA Technology Forecast Update
956 | Develop non-VC cooling systems (Thermoelectric, magnetic, etc.) to replace all room AC cooling with suitable efficiency, cost, and performance compared to next generation HVAC equipment. Various non-vapor compression cooling cycles exist that offer the potential for significant energy savings over current and future vapor-compression systems, but require additional development before wide commercialization for HVAC systems. | R: Non-VC System to replace Room AC* | 0 | Residential | Cooling | All residential cooling using room A/Cs | Energy Savings (%) | 40% | 0% | 600 | 440 | 600 | 440 | 160 | 10 | 10 | 1. Savings estimated from Navigant Non-Vapor-Compression Report, thermoelastic and membrane cooling 2. Cost premium: Assumes cost premium equal to residential high efficiency room A/Cs from EIA Technology Forecast Update 3. Lifetime: Median of Residential room A/C from EIA Technology Forecast Update
957 | Develop non-VC cooling systems (Thermoelectric, magnetic, etc.) to replace commercial cooling by RTUs and ASHPs with suitable efficiency, cost, and performance compared to next generation HVAC equipment. Various non-vapor compression cooling cycles exist that offer the potential for significant energy savings over current and future vapor-compression systems, but require additional development before wide commercialization for HVAC systems. | C: Non-VC System to replace RTU and ASHP cooling* | 0 | Commercial | Cooling | Total commercial cooling by RTUs and ASHPs | Energy Savings (%) | 40% | 0% | 12.1429 | 4.3095 | 12.1429 | 4.3095 | 7.8333 | 15 | 15 | 1. Savings estimated from Navigant Non-Vapor-Compression Report, thermoelastic and membrane cooling 2. Cost premium: Assumes cost premium equal to commercial high efficiency Rooftop unit from EIA Technology Forecast Update 3. Lifetime: Commercial Rooftop Unit AC from EIA Technology Forecast Update
958 | Develop hybrid systems to combine mechanical and natural ventilation techniques, aka mixed-mode conditioning or integrated window ventilation. When conditions allow, automatic window dampers can allow outside air into a space and offset ventilation and/or cooling provided by mechanical systems. | C: Hybrid Mechanical & Natural Ventilation* | 0 | Commercial | HVAC | Total commercial cooling and ventilation | Energy Savings (%) | 15% | 0% | 5 | 0 | 5 | 0 | 5 | 15 | 40 | 1. Savings estimated from LBNL http://www.cbe.berkeley.edu/mixedmode/aboutmm.html 2. Cost premium: Assumes $5/SF from NSF/IUCRC. 2004. “Guidelines for High Performance Buildings 2004.” 3. Lifetime for efficient unit: Navigant estimate for lifetime, assumes motor/actuator replacement and maintenance 4. Lifetime for old unit is set at the expected life of a window.
959 | Investigate new absorption pairs, compact heat exchangers, and other material advances to reduce the cost of absorption systems for residential gas heating applications. Absorption systems utilize thermal energy to drive a heat-pump cycle where a refrigerant is cyclically absorbed and desorbed from a secondary fluid, but barriers exist with regard to size/weight, operating risk, and cost compared to conventional systems. Advances in absorption pairs, heat and mass exchanger designs, and other advances could improve their viability for residential systems. | R: Advances in Absorption Gas Systems* | 0 | Residential | Heating | Total residential heating energy use by natural gas furnaces in all homes. | Energy Savings (%) | 40% | 0% | 12000 | 2300 | 12000 | 2300 | 9700 | 15 | 15 | 1. Savings estimated from Navigant Residential HVAC Report 2. Cost premium: Estimated as residential gas heat pump (low range) against furnace for EIA Technology Forecast Update 3. Lifetime: Residential gas-fired heat pump from EIA Technology Forecast Update
960 | Investigate new absorption pairs, compact heat exchangers, and other material advances to reduce the cost of absorption systems for commercial gas heating applications. Absorption systems utilize thermal energy to drive a heat-pump cycle where a refrigerant is cyclically absorbed and desorbed from a secondary fluid, but barriers exist with regard to size/weight, operating risk, and cost compared to conventional systems. Advances in absorption pairs, heat and mass exchanger designs, and other advances could improve their viability for light commercial systems. | C: Advances in Absorption Gas Systems* | 0 | Commercial | Heating | Total natural gas heating | Energy Savings (%) | 40% | 0% | 66900 | 22300 | 66900 | 22300 | 1.7422 | 15 | 15 | 1. Savings estimated from Navigant Residential HVAC Report 2. Cost premium: Estimated as 200% increase (Navigant Residential HVAC Report) on gas-fired boiler ($22.3k per 800kBtuh) for EIA Technology Forecast Update 3. Lifetime: Residential gas-fired heat pump from EIA Technology Forecast Update (commercial will be similar to modular residential)
961 | Develop a direct-current (DC)-powered HVAC system to utilize DC power from a solar photovoltaic (PV) system ,or other distributed DC generation, without inverter losses and facilitate micro grid integration. As one of the largest building loads, HVAC systems designed for DC-power would reduce the losses normally incurred from conversion of solar PV and battery electricity to AC power. While some products exist for telecommunications, electronics, and transportation systems, research into DC-based air conditioners could enable greater usage of microgrid and renewable systems. | R: DC-powered HVAC* | 0 | Residential | Heating & Cooling | Total residential cooling by CAC and ASHPs as well as ASHP heating | Energy Savings (%) | 66% | 0% | 5870 | 1150 | 5870 | 1150 | 4720 | 18 | 18 | 1. Savings assumed by eliminating site-to-source losses 2. Cost premium: Baseline cost for 1-ton ductless minisplit assumed as 50% of 3-ton split system. Efficient unit costs obtained from Hotspot Energy http://www.hotspotenergy.com/DC-air-conditioner/DC-AC-Complete-Systems.php 3. Lifetime: Median of Residential central A/C from EIA Technology Forecast Update
962 | Develop less expensive magnets for magnetocaloric cooling systems. Magnetocaloric cooling systems can potentially provide space cooling (and potentially heating) without high-GWP refrigerants, but requires further advances on cost, size, weight, etc. | R: Magnets for magnetocaloric systems to replace CAC and ASHP heating* | 0 | Residential | Heating & Cooling | Total residential cooling by CAC and ASHPs as well as ASHP heating | Energy Savings (%) | 20% | 0% | 5300 | 2300 | 5300 | 2300 | 3000 | 18 | 18 | 1. Savings estimated from Navigant Non-Vapor-Compression Report 2. Cost premium: Assumes cost premium equal to residential high efficiency central A/Cs from EIA Technology Forecast Update 3. Lifetime: Median of Residential central A/C from EIA Technology Forecast Update
963 | Develop less expensive magnets for magnetocaloric cooling systems. Magnetocaloric cooling systems can potentially provide space cooling (and potentially heating) without high-GWP refrigerants, but requires further advances on cost, size, weight, etc. | R: Magnets for magnetocaloric room AC cooling* | 0 | Residential | Cooling | All residential cooling using room A/Cs | Energy Savings (%) | 20% | 0% | 600 | 440 | 600 | 440 | 160 | 10 | 10 | 1. Savings estimated from Navigant Non-Vapor-Compression Report 2. Cost premium: Assumes cost premium equal to residential high efficiency room A/Cs from EIA Technology Forecast Update 3. Lifetime: Median of Residential room A/C from EIA Technology Forecast Update
964 | Develop less expensive magnets for magnetocaloric cooling systems. Magnetocaloric cooling systems can potentially provide space cooling (and potentially heating) without high-GWP refrigerants, but requires further advances on cost, size, weight, etc. | C: Magnets for magnetocaloric systems to replace RTU and ASHP* | 0 | Commercial | Heating & Cooling | All commercial cooling by ASHPs and RTUs; and heating by ASHPs | Energy Savings (%) | 20% | 0% | 12.1429 | 4.3095 | 12.1429 | 4.3095 | 7.8333 | 15 | 15 | 1. Savings estimated from Navigant Non-Vapor-Compression Report 2. Cost premium: Assumes cost premium equal to commercial high efficiency Rooftop unit from EIA Technology Forecast Update 3. Lifetime: Commercial Rooftop Unit AC from EIA Technology Forecast Update
965 | Develop methods, technologies, and other innovations to easily integrate seasonal energy storage. Thermal energy storage allows heating and cooling loads to be met by low-cost energy produced at a different time, including the integration of renewables, or improves the seasonal efficiency of GSHPs. Currently high cost of installation, design, etc. prohibit usage. | R: Seasonal Thermal Energy Storage* | 0 | Residential | Heating | Total primary and secondary heating (electricity, distillate, geothermal, LPG and Kerosene) | Energy Savings (%) | 30% | 0% | 1200 | 0 | 1200 | 0 | 1200 | 25 | 25 | 1. Savings estimated at 30% based on solar thermal system storage, can vary much higher, http://www.itw.uni-stuttgart.de/dokumente/Publikationen/publikationen_03-09.pdf 2. Cost premium: Cost estimate for 20m^3 storage system in addition to baseline furnace/boiler at $600/m^3 (@$1.35/1 Euro) from http://www.rhc-platform.org/fileadmin/Events/4_-_Kerskes_seasonal_TES.pdf 3. Lifetime: Navigant assumption for minimal maintenance and degradation over time
966 | Develop methods, technologies, and other innovations to easily integrate seasonal energy storage. Thermal energy storage allows heating and cooling loads to be met by low-cost energy produced at a different time, including the integration of renewables, or improves the seasonal efficiency of GSHPs. Currently high cost of installation, design, etc. prohibit usage. | C: Seasonal Thermal Energy Storage* | 0 | Commercial | Heating | All commercial heating | Energy Savings (%) | 30% | 0% | 4.7 | 0 | 4.7 | 0 | 4.7 | 15 | 15 | 1. Savings estimated at 30% based on solar thermal system storage, can vary much higher, http://www.itw.uni-stuttgart.de/dokumente/Publikationen/publikationen_03-09.pdf 2. Cost premium: Cost estimate for large scale hot water storage system $4.7/SF (@$1.35/1 Euro)based on survey of Systems http://www.itw.uni-stuttgart.de/dokumente/Publikationen/publikationen_03-09.pdf, and costs from http://www.rhc-platform.org/fileadmin/Events/4_-_Kerskes_seasonal_TES.pdf 3. Lifetime: Navigant assumption for minimal maintenance and degradation over time
967 | Research strategies to improve ground-source heat pump (GSHP) ground-loop cost and performance; also consider siting, installation, and modeling to reduce costs. GSHPs utilize the relatively stable temperatures of the ground, water, or other thermal mass, as a thermal source/sink for a heat pump, decreasing the temperature lift compared to air-systems. Currently high cost of installation, design, etc. prohibit usage. | R: GSHP - only HVAC* | 0 | Residential | Heating & Cooling | All electric heating, proportion of cooling in homes with electric heating | Energy Savings (%) | 30% | 0% | 10000 | 2300 | 10000 | 2300 | 7700 | 25 | 20 | 1. Savings estimate from Navigant Residential HVAC Report 2. Cost premium: Assumes cost premium equal to commercial GSHP (low estimate) vs. standard commercial ASHP from EIA Technology Forecast Update 3. Lifetime: Residential GSHP from EIA Technology Forecast Update
968 | Research strategies to improve ground-source heat pump (GSHP) ground-loop cost and performance; also consider siting, installation, and modeling to reduce costs. GSHPs utilize the relatively stable temperatures of the ground, water, or other thermal mass, as a thermal source/sink for a heat pump, decreasing the temperature lift compared to air-systems. Currently high cost of installation, design, etc. prohibit usage. | C: GSHP - only HVAC* | 0 | Commercial | Heating & Cooling | Total commercial electric heating and proportion of cooling in buildings with electric heating | Energy Savings (%) | 30% | 0% | 16500 | 7700 | 16500 | 7700 | 4.1905 | 25 | 15 | 1. Savings estimate from Navigant Residential HVAC Report 2. Cost premium: Assumes cost premium equal to residential GSHP (low estimate) vs. standard central ASHP from EIA Technology Forecast Update 3. Lifetime: Commercial GSHP from EIA Technology Forecast Update
969 | Improving Buildings Energy Performance by Integrating non-Energy Plus Energy Modeling in the Design Stage, New Buildings | C: Modeling Integration in Building Design (N) | 3 | Commercial | All End Uses | Total HVAC load in new commercial buildings | Energy Savings (%) | 15% | 0% | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 2013 AIA 2030 Commitment Annual Report (to be published on the AIA website soon) 1) No good incremental cost data available, costs were estimated to be similar to EnergyPlus integration modeling #878; 2) The energy savings estimates are for architectural firms that are participating in the AIA 2030 Commitment. These are generally large architecture firms that we consider to be aggressive in pursuing energy efficiency (i.e. data is not from a random or representative sample) 3) The energy savings estimate is for the marginal energy savings improvement of simulation/integrative design measures on building designs that already meet “beyond-code prescriptive” performance levels 4) Modeling improves all areas of building consumption, although currently savings were only applied to HVAC because that's the largest active component and because we don't have good data at this point to partition the savings at a finer granularity.
970 | Improving Buildings Energy Performance by Integrating non-Energy Plus Energy Modeling in the Design Stage, Existing Buildings | C: Modeling Integration in Building Retrofit (E) | 3 | Commercial | All End Uses | Total HVAC load in existing commercial buildings | Energy Savings (%) | 7.5% | 0% | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 2013 AIA 2030 Commitment Annual Report (to be published on the AIA website soon) 1) This measure is based on #969, but due to retrofit applications was estimated to be half the benefit of new construction. 2) Modeling improves all areas of building consumption, although currently savings were only applied to HVAC because that's the largest active component and because we don't have good data at this point to partition the savings at a finer granularity.
983 | Commercialize and deploy advanced sequential dual evaporator cycle in residential refrigeration applications. It provides individual cooling needs of freezer and fresh food compartments; uses a single compressor and a three way diverter valve to deliver refrigerant to dual evaporators; improves refrigerator COP by operating the fresh food compartment evaporator at a higher temperatrue and pressure than the freezer compartment evaporator. | R: Sequential Dual Evaporator in Refrigerators | 2 | Residential | Refrigeration | All residential refrigerators and freezers | Energy Savings (%) | 20% | 0% | 0 | 0 | 0 | 0 | 100 | 17 | 17 | 1) Saving and incremental cost from pg. D-20 of DOE BTP Building R&D Breakthroughs: Technologies and Products supported by the Building Technologies Program. April 2012.
986 | UTRC and University of Illinois, Urbana Champaign with funding from DOE in 2013 designed, developed and demonstrated a safe, very low global warming potential, and very high performance air conditioning (VHPAC) residential system. Direct GWP reduction: >350X, one prototype has shown 31% reduction in energy consumpmtion, and 25% reduction in outdoor unit size. | R: Natural Refrigerant AC System | 2 | Residential | Cooling | Total residential cooling (CAC & ASHP) other than room A/Cs | Energy Savings (%) | 30% | 0% | 0 | 0 | 0 | 0 | 451.6313 | 16 | 16 | 1) Energy savings from Y. Feng; P. Verma; J. Wang; F. Zhao, etc. Natural Refrigerant Very High Efficiency Residential AC System. United Technologies Research Center. May 20th, 2013. DOE Award #: DE-EE0003955. http://www.osti.gov/scitech/servlets/purl/1081327 2) Expected incremental costs were not provided in the report. Cost was estimated based on a typcial 3 year payback.
987 | Energy Star Specification in 2010 Residential Electric Heating | R: Energy Star Electric Heating | 3 | Residential | Heating | Total residential electric heating using ASHP | HSPF | 8.2 | 8 | 6450 | 4950 | 6450 | 4950 | 1500 | 15 | 15 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010.
988 | Energy Star Specification in 2010 for Residential Central Air Conditioning | R: Energy Star CAC | 3 | Residential | Cooling | Total energy consumption by residential central air conditioning in single- and multi-family homes | SEER | 14.5 | 13 | 4100 | 3000 | 4100 | 3000 | 1100 | 17 | 17 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010.
989 | Energy Star Specification in 2010 Residential Electric Water Heating | R: Energy Star Electric WH | 3 | Residential | Water Heating | Total electric water heating energy consumption | Energy Factor | 2 | 0.9 | 1850 | 575 | 1850 | 575 | 1275 | 13 | 13 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010.
990 | Energy Star Specification in 2010 Residential Refrigeration | R: Energy Star Refrigeration | 3 | Residential | Refrigeration | All residential refrigerators and freezers | kWh/yr | 408 | 453 | 525 | 500 | 525 | 500 | 25 | 16 | 16 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010.
991 | Residential Electric Dryer (No Energy Star Spec in 2010, only 2015. Took high performance for 2010.) | R: Energy Star Electric Dryer (2015) | 3 | Residential | Washing & Drying | Total energy use by all electric clothes dryers | lb/kWh | 3.16 | 3.01 | 750 | 550 | 750 | 550 | 200 | 12 | 12 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010.
992 | Energy Star Specification in 2010 Residential Gas Heating (furnaces and boilers) | R: Energy Star Gas Heating | 3 | Residential | Heating | Total residential heating using natural gas furnaces and boilers | AFUE | 0.88 | 0.79 | 3500 | 2900 | 3500 | 2900 | 600 | 15 | 15 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010.
993 | Energy Star Specification in 2010 Residential Gas Water Heating | R: Energy Star Gas WH | 3 | Residential | Water Heating | Total gas water heating energy consumption | Energy Factor | 0.67 | 0.59 | 1245 | 940 | 1245 | 940 | 305 | 13 | 13 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010.
994 | Energy Star Specification in 2010 Commercial Electric Heating | C: Energy Star Electric Heating | 3 | Commercial | Heating | Total commercial ASHP heating | COP | 3.4 | 3.3 | 4.1429 | 3.2857 | 4.1429 | 3.2857 | 1.9048 | 15 | 15 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010.
995 | Energy Star Specification in 2010 Commercial Electric Cooling | C: Energy Star Electric Cooling (RTU+ASHP) | 3 | Commercial | Cooling | Total commercial cooling by RTUs and ASHPs | SEER | 14.5 | 14 | 4.3333 | 3.5476 | 4.3333 | 3.5476 | 0.78571 | 15 | 15 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010.
996 | Energy Star Specification in 2010 Commercial Reach-in Solid-door Refrigerators and Freezers (according to CRE rulemaking solid door is the typical unit) | C: Energy Star Refrigeration and Freezers | 3 | Commercial | Refrigeration | All commercial reach-Ins | kWh/day | 8.5232 | 12.9676 | 4024.3805 | 4009.8068 | 4024.3805 | 4009.8068 | 14.5737 | 15 | 15 | 1) % savings and incremental installed cost was derived from 2011 data from EIA Technology Forecast 2012 for commercial reach-in refrigerators and freezers. Costs and savings were derived using a weighted average based on installed market base.
998 | Energy Star Specification in 2010 for Cooling using Residential Air Source Heat Pumps | R: Energy Star ASHP Cooling | 3 | Residential | Cooling | Total residential cooling using ASHP | SEER | 14.5 | 13 | 6450 | 4950 | 6450 | 4950 | 1500 | 17 | 17 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010.
1011 | Building Energy Management Open Source Software (BEMOSS) platform was developed by Virginia Tech, which has a user interface for three plug-and-play compatible controllers - one each for HVAC, lighting and plug load control. The BEMOSS platform is expected to improve energy efficiency and demand response implementation. | C: BEMOSS (<50,000SF) | 3 | Commercial | All End Uses | All HVAC and lighting energy use in small commercial buildings <50,000 ft | Energy Savings (%) | 30% | 0% | 5.45 | 0 | 5.45 | 0 | 5.45 | 10 | 10 | 1) Energy reduction estimate of approximately 30% - this is the sum of all the EUI reductions shown on page 104 of the "Status Update" document, which simulated the effect of advanced control options in small EPlus offices. 2) Installed cost: the "SmallMediumBuildingControlsScopingStudy" document gives two estimates on page 48-49 which would yield a 3 and 5 year payback for an owner. We used the one associated with the 20,000 square feet commercial building (5 year payback), to be consistent with the energy savings estimate. This is listed as $109,000 (or $5.45/sf).
1012 | CRADA with Hill Phoenix: Transcritical CO2 Market Refrigeration System (Advansor System) | C: Transcritical CO2 Refrigeration System | 3 | Commercial | Refrigeration | All supermarket refrigeration systems (cond, comp, walk-ins, & display) | Energy Savings (%) | 25% | 0% | 0 | 0 | 0 | 0 | 628008 | 12 | 12 | 1) Energy Savings: 25% from High Efficiency Low Emission Refrigeration System. 2014 BTO Peer Review Presentation. ORNL. From Tony Bouza: Developed prototype system (CO2 transcritical booster) and fabricated prototype refrigeration system. CRADA partner (Hill Phoenix) plans to deploy low emission, high efficiency systems in 2014 (Potential for transcritical CO2 system: 39% more efficient and 78% less emissions than baseline systems). 2) No cost data. Incremental cost was calculated based on a 5 year simple payback.
1013 | Engine Driven Heat Pump in commercial buildings. This measure is similar to #680, except it's performance is based on NextAire Packaged Gas Heat Pump developed by IntelliChoice Energy, with assistance from Southwest Gas Corporation and ORNL, commercialized in 2010. | C: NextAire Engine Driven HP (FS to gas) | 3 | Commercial | Heating & Cooling | Total commercial electric heating and proportion of cooling in buildings with electric heating | COP | 1.3 | 3.2 | 18.8 | 9.4 | 18.8 | 9.4 | 9.4 | 15 | 15 | 1) COP performance of 1.4 for heating and 1.1 for cooling from Buildings R&D Breakthroughs: Technologies and Products Supported by the BTP. may 2011. Page C-8. NextAire Packaged Gas Heat Pump. 2) Cost data is based on measure #680 ( Omar Abdelaziz. Oak Ridge National Laboratory. 2011. Personal communicationBaseline cost from RS Means Assemblies Cost Data, 33rd Edition ($9.4/ft2 for twenty single-zone RTUs, 2 tons each, including ductwork and controls)
1014 | Energy Star Specification in 2010 for Cooling using Residential Geothermal Heat Pumps | R: Energy Star GSHP Cooling | 3 | Residential | Cooling | Total residential cooling using GSHP | EER | 16.1 | 13.4 | 11000 | 10000 | 11000 | 10000 | 1000 | 25 | 25 | 1) % savings, incremental installed cost, and lifetime from EIA Technology Forecast 2010.
1015 | Energy Star Specification in 2010 for Heating using Residential Geothermal Heat Pumps | R: Energy Star GSHP Heating | 3 | Residential | Heating | Total residential heating using GSHP | COP | 3.5 | 3.1 | 11000 | 10000 | 11000 | 10000 | 1000 | 25 | 25 | 1) % savings, incremental installed cost, and lifetime from EIA Technology Forecast 2010.
1016 | Energy Star Specification in 2010 Residential LPG Heating (furnaces and boilers) | R: Energy Star LPG Furnace | 3 | Residential | Heating | Total residential heating using LPG furnaces or other LPG heating equipment | AFUE | 0.88 | 0.79 | 3500 | 2900 | 3500 | 2900 | 600 | 15 | 15 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010.
1017 | Energy Star Specification in 2010 Residential Solar with Electric Back-Up Water Heating | R: Energy Star Solar WH, Electric BU | 3 | Residential | Water Heating | Total electric water heating energy consumption | Solar Fraction (SF) | 0.5 | 1 | 8800 | 575 | 8800 | 575 | 8225 | 13 | 13 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010.
1018 | Energy Star Specification in 2010 Residential Solar with Gas Back-Up Water Heating | R: Energy Star Solar WH, Gas BU | 3 | Residential | Water Heating | Total gas water heating energy consumption | Solar Fraction (SF) | 0.5 | 1 | 8800 | 940 | 8800 | 940 | 8225 | 13 | 13 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010.
1019 | Residential Energy Star Clothes Washer 2010 Specifications for machine energy use and hot water energy consumption | R: Energy Star CW (machine+hot water) | 3 | Residential | Washing & Drying | Total residential clothes washer and its water heating energy use | Energy Usage, kWh/yr | 0.5 | 1 | 725 | 500 | 725 | 500 | 225 | 11 | 11 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010.
1020 | Residential Energy Star 2010 Dishwasher for machine energy use and hot water energy consumption | R: Energy Star DW (machine+hot water) | 3 | Residential | Dishwashing | All residential dishwashing and its water heating energy use | Energy Usage, kWh/yr | 324 | 355 | 800 | 350 | 800 | 350 | 450 | 19 | 19 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010.
1021 | Increase deployment of Energy Star 2011 CFL Reflectors for residential lighting in place of incandescents and halogen reflectors | R: Energy Star CFL Reflectors | 5 | Residential | Lighting | Total residential incandescent and halogen reflector lighting | lumens/watt | 40 | 10.5561 | 8.83 | 22.1569 | 8.83 | 22.1569 | -13.3269 | 6.6 | 2 | 1) 2010 U.S. Lighting Market Characterization; 2012 Energy Savings Potential of SSL 2) Daily operating hours from the PNNL: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/2012_residential-lighting-study.pdf
1025 | Increase deployment of Energy Star commercial gas ovens | C: Energy Star Gas Oven | 5 | Commercial | Cooking | All commercial natural gas ovens | Energy Savings (%) | 16% | 0% | 0 | 0 | 0 | 0 | 0 | 33 | 10 | 1) % energy savings and incremental cost from ENERGY STAR Qualified Commercial Kitchen Equipment Savings Calculator (Excel file). Retrieved from: http://www.energystar.gov/products/certified-products/detail/commercial-ovens
1026 | Increase deployment of Energy Star commercial electric ovens | C: Energy Star Electric Oven | 5 | Commercial | Cooking | All commercial electric ovens | Energy Savings (%) | 16% | 0% | 0 | 0 | 0 | 0 | 0 | 33 | 10 | 1) % energy savings and incremental cost from ENERGY STAR Qualified Commercial Kitchen Equipment Savings Calculator (Excel file). Retrieved from: http://www.energystar.gov/products/certified-products/detail/commercial-ovens
Note on C1: Key: Buildings: (N): This measure is applicable only to new homes or buildings constructed after the technology or measure penetrates its market. (E): This measure is applicable only to existing homes or buildings constructed prior to 2010. Markets: C: Commercial R: Residential I: Industrial O: Outdoor Other: FS: Fuel Switching MYP: BTO Multi-Year Plan target * - target

## Response List (hidden)
Deployment Level Criteria: | Fuel Selection / Fuel Switching Option
<Please select from the list> | <Please select from the list>
0: Roadmap Goal / Target | 1 C/R: No FS: All electric to all electric
1: Early R&D: not basic science, but still lab bench | 2 C/R: No FS: All gas to all gas
2: Late R&D: cost reduction, performance improvement, may be available to early adopters | 3 C/R: FS: All electric to all gas
3: Early Deployment: savings not yet proven in whole building context | 4 C/R: FS: All gas to all electric
4: Late Deployment: savings proven, but need to transform the market | 5 R: No FS: All fuels HVAC (heating+cooling, no separate ventilation component)
5: Standards: rule in place, underway, or ready to be planned. | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation)
7 C: No FS: All fuels heating and cooling
Sector | 8 R: No FS: All fuels heating
<Please select from the list> | 9 C: No FS: All fuels heating
Commercial | 10 C: No FS: All fuels cooling (elec+NG)
Residential | 11 C: No FS: Boiler heating (elec+NG+oil)
Industrial | 12 C: No FS: gas heating and electric cooling (RTU)
Outdoor | 13 R: No FS: HVAC and lighting
Commercial & Residential | 14 C: No FS: HVAC and lighting
Commercial & Industrial | 15 C: FS: All fuel cooling (elec+gas) to all electric
Commercial/Industrial/Outdoor | 16 R: FS: All non-electric heating, non-electric WH and CAC in homes with electric heating switch to electric
Commercial/Residential/Industrial | 17 R: FS: All non-electric heating, non electric WH and CAC in homes with electric heating switch to natural gas
Commercial/Industrial/Outdoor/Residential | 18 C: FS: All non-electric heating, proportion of cooling and hot water in buildings with non-electric heating switch to electric
19 C: FS: All non-electric heating, proportion of cooling and hot water in buildings with non-electric heating switch to natural gas
20 R: FS: All non-electric heating, proportion of cooling switch to electric
Component | 21 C: FS: All non-electric heating, proportion of cooling switch to electric
<Please select from the list> | 22 R: FS: All non-electric heating, proportion of cooling switch to natural gas
System | 23 C: FS: All non-electric heating, proportion of cooling switch to natural gas
Use Intensity | 24 R: FS: Non-electric, Non-NG heating, proportion of cooling to electric
Maintenance | 25 R: FS: NG heating, proportion of cooling of homes with NG heating to electric
Standby | 26 C: FS: Electric heating, electric cooling, and hot water in buildings with electric heating to all electric
Parasitic | 27 R: FS: Non electric heating, central cooling, and all water heating to electric
Whole Building | 28 R: No FS: Window conduction specific
Controls | 29 R: No FS: Window radiation specific
Windows | 30 R: No FS: Window (cond+rad) specific
Walls | 31 C: No FS: Window conduction specific
Roof | 32 C: No FS: Window radiation specific
Basement | 33 C: No FS: Window (cond+rad) specific
Doors | 34 R: No FS: Wall specific
Infiltration | 35 C: No FS: Wall specific
Distribution | 36 R: No FS: Roof specific
Lamp | 37 C: No FS: Roof specific
Ballasts | 38 R: No FS: Foundation specific
Luminaire | 39 C: No FS: Foundation specific
Compressor | 40 R: No FS: Infiltration specific
Condenser | 41 C: No FS: Infiltration specific
Evaporator | 42 R: No FS: Wall and infiltration specific
Heat Exchanger | 43 C: No FS: Wall and infiltration specific
Thermal Transfer | 44 R: No FS: Wall and foundation specific
Heat Loss (non-Envelope) | 45 C: No FS: Wall and foundation specific
Computer | 46 R: No FS: Door specific
Sprayer | 47 R: No FS: All fuels WH to all fuels WH
Motor | 48 C: No FS: All fuels WH to all fuels WH
Spin Cycle | 49 R: No FS: LPG and distillate WH
Other | 50 R: No FS: Dishwashing and its associated water heating energy use
51 R: No FS: All clothes dryer (elec+NG) to all clothes dryer (elect+NG)
End-Use | 52 C: No FS: All clothes dryer (elec+NG) to all clothes dryer (elect+NG)
<Please select from the list> | 53 C: FS: All clothes dryers (elec+NG) to all electric energy use
All usage | 54 R: No FS: Total clothes washing, clothes drying and water heating energy
Building | 55 C: No FS: Dry Cleaning Energy Use
Cooking | 56 R: No FS: All fuels cooking
Cooling | 57 C: No FS: All fuels cooking
Cooling & Water Heating | 58 C: All electric and gas griddles
Dishwashing | 59 R: No FS: All fuels/end-uses
Heating | 60 C: No FS: All fuels/end-uses
Heating & Coolings | 61 Manual
Heating & Cooling & Water
HVAC
Lighting
MELs
Refrigeration
Ventilation
Washing & Drying
Water Heating
Water Heating & Heating
Whole Building
Market Source
<Please select from the list>
AEO 2014 NEMS
AEO 2010 NEMS
Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
Other, please specify and provide source below:
Market Selection Options:
0
1
New measure?
<Please select from the list>
New measure
Edits to an existing measure
New market?
<Please select from the list>
Yes
No
Note on J30: Oxana Petritchenko: It's not clear what's wrong with this one… Reviewed, seems reasonable.

## GhostForm (hidden)
Building Technologies Program
Prioritization Tool Measure Update or Addition Request Form
Please use this form to submit updates, changes and literature references for measures provided in the RFI or to provide information for new measures for the Pritoritization Tool analysis.
Please fill in the blue field with a measure number of interest. This will auto-populate the remaining fields in this form and in the Market Definition form based on existing data in the Prioritization Tool. If you wish to make changes to the data, make the change in the associated cell. You will notice the cell with updated data will turn red. Please provide a literature source that was used to recommend the change. If you are providing information for a new measure, you may use the information provided for an existing measure as a reference to help you fill out the required data in this form.
Grey fields are optional.
Measure/Technology Description
Measure number: | 890
Brief measure title: | C: Grey-Water HPWH*
Detailed description of measure (max. 200 characters): | A grey-water-source heat pump water heater can greatly reduce WH energy consumption when replacing a standard electric stoarage WH with 54kW capacity and thermal efficiency of 98%, especially in commercial buildings that have high WH loads (restaurants, laundromats, hotels, etc.) by recovering heat in grey water replacing electric storage WH via a water-to-water heat pump. Assume no impact on space heating and cooling of this measure.
Deployment Level: | 0: Roadmap Goal / Target
End-use: | Water Heating
Component: | System
Comments:
Market Characteristics
Sector(s): | Commercial
Market targeted: | Total energy consumption by all commercial electric storage water heaters
Fuel Selection / Fuel Switching Option | 1 C/R: No FS: All electric to all electric
If another market is targeted, full market description (if relevant, include equipment class, building type (new, existing, all), region, climate zones, etc.):
Market data source(s): | AEO 2010 NEMS
If other, suggested market data source(s):
Year of market entry (based of target cost or performance): | 2016
Comments:
Measure/Technology Performance
Energy consumption or efficiency of a baseline unit: | 0.92
Measure's improvement in energy consumption or efficiency over the baseline unit: | 2.4
Units: | Energy Factor
Lifetime of a baseline unit (years): | 13
Lifetime of new measure (years): | 13
Data source(s): | 1) Baseline unit performance: Assuming roughly the same EF as a residential gas-fired storage WH for standard unit (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment) 2) Efficient unit performance: Assuming roughly the same performance as a ground-source heat pump, 3.5 COP (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) -Converting to 2.4 EF using a 0.698 conversion factor which accounts for differences between lab rating and typical field performance (Source: Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007)) 3) Baseline unit cost: Average installed cost for a 54 kW electric storage WH is $5,430 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) 4) Efficient unit cost: TARGET Installed Cost -Assuming a 48kBtu/Hr ground-source heat pump has a retail equipment cost of $7,000 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) -Assuming roughly 30% of that cost represents the water-to-air heat pump gives a cost of $2,100 (Source: COST CONTAINMENT FOR GROUND-SOURCE HEAT PUMPS, S. Kavanaugh, http://geoheat.oit.edu/pdf/tp72.pdf) -Assuming that the water-to-air heat pump is a reasonable proxy for a water-to-water heat pump and scaling this cost up to 200,000 kBtu/Hr capacity gives a cost of $8,750, and adding 40% for installation gives $12,250 -Assuming a 25% cost reduction for improved design results in a target installed cost of roughly $9,200
Comments:
Measure/Technology Cost*
Market cost of a baseline unit: | 5430
Market cost of new measure: | 9200
Incremental cost: | 3770
Units (e.g., $/sq. ft., $/unit): | per unit
Data source(s): | 1) Baseline unit performance: Assuming roughly the same EF as a residential gas-fired storage WH for standard unit (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment) 2) Efficient unit performance: Assuming roughly the same performance as a ground-source heat pump, 3.5 COP (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) -Converting to 2.4 EF using a 0.698 conversion factor which accounts for differences between lab rating and typical field performance (Source: Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007)) 3) Baseline unit cost: Average installed cost for a 54 kW electric storage WH is $5,430 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) 4) Efficient unit cost: TARGET Installed Cost -Assuming a 48kBtu/Hr ground-source heat pump has a retail equipment cost of $7,000 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) -Assuming roughly 30% of that cost represents the water-to-air heat pump gives a cost of $2,100 (Source: COST CONTAINMENT FOR GROUND-SOURCE HEAT PUMPS, S. Kavanaugh, http://geoheat.oit.edu/pdf/tp72.pdf) -Assuming that the water-to-air heat pump is a reasonable proxy for a water-to-water heat pump and scaling this cost up to 200,000 kBtu/Hr capacity gives a cost of $8,750, and adding 40% for installation gives $12,250 -Assuming a 25% cost reduction for improved design results in a target installed cost of roughly $9,200
Comments:
*Please attempt to provide costs at large-scale market adoption price.
Note on B26: If a different market is necessary/preferred for a given measure, please use the market definition form in this workbook to define the market.
Note on B48: Incremental cost is the difference between market cost of a new measure and its baseline unit.

## Database (hidden)
Measure no. | Description | Brief description | Component | Data quality | R&D/ Deployment/ Standards | Sector | End-Use | Device | Market targeted | Efficiency Units | Efficient Operation | Baseline operation | Reduces service demand | Market Cost (as defined in the source) | Market cost (per standard unit) if needed | Market cost (per efficient unit, at scale) | Incremental measure cost | Stock Unit Definition | Fuel Composition/Switching | Targeted Market | Expected Lifetime of Baseline Unit | Min year on market | Source | Notes | Market # | Expected Lifetime of Baseline Unit | Expected Lifetime of Baseline Unit | Market Source
1 | Use most cost effective insulation in new commercial gas and electric fryers | C: Fryers - improved insulation | Use Intensity | 5 | 3 | Commercial | Cooking | Fryer | Gas and Electric | Energy Savings (%) | 7% | 0% | Yes | Not availalble |  |  |  | per unit | 61 Manual | All commercial electric and gas fryers | 12 | 2010 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. Other Supporting Sources: Cost data are from google searches of commercially available appliances | Appendix B: Page 51, Table 2-42 | 3-3409 | 12 | 12 | AEO 2010 NEMS
2 | Use most cost effective insulation in new commercial gas and electric griddles | C: Improved Insulation in Griddles | Use Intensity | 5 | 3 | Commercial | Cooking | Griddle | Gas and Electric | Energy Savings (%) | 7% | 0% | Yes | Not availalble |  |  |  | per unit | 58 C: All electric and gas griddles | All commercial electric and gas griddles | 22 | 2010 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. | Appendix B: Page 51, Table 2-42 | 3-3408 | 22 | 22 | AEO 2010 NEMS
5 | Increase deployment of more efficient commercial gas connectionless steamers | C: Gas Connectionless Steamer | System | 5 | 5 | Commercial | Cooking | Steamer | Gas | Energy Savings (%) | 73% | 0% | No | 3700 |  |  | 3700 | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas steamers | 10 | 2010 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. | BTO Tool: Incremental Cost. 3.8 year payback period. Appendix B: Page 56: Table 2-48 and Page 56: Table 2-49 | 3-3407 | 10 | 10 | AEO 2010 NEMS
6 | Increase deployment of more efficient commercial electric connectionless steamers | C: Electric Connectionless Steamer | System | 5 | 5 | Commercial | Cooking | Steamer | Electric | Energy Savings (%) | 73% | 0% | No | 2500 |  |  | 2500 | per unit | 1 C/R: No FS: All electric to all electric | All commercial electric steamers | 10 | 2010 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. | BTO Tool: Incremental Cost. 2.7 year payback period. Appendix B: Page 56: Table 2-48 and Page 56: Table 2-49 | 3-3399 | 10 | 10 | AEO 2010 NEMS
7 | Increase deployment of more efficient commercial gas ovens | C: Gas Oven | System | 5 | 5 | Commercial | Cooking | Oven | Gas | Energy Savings (%) | 29.09% | 0% | No | 0 |  |  | 0 | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas ovens | 10 | 2010 | ENERGY STAR (n.d.). Savings Calculator for ENERGY STAR Qualified Commercial Kitchen Equipment. Retrieved from: http://www.energystar.gov/ia/business/bulk_purchasing/bpsavings_calc/commercial_kitchen_equipment_calculator.xls?ba38-b08e | BTO Tool: $0 more for energy efficient compared to standard Appendix B: Using indicated spreadsheet Enter "1" for gas oven: "results summary" tab shows energy savings and cost | 3-3405 | 10 | 10 | AEO 2010 NEMS
8 | Increase deployment of more efficient commercial electric convection ovens | C: Convection Ovens | System | 5 | 5 | Commercial | Cooking | Oven | Electric | Energy Savings (%) | 15.41% | 0% | No | 800 |  |  | 800 | per unit | 1 C/R: No FS: All electric to all electric | All commercial electric ovens | 10 | 2010 | EnergyStar | BTO Tool: $800 more for energy efficient compared to standard | 3-3397 | 10 | 10 | AEO 2010 NEMS
11 | Improve electric ignition reliability for commercial gas cooking appliances | C: Gas Cooking Elec. Ignition | Parasitic | 5 | 2 | Commercial | Cooking | Fryer, Griddle, Oven, Broilers, Range, Steamer | Gas | Energy Savings (%) | 3.555% | 0% | No | See incremental cost |  |  | 100 | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas cooking | 10 | 2018 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. | Appendix B: Page 53, Table 2-46 and Page 54, Table 2-47 | 3-3401 | 10 | 10 | AEO 2010 NEMS
14 | Commercial lighting: troffers 1-to-1 replacement (2x4,2x2,1x4) | C: LED Troffers | Luminaire | 5 | 4 | Commercial | Lighting | Luminaire | All Troffers | lumens/watt | 95 | 74 | Yes | Standard and efficient unit costs are first costs; incremental cost includes relamping an maintenance calculations. | 97.5 | 498.05 | 358.05 | per luminaire | 1 C/R: No FS: All electric to all electric | All commercial troffers | 5 | 2013 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 3-3467 | 5 | 12 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
15 | Commercial lighting: troffers 1-to-1 replacement (2x4,2x2,1x4) with added controls | C: LED Troffers + Ctrls | Luminaire | 5 | 4 | Commercial | Lighting | Luminaire | All Troffers | lumens/watt | 109 | 74 | Yes | Standard and efficient unit costs are first costs; incremental cost includes relamping an maintenance calculations. | 97.5 | 648.05 | 508.05 | per luminaire | 1 C/R: No FS: All electric to all electric | All commercial troffers | 5 | 2013 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 3-3467 | 5 | 12 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
16 | Replace metal halide parking lot lighting with LEDs | O: Parking Lot LEDs | Luminaire | 5 | 4 | Outdoor | Lighting | Luminaire | MH in Parking lots | lumens/watt | 83 | 60 | Yes | Standard and efficient unit costs are first costs; incremental cost includes relamping an maintenance calculations. | 240 | 478 | -5.6 | per luminaire | 1 C/R: No FS: All electric to all electric | All metal halide lighting in parking lots | 4 | 2013 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 3-3468 | 4 | 11 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
18 | Increase deployment of more efficient commercial gas fryers | C: Gas Fryers | System | 5 | 5 | Commercial | Cooking | Fryer | Gas | Energy Savings (%) | 31.02% | 0% | No | 4113 | 2894 | 4113 | 1219 | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas fryers | 12 | 2010 | EnergyStar Primary Source: Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. Other Supporting Sources: Cost data are from google searches of commercially available appliances | BTO Tool: Compares to $2894 conventional Appendix B: Page 376, Table A-17 and A-18 | 3-3403 | 12 | 12 | AEO 2010 NEMS
19 | Increase deployment of more efficient commercial electric fryers | C: Electric Fryers | System | 5 | 5 | Commercial | Cooking | Fryer | Electric | Energy Savings (%) | 6.48% | 0% | No | 275 |  |  | 275 | per unit | 1 C/R: No FS: All electric to all electric | All commercial electric fryers | 12 | 2010 | ENERGY STAR (n.d.). Savings Calculator for ENERGY STAR Qualified Commercial Kitchen Equipment. Retrieved from: http://www.energystar.gov/ia/business/bulk_purchasing/bpsavings_calc/commercial_kitchen_equipment_calculator.xls?ba38-b08e | BTO Tool: $275 more for energy efficient compared to standard Appendix B: Using indicated spreadsheet Enter "1" for gas oven: "results summary" tab shows energy savings and cost | 3-3395 | 12 | 12 | AEO 2010 NEMS
23 | Standard Max Tech ASHP (FS only) | R: Max Tech ASHP (FS) | System | 5 | 0 | Residential | Heating & Cooling | Heat pump | All | Energy Savings (%) | 40.77% | 0% | Yes | See existing & efficient costs | 3330 | 4508 | 1178 | per unit | 20 R: FS: All non-electric heating, proportion of cooling switch to electric | All non-electric heating, proportion of cooling | 15 | 2015 | Hewitt et.al. demonstrates high COP; cost represnts road map target Primary Source: Hewitt, N.J., Huang, M.J., Anderson, M. & Quinn, M. Advanced air source heat pumps for UK and European domestic buildings. Applied Thermal Engineering 31, 3713-3719 (2011); ASHP TSD | Appendix B: Savings and cost targets reflect Building Technology Program funded targets; Hewitt et.al. demonstrate technical feasibility Single Package HP, 16.5 SEER National Average: $4866 Split System HP, 22 SEER National Average: $4149 Use Average: $4508 (instead of current cost of $5800) ASHP FS measure, Std Unit market cost changed from $3330 to $1079 (pulled from measure 695); ASHP no FS measure, Std Unit market cost changed from $4680 to $552 (pulled from measure 694) | 1-97 | 15 | 15 | AEO 2014 NEMS
24 | Increase deployment of more efficient commercial gas griddles | C: Gas Griddle | System | 5 | 5 | Commercial | Cooking | Griddle | Gas | Energy Savings (%) | 12.25% | 0% | No | 800 |  | 800 | 800 | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas griddles | 22 | 2013 | LBNL 2008 Primary Source: ENERGY STAR (n.d.). Savings Calculator for ENERGY STAR Qualified Commercial Kitchen Equipment. Retrieved from: http://www.energystar.gov/ia/business/bulk_purchasing/bpsavings_calc/commercial_kitchen_equipment_calculator.xls?ba38-b08e | BTO Tool: $800 more for energy efficient compared to standard Appendix B: Enter "1" for Gas Griddle and tab over to the "results summary" tab for the energy savings and cost | 3-3404 | 22 | 22 | AEO 2010 NEMS
25 | Increase deployment of more efficient commercial electric griddles | C: Electric Griddle | System | 5 | 5 | Commercial | Cooking | Griddle | Electric | Energy Savings (%) | 11.06% | 0% | No | 800 |  | 800 | 800 | per unit | 1 C/R: No FS: All electric to all electric | All commercial electric griddles | 22 | 2013 | LBNL 2008 Primary Source: ENERGY STAR (n.d.). Savings Calculator for ENERGY STAR Qualified Commercial Kitchen Equipment. Retrieved from: http://www.energystar.gov/ia/business/bulk_purchasing/bpsavings_calc/commercial_kitchen_equipment_calculator.xls?ba38-b08e | BTO Tool: $800 more for energy efficient compared to standard Appendix B: Enter "1" for electric Griddle and tab over to the "results summary" tab for the energy savings and cost | 3-3396 | 22 | 22 | AEO 2010 NEMS
26 | Early replacement of residential gas cook top with induction | R: Induction cooktop (FS) | Thermal transfer | 5 | 4 | Residential | Cooking | Range | Gas | Energy Savings (%) | 70.1% | 0% | No | 2000 | 0 | 1999 | 1999 | per unit | 4 C/R: FS: All gas to all electric | Total residential cooking energy consumption using natural gas stove | 17 | 2013 | Electrolux Appliances, http://www.electroluxappliances.com/kitchen-appliances/cooktops/induction/ew30ic60is; for payback period use EnergyStar oven assumptions with cost differential between gas and induction cook top | BTO Tool: Compares to $1199 for gas cook top, also 30" | 1-7 | 17 | 17 | AEO 2014 NEMS
28 | National campaign for residential desktop users to employ energy saving settings | R: Desktop Power Management | Computer | 5 | 4 | Residential | MELs | Desktop PCs | All | Energy Savings (%) | 44% | 0% | Yes | Negligible (incremental) |  |  | 0 | per unit | 1 C/R: No FS: All electric to all electric | Total energy use by residential desktop PCs | 4 | 2013 | TIAX 2007, 2004 Primary Source: Roth, K.W., Mckenney, K., Ponoum, R. & Paetsch, C. Residential Miscellaneous Electric Loads: Energy Consumption Characterization and Savings Potential. Energy 197 (2007). Other Supporting Sources: Cost data are from google searches of commercially available appliances | Appendix B: Page 4-31, last sentence. | 1-40 | 4 | 4 | AEO 2014 NEMS
29 | National campaign for residential notebook users to employ energy saving settings | R: Laptop Power Management | Use Intensity | 5 | 4 | Residential | MELs | Notebook PCs | All | Energy Savings (%) | 28% | 0% | Yes | Negligible (incremental) |  |  | 0 | per unit | 1 C/R: No FS: All electric to all electric | Total energy use by residential and commercial notebook PCs | 4 | 2013 | TIAX 2007, 2004 Primary Source: Roth, K.W., Mckenney, K., Ponoum, R. & Paetsch, C. Residential Miscellaneous Electric Loads: Energy Consumption Characterization and Savings Potential. Energy 197 (2007). Other Supporting Sources: Cost data are from google searches of commercially available appliances | Appendix B: Page 4-31, last sentence. | 1-72 | 4 | 4 | AEO 2014 NEMS
30 | Heat pipe griddle | C: Heat Pipe Griddle | Use Intensity | 5 | 3 | Commercial | Cooking | Griddle | Gas | Energy Savings (%) | 4.3% | 0% | No | Not availalble |  |  |  | per unit | 58 C: All electric and gas griddles | All commercial electric and gas griddles | 22 | 2013 | 1. Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. 2. http://www.accutemp.net/accu-steam_main.htm | Appendix B: Page 377, Table A-20 | 3-3408 | 22 | 22 | AEO 2010 NEMS
33 | Increase deployment of high efficiency motors in food preparation | C: Food Prep Motor | Use Intensity | 5 | 5 | Commercial | Cooking | Food Preparation | Electric | Energy Savings (%) | 2.2% | 0% | No | Not availalble |  |  |  | per unit | 1 C/R: No FS: All electric to all electric | All commercial food preparation appliances energy use | 12 | 2013 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. | Appendix B: Page 78, Table 3-9 | 3-3452 | 12 | 12 | AEO 2010 NEMS
34 | Stock Pot Heat Transfer Fins | C: Stock Pot Heat Transfer Fins | Use Intensity | 5 | 3 | Commercial | Cooking | Range | Gas | Energy Savings (%) | 5% | 0% | Yes | Not availalble |  |  |  | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas griddles | 10 | 2013 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. | Appendix B: Page 56: Table 2-48 | 3-3404 | 10 | 10 | AEO 2010 NEMS
35 | Increase deployment of commercial electric ovens | C: Electric Oven | System | 5 | 5 | Commercial | Cooking | Oven | Electric | Energy Savings (%) | 39% | 0% | No | 8325 | 4500 | 8325 | 3825 | per unit | 1 C/R: No FS: All electric to all electric | All commercial electric ovens | 10 | 2013 | LBNL 2008, U.S. Building-Sector Energy Efficiency Potential Primary Source: ENERGY STAR (n.d.). Savings Calculator for ENERGY STAR Qualified Commercial Kitchen Equipment. Retrieved from: http://www.energystar.gov/ia/business/bulk_purchasing/bpsavings_calc/commercial_kitchen_equipment_calculator.xls?ba38-b08e | BTO Tool: Compares to $4500 conventional Appendix B: Enter "1" for electric oven and tab over to the "results summary" tab for the energy savings and cost | 3-3397 | 10 | 10 | AEO 2010 NEMS
36 | Increase deployment of more efficient commercial gas ranges | C: Gas Range | System | 5 | 5 | Commercial | Cooking | Range | Gas | Energy Savings (%) | 25% | 0% | No | 4830 | 3000 | 4830 | 1830 | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas ranges | 10 | 2013 | LBNL 2008, U.S. Building-Sector Energy Efficiency Potential Primary Source: Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. Other Supporting Sources: Cost data are from google searches of commercially available appliances | BTO Tool: Compares to $3000 conventional Appendix B: Page 51: "Insulation at major heat loss locations in cooking appliances can reduce standby heat loses by 25% in both electric and gas powered models" | 3-3406 | 10 | 10 | AEO 2010 NEMS
37 | Increase deployment of more efficient commercial electric ranges | C: Electric Range | System | 5 | 5 | Commercial | Cooking | Range | Electric | Energy Savings (%) | 24% | 0% | No | 7400 | 4000 | 7400 | 3400 | per unit | 1 C/R: No FS: All electric to all electric | All commercial electric ranges | 10 | 2013 | LBNL 2008, U.S. Building-Sector Energy Efficiency Potential Primary Source: Brown, R., Borgeson, S., Koomey, J. & Biermayer, P. U . S . Building-Sector Energy Efficiency Potential. Environmental Protection 33 (2008). | BTO Tool: Compares to $4000 conventional Appendix B: Page 8, Table 5. Cost is $7,400 - $4,000 = $3,400 | 3-3398 | 10 | 10 | AEO 2010 NEMS
38 | Increase deployment of more efficient commercial gas steam cookers | C: Gas Steamer | System | 5 | 5 | Commercial | Cooking | Steamer | Gas | Energy Savings (%) | 43% | 0% | No | 10500 | 10500 | 10500 | 0 | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas steamers | 10 | 2013 | LBNL 2008, U.S. Building-Sector Energy Efficiency Potential Primary Source: Brown, R., Borgeson, S., Koomey, J. & Biermayer, P. U . S . Building-Sector Energy Efficiency Potential. Environmental Protection 33 (2008). | BTO Tool: Same price as conventional Appendix B: Page 11, Table 6 | 3-3407 | 10 | 10 | AEO 2010 NEMS
39 | Increase deployment of more efficient commercial electric steam cookers | C: Electric Steamer | System | 5 | 5 | Commercial | Cooking | Steamer | Electric | Energy Savings (%) | 57% | 0% | No | 10000 | 10000 | 10000 | 0 | per unit | 1 C/R: No FS: All electric to all electric | All commercial electric steamers | 10 | 2013 | LBNL 2008, U.S. Building-Sector Energy Efficiency Potential Primary Source: Brown, R., Borgeson, S., Koomey, J. & Biermayer, P. U . S . Building-Sector Energy Efficiency Potential. Environmental Protection 33 (2008). | BTO Tool: Same price as conventional Appendix B: Page 8, Table 5 | 3-3399 | 10 | 10 | AEO 2010 NEMS
41 | Reduce idle use in commercial gas broilers | C: Idle Energy Reduction in Gas Broilers | Use Intensity | 5 | 3 | Commercial | Cooking | Broilers | Gas | Energy Savings (%) | 26% | 0% | Yes | Not availalble |  |  |  | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas broilers | 10 | 2013 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. | BTO Tool: Full size, operating 15 hrs/day Appendix B: Page 56, Table 2-48 | 3-3402 | 10 | 10 | AEO 2010 NEMS
42 | Eliminate idle energy use in new residential microwaves | R: Microwave: Deploy 0W Standby | Parasitic | 5 | 4 | Residential | Cooking | Microwave | Electric | Energy Savings (%) | 20% | 0% | Yes | See incremental cost |  |  | 1 | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by residential microwaves | 9 | 2013 | TIAX LLC 2007, Residential Misc Electric Loads http://www.iepec.org/TIAX_MiscElecLoadsReportToDOE.pdf | No notes | 1-76 | 9 | 9 | AEO 2014 NEMS
44 | Deploy improved magnetrons in new residential microwaves | R: Microwaves - Improve magnetron efficiency | Thermal transfer | 5 | 4 | Residential | Cooking | Microwave | Electric | Magnetron efficiency | 75% | 71% | No | See incremental cost |  |  | 15 | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by residential microwaves | 9 | 2014 | LBNL 1998 TSD, active 80% of energy consumption: TIAX 2007 | BTO Tool: Incremental cost | 1-76 | 9 | 9 | AEO 2014 NEMS
45 | Deploy improved power supplies in new residential microwaves | R: Microwaves - Improve magnetron power supply efficiency | Parasitic | 5 | 4 | Residential | Cooking | Microwave | Electric | Energy Savings (%) | 2.9% | 0% | Yes | See incremental cost |  |  | 9 | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by residential microwaves | 9 | 2014 | LBNL 1998 TSD, active 80% of energy consumption: TIAX 2007 | BTO Tool: Incremental cost | 1-76 | 9 | 9 | AEO 2014 NEMS
46 | Replace residential gas cook top with induction at end of life | R: Induction Cooktop (FS) | Thermal transfer | 5 | 4 | Residential | Cooking | Range | Gas | Energy Savings (%) | 70% | 0% | No | 2000 | 1199 | 1999 | 800 | per unit | 4 C/R: FS: All gas to all electric | Total residential cooking energy consumption using natural gas stove | 17 | 2010 | Electrolux. (n.d.). 30" Induction Cooktop. Retrieved from http://www.electroluxappliances.com/kitchen-appliances/cooktops/induction/ew30ic60is | BTO Tool: Compares to $1199 for gas cook top, also 30" Appendix B: "Cooking with induction is 70% more efficient than gas..." and MSRP of induction stove is $2,000 | 1-7 | 17 | 17 | AEO 2014 NEMS
47 | Replace residential electric cook top with induction at end of life | R: Induction Cooktop | Thermal transfer | 5 | 4 | Residential | Cooking | Range | Electric | Energy Savings (%) | 20% | 0% | No | 2000 | 1449 | 1999 | 550 | per unit | 1 C/R: No FS: All electric to all electric | Total residential cooking energy consumption using electric stove | 17 | 2010 | Electrolux. (n.d.). 30" Induction Cooktop. Retrieved from http://www.electroluxappliances.com/kitchen-appliances/cooktops/induction/ew30ic60is | BTO Tool: Compares to $1449 for electric cook top, also 30" Appendix B: "Cooking with induction is...20% more efficient than electric." and MSRP of induction stove is $2,000 | 1-8 | 17 | 17 | AEO 2014 NEMS
49 | Move toward replacing conventional burners with infrared burners in new commercial gas fryers | C: Infrared Burners in Fryers | Thermal transfer | 5 | 4 | Commercial | Cooking | Fryer | Gas | Energy Savings (%) | 30% | 0% | No |  |  |  | 750 | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas fryers | 12 | 2010 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. | Appendix B: Page 48, Table 2-33 and Page 49, Table 2-35 | 3-3403 | 12 | 12 | AEO 2010 NEMS
50 | Standardize replacement of conventional burners with infrared burners in new commercial gas broilers | C: Infrared Burners in Broilers | Thermal transfer | 5 | 4 | Commercial | Cooking | Broilers | Gas | Energy Savings (%) | 37% | 0% | No |  |  |  | 1750 | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas broilers | 10 | 2010 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. | Appendix B: Page 48, Table 2-33 and Page 49, Table 2-35 | 3-3402 | 10 | 10 | AEO 2010 NEMS
51 | Standardize replacement of conventional burners with infrared burners in new commercial gas ovens | C: Infrared Burners in Gas Ovens | Thermal transfer | 5 | 4 | Commercial | Cooking | Oven | Gas | Energy Savings (%) | 30% | 0% | No |  |  |  | 1000 | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas ovens | 10 | 2010 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. | Appendix B: Page 48, Table 2-33 and Page 49, Table 2-35 | 3-3405 | 10 | 10 | AEO 2010 NEMS
52 | Demonstrate and deploy infrared burners as replacement to conventional burners in new commercial gas ranges | C: Infrared Burners in Gas Ranges | Thermal transfer | 5 | 4 | Commercial | Cooking | Range | Gas | Energy Savings (%) | 39% | 0% | No |  |  |  | 1700 | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas ranges | 10 | 2010 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. | Appendix B: Page 48, Table 2-33 and Page 49, Table 2-35 | 3-3406 | 10 | 10 | AEO 2010 NEMS
54 | Increase deployment of efficient fans in new residential microwaves | R: Efficient fans in microwaves | Parasitic | 5 | 5 | Residential | Cooking | Microwave | Electric | Energy Savings (%) | 0.23% | 0% | Yes | See incremental cost |  |  | 10 | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by residential microwaves | 9 | 2010 | LBNL 1998 TSD, active 80% of energy consumption: TIAX 2007 | BTO Tool: Incremental cost | 1-76 | 9 | 9 | AEO 2014 NEMS
55 | Increase amount of heat transferred to surfaces in new gas fryers: Use a blower to force a premixed air-fuel mixture into the burner, allowing higher combustion gas temperature to be reached as the fuel mixture contains less excess air | C: Power Burners in Gas Fryers | Thermal transfer | 5 | 3 | Commercial | Cooking | Fryer | Gas | Energy Savings (%) | 31% | 0% | Yes | 500 |  |  | 500 | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas fryers | 12 | 2010 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. | BTO Tool: Incremental cost for Power Burner. 1.9 year payback period Appendix B: Page 49, Table 2-36 and Page 50, Table 2-38 | 3-3403 | 12 | 12 | AEO 2010 NEMS
56 | Increase amount of heat transferred to surfaces in new gas ranges: Use a blower to force a premixed air-fuel mixture into the burner, allowing higher combustion gas temperature to be reached as the fuel mixture contains less excess air | C: Power Burners in Gas Ranges | Thermal transfer | 5 | 3 | Commercial | Cooking | Range | Gas | Energy Savings (%) | 34% | 0% | No | 3000 |  |  | 3000 | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas ranges | 10 | 2010 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. | BTO Tool: Incremental cost for Power Burner. 6.2 year payback period. Assumes 6 burners per range. Appendix B: Page 49, Table 2-36 and Page 50, Table 2-38 | 3-3406 | 10 | 10 | AEO 2010 NEMS
57 | Development, demonstration and deployment of pulse combustion burners in commercial natural gas fryers and griddles | C: Pulse Combustion Burners in Gas Fryers and Griddles | Thermal transfer | 5 | 2 | Commercial | Cooking | Fryer and Griddle | Gas | Energy Savings (%) | 31% | 0% | No | See incremental cost |  |  | 760 | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas fryers and griddles | 22 | 2016 | Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. | Appendix B: Page 377, Table A-18 and Page 51, Table 2-41 | 3-3451 | 22 | 22 | AEO 2010 NEMS
58 | Max tech microwave (combination of other measures) | R: Max tech microwave | System | 5 | 2 | Residential | Cooking | Microwave | Electric | Energy Savings (%) | 20% | 0% | No | See incremental cost |  |  | 55 | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by residential microwaves | 9 | 2015 | TIAX LLC 2007, Residential Misc Electric Loads; LBNL 1998 TSD, active 80% of energy consumption Primary Source: Roth, K.W., Mckenney, K., Ponoum, R. & Paetsch, C. Residential Miscellaneous Electric Loads: Energy Consumption Characterization and Savings Potential. Energy 197 (2007). | BTO Tool: Incremental cost Appendix B: Table 4-32: Theoretical Energy Savings Scenarious for Microwave Ovens | 1-76 | 9 | 9 | AEO 2014 NEMS
60 | Increase deployment of commercial gas steam cookers | C: Gas Steam Cooker | System | 5 | 5 | Commercial | Cooking | Steamer | Gas | Energy Savings (%) | 34.58% | 0% | No | 10568 | 6836 | 10568 | 3732 | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas steamers | 10 | 2010 | EnergyStar | BTO Tool: Compares to $6836 conventional | 3-3407 | 10 | 10 | AEO 2010 NEMS
61 | Increase deployment of commercial electric steam cookers | C: Electric Steam Cooker | System | 5 | 5 | Commercial | Cooking | Steamer | Electric | Energy Savings (%) | 51.16% | 0% | No | 5890 | 3400 | 5890 | 2490 | per unit | 1 C/R: No FS: All electric to all electric | All commercial electric steamers | 10 | 2010 | EnergyStar | BTO Tool: Compares to $3400 conventional | 3-3399 | 10 | 10 | AEO 2010 NEMS
65 | National campaign to improve power management of video game systems in homes | R: Video Game Power Management | Use Intensity | 5 | 4 | Residential | MELs | Video game consoles | All | Energy Savings (%) | 72% | 0% | No | See incremental cost |  |  | 0 | per unit | 1 C/R: No FS: All electric to all electric | Total energy use by residential video game consoles | 5 | 2011 | MTAB Report; Priority Setting Estimates Primary Source: Desroches, L.B., & Garbesi, K. (2011). Max Tech and Beyond. Lawrence Berkeley National Laboratory. | Appendix B: Page 20, Table 3 | 1-86 | 5 | 5 | AEO 2014 NEMS
69 | Demonstrate and deploy indirect evaporative (e.g., Coolerado) A/C in residential homes in mixed-dry and hot-dry climates. "Instead of using chemical refrigerants and compressors to cool recycled interior air, we use a new, patented process that runs fresh outside air through air filters and then a heat mass exchanger (HMX)." | R: Coolerado, mixed/hot-dry CZ | System | 5 | 3 | Residential | Cooling | A/C | Central | Energy Savings (%) | 87.5% | 0% | Yes | $150/kBTU/hr | 6545 | 9230 | 2685 | per home; 5 ton | 1 C/R: No FS: All electric to all electric | Total cooling in mixed-dry and hot-dry climates | 19 | 2013 | Primary Source: Coolerado technical manuals,http://www.coolerado.com/solutions/ , Desroches, L.-B. et al. Max Tech and Beyond. 60 (2011). Dean, Herrmann, etc. NREL. 2012. Dew Point Evaporative Comfort Cooling. http://www.nrel.gov/docs/fy13osti/56256-1.pdf | Appendix B: "Utilizing the Maisotsenko cycle, indirect evaporative coolers can provide approximately 80% energy savings compared to standard vapor-compression air conditioners." Cost and savings taken from manufacturer's website and documentation. Phil stated that Coolerado was excluded from the original UBER list because it is a private company with a specific technology, which makes it out of scope of what BTO can help (i.e., BTO can't choose winners). | 1-18 | 19 | 19 | AEO 2014 NEMS
70 | Demonstrate and deploy indirect evaporative (e.g., Coolerado) A/C in commercial buildings in mixed-dry and hot-dry climates. "Instead of using chemical refrigerants and compressors to cool recycled interior air, we use a new, patented process that runs fresh outside air through air filters and then a heat mass exchanger (HMX)." | C: Coolerado, mixed/hot-dry CZ | System | 5 | 3 | Commercial | Cooling | A/C | Central | Energy Savings (%) | 87.5% | 0% | Yes | $150/kBTU/hr | 4.3633 | 6.1533 | 1.79 | per square foot (~24,000 sq.ft.) | 10 C: No FS: All fuels cooling (elec+NG) | Total cooling in hot, dry climates in all commercial buildings | 15 | 2013 | Coolerado technical manuals, http://www.coolerado.com/solutions/ , Desroches, L.-B. et al. Max Tech and Beyond. 60 (2011) Dean, Herrmann, etc. NREL. 2012. Dew Point Evaporative Comfort Cooling. http://www.nrel.gov/docs/fy13osti/56256-1.pdf | Appendix B: "Utilizing the Maisotsenko cycle, indirect evaporative coolers can provide approximately 80% energy savings compared to standard vapor-compression air conditioners." Cost and savings taken from manufacturer's website and documentation. Phil stated that Coolerado was excluded from the original UBER list because it is a private company with a specific technology, which makes it out of scope of what BTO can help (i.e., BTO can't choose winners). | 3-3667 | 15 | 15 | AEO 2010 NEMS
71 | Research, demonstrate, and deploy advanced liquid desiccant A/C (e.g., DeVAP, DuCool) in homes in mixed humid and hot humid climates | R: DEVAP, humid CZ | System | 5 | 1 | Residential | Cooling | A/C | Central | Energy Savings (%) | -105.3% | 0% | Yes | Either NREL estimte of $6,950 or NREL materials of $2900+30% + 2080 installation + 30 ft of plumbing at $20/ft; UPDATE: Equipment cost of baseline DX system in non-hot/dry climate is $2600; DEVap equipment cost estimate is $8100 | 2600 | 8100 | 5500 | per home, 3 ton unit | 61 Manual | Total residential central cooling in humid climates | 17 | 2017 | Kozubal, E.; Woods, J.; Judkoff, R.; "Development and Analysis of Desiccant Enhanced Evaporative Air Conditioner Prototype"; NREL, 2012. http://www.nrel.gov/docs/fy12osti/54755.pdf Kozubal, E. et. al.; "Desiccant Enhanced Evaporative Air-Conditioning (DEVap): Evaluation of a New Concept in Ultra Efficient Air Conditioning"; NREL, 2011. http://www.nrel.gov/docs/fy11osti/49722.pdf; NCI Internal DeVAP Report Cost (listed value is not consistent with this source: "Rooftop units using DEVAP design are initially expected to cost ~30% more than competing models." Kozubal. NREL. July 2 2012. http://www.nrel.gov/docs/fy12osti/55740.pdf | BTO Tool: MTAB, NREL website, DuCool?AdvantixSystems website; Assume households need both CAC and NG to be suitable for DEVap Appendix B: "Modeling at NREL has shown that the yearly combined source energy for the thermal and electrical energy required to operate DEVap is expected to be 30%–90% less than state-of-the-art direct expansion cooling (depending on whether it is applied in a humid or a dry climate)", NREL research team performed climate and sector specific calculations | 1-9 | 17 | 17 | AEO 2014 NEMS
72 | Research, demonstrate, and deploy advanced liquid desiccant A/C (e.g., DeVAP, DuCool) in commercial buildings in mixed humid and hot humid climates | C: DEVAP, humid CZ | System | 5 | 1 | Commercial | Cooling | A/C | Central | Energy Savings (%) | -44.24% | 0% | Yes | 10 ton unit costed by NREL at $8,100 material + markup and business expense; UPDATE BASED ON NCI REPORT: End User Equipment Cost of Baseline DX rooftop unit is $9300; DEVap manufacturer cost estimate: (100k units/yr) $12,000, (1k units/yr) $19,000 | 9300 | 19000 | 1.6167 | per square foot; 1 ton per 280 sq.ft. | 61 Manual | Total cooling in humid climates by all commercial RTUs | 15 | 2020 | Kozubal, E.; Woods, J.; Judkoff, R.; "Development and Analysis of Desiccant Enhanced Evaporative Air Conditioner Prototype"; NREL, 2012. http://www.nrel.gov/docs/fy12osti/54755.pdf Kozubal, E. et. al.; "Desiccant Enhanced Evaporative Air-Conditioning (DEVap): Evaluation of a New Concept in Ultra Efficient Air Conditioning"; NREL, 2011. http://www.nrel.gov/docs/fy11osti/49722.pdf; NCI Internal DeVAP Report Cost (listed value is not consistent with this source: "Rooftop units using DEVAP design are initially expected to cost ~30% more than competing models." Kozubal. NREL. July 2 2012. http://www.nrel.gov/docs/fy12osti/55740.pdf | BTO Tool: MTAB, NREL website, DuCool?AdvantixSystems website Appendix B: "Modeling at NREL has shown that the yearly combined source energy for the thermal and electrical energy required to operate DEVap is expected to be 30%–90% less than state-of-the-art direct expansion cooling (depending on whether it is applied in a humid or a dry climate)", NREL research team performed climate and sector specific calculations | 3-3722 | 15 | 15 | AEO 2010 NEMS
76 | Launch campaign to encourage cleaning home A/C coils annually | R: Clean AC coils | Maintenance | 5 | 3 | Residential | Cooling | A/C | All | Energy Savings (%) | 6% | 0% | Yes | 10 |  |  | 10 | per unit | 1 C/R: No FS: All electric to all electric | Total residential cooling by CAC and ASHPs as well as ASHP heating | 16 | 2010 | http://www.fuller.com/products_detail.asp?cat=1&subcat=5&id=216 Primary Source: Choi-Granade et. Al.; "Unlocking Energy Efficiency in the U.S. Economy"; McKinsey & Company (2009) | Appendix B: Savings and cost estimates derived from Exhibits 7, 13 and personal communication | 1-178 | 16 | 16 | AEO 2014 NEMS
80 | Demonstrate and deploy filters with lower pressure drop in homes with central air systems (furnace fans) | R: Low ΔP Air Filter | System | 5 | 3 | Residential | HVAC | Blower system | Central | Blower energy savings (%) | 10% | 0% | Yes | Based on home depot costs, a higher filtration filter is 2x the price of a regular basic filter of $15. | 15 | 30 | 15 | per unit; assume one filter per furnace fan | 1 C/R: No FS: All electric to all electric | Furnace Fans Pumps | 0.25 | 2013 | 1) Energy savings: LBNL's "System Effects of High Efficiency Filters" report 2) Costs from www. Homedepot.com 3) Other supporting sources: "Energy Savings Potential and RD&D Opportunities for Residential Building HVAC Systems. October 2012" http://www1.eere.energy.gov/buildings/pdfs/residential_hvac_research_opportunities.pdf; "System Effects of High Efficiency Filters in Homes." LBNL Environmental Energy Technology Division, March 2013. http://eetd.lbl.gov/sites/all/files/lbnl-6144e.pdf. ENERGY STAR "Maintenance Checklist". http://www.energystar.gov/index.cfm?c=heat_cool.pr_maintenance; Camfil, AFE journal, HPAC Engineering journal, NREL feedback. "Air-Filter Life-Cycle Cost", Seyffer, C.; HPAC Engineering 9/2010. Proper Air Filter Selection Goes a Long Way", Matela, D.AFE Journal 10/2010. Expert interviews suggest 25% is more typical savings. | BTO Tool: Estimated at $400 savings lifetime, +$60 cost; Assumed uniform savings difference from 10-40% from min/max of source: 25% used Appendix B: "As much as 40 percent of HVAC-system electricity demand could be reduced by applying air-filter life-cycle-cost analysis." Typical fan motors are PSC or brushless permanent magnet motors (BPM). (LBNL) | 1-44 | 0.25 | 0.25 | AEO 2014 NEMS
81 | Demonstrate and deploy filters with lower pressure drop in variable air volume (VAV) systems in commercial buildings | C: Low ΔP Air Filter | Distribution | 5 | 3 | Commercial | HVAC | HVAC | Central | Energy savings (%) | 2.668% | 0% | No | payback of 0.25 years based on propriatry information |  |  | 0.11 | per square foot; represents 6 filter changes over lifetime; 1 per 1,500 sq.ft. of service | 1 C/R: No FS: All electric to all electric | Total commercial variable volume ventilation and air handlers in all commercial buildings | 6 | 2013 | Camfil, AFE journal, HPAC Engineering journal Primary Source: "Air-Filter Life-Cycle Cost", Seyffer, C.; HPAC Engineering 9/2010 Other Supporting Sources: Proper Air Filter Selection Goes a Long Way", Matela, D.AFE Journal 10/2010 Expert interviews suggest 25% is more typical savings | BTO Tool: Estimated at $400 savings lifetime, +$60 cost; Assumed uniform savings difference from 10-40% from min/max of source: 25% used Appendix B: "As much as 40 percent of HVAC-system electricity demand could be reduced by applying air-filter life-cycle-cost analysis." Cost taken from manufacturer website | 3-3694 | 6 | 6 | AEO 2010 NEMS
85 | Move to include duct insulation in building codes: residential | R: Duct Insulation (N) | Distribution | 5 | 5 | Residential | HVAC | Ducts | New buildings | R-value | 8 | 4 | Yes | $1.3/ft2 and $1.1/ft2 for supply (R-8) and return (R-6) ducts respectively |  | 518 | 518 | per home; 195 ft^2 of supply duct and ^240 ft^2 return duct for 1500 ft^2 home | 5 R: No FS: All fuels HVAC (heating+cooling, no separate ventilation component) | New homes lacking duct insulation | 20 | 2010 | NREL Retrofit efficiency measures database; HES pro; ducts.lbl.gov Primary Source: Cost: NREL retrofit measure database Savings: First principles of moving ducts from R-4 to R-8 as per recent code changes Other Supporting Sources: LBNL. 2011. Thermal Energy Distribution Website. ducts.lbl.gov. | Expected & new equipment lifetime value are based on an assumption that these last 20 years. We do not have a good source to support this assumption. BTO Tool: Using average code level for ducts in unconditioned/external space | 1-98 | 20 | 20 | AEO 2014 NEMS
86 | Move to include duct insulation in building codes: commercial | C: Duct Insulation (N) | Distribution | 5 | 5 | Commercial | HVAC | Ducts | New buildings | R-value | 8 | 4 | Yes | $0.80/sq.ft. of duct surf. Area |  |  | 0.32 | per square foot | 7 C: No FS: All fuels heating and cooling | All commercial heating and cooling in new buildings with uninsulated ducts | 20 | 2010 | ducts.lbl.gov Primary Source: Cost: NREL retrofit measure database Savings: First principles of moving ducts from R-4 to R-8 as per recent code changes Other Supporting Sources: LBNL. 2011. Thermal Energy Distribution Website. ducts.lbl.gov. | Expected & new equipment lifetime value are based on an assumption that these last 20 years. We do not have a good source to support this assumption. BTO Tool: Using average code level for ducts in unconditioned/external space | 3-3623 | 20 | 20 | AEO 2010 NEMS
87 | Demonstrate and deploy natural ventilation in new homes in temperate climates | R: Natural ventilation/controls (N), temp. CZ | Use Intensity | 5 | 3 | Residential | Cooling | HVAC | Temperate | Energy Savings (%) | 46% | 0% | Yes | -0.65 | 6000 | 3000 | -3000 | per home, 3 ton equivalent cooling | 1 C/R: No FS: All electric to all electric | Central cooling in new homes in mixed-humid and marine climates | 17 | 2013 | Aarhus Engineering college, windowmaster.com Primary Source: Cardinale, N., Micucci, M. & Ruggiero, F. Analysis of energy saving using natural ventilation in a traditional Italian building. Energy and Buildings 35, (2003). Walker, A (2010). "Natural Ventilation". Whole Building Design Guide(http://www.wbdg.org/resources/naturalventilation.php) Price: Windowmaster/ Aarhus Engineering College websites Other Supporting Sources: Choi-Granade et. Al.; "Unlocking Energy Efficiency in the U.S. Economy"; McKinsey & Company (2009) | BTO Tool: Replace A/C with automated ventilation system, no ducting cost or HVAC Appendix B: Replace A/C with automated ventilation system in temperate climates: no ducting cost or HVAC Cardinale: Simulations (Italina homes) showed savings of 41%, 46%, and 52%; using average of 46% New home installed cost of $3,000 vs. $6,000 for conventional | 1-11 | 17 | 17 | AEO 2014 NEMS
91 | Deploy enhanced duct sealing | R: Enhance Duct Sealing (N) | Distribution | 5 | 3 | Residential | HVAC | Ducts | New | Energy Savings (%) | 5% | 0% | Yes | $0.33/sq.ft. |  |  | 638.22 | per home; 1,934 square foot of floor space (BED 2011) | 5 R: No FS: All fuels HVAC (heating+cooling, no separate ventilation component) | New homes with IECC 2009 code-compliant duct sealing | 20 | 2010 | NREL Retrofit efficiency measures database, McKinsey; Aeroseal website: http://www.aeroseal.com/commercial_duct_sealing.html; Modera 2005: Fixing Duct Leaks, ASHRAE Journal; typical new home duct leakage from BA House Simulation Protocols (http://www.nrel.gov/docs/fy11osti/49246.pdf) Primary Source: Hendron, R., and Engebrecht, C. 2010. Building America House Simulation Protocols. DOE/GO-102010-3141. http://apps1.eere.energy.gov/buildings/publications/pdfs/building_america/house_simulation_revised.pdf Modera, M Fixing Duct Leaks in Commercial Buildings ASHRAE Journal June 2005 | Expected & new equipment lifetime value are based on an assumption that these last 20 years. We do not have a good source to support this assumption. BTO Tool: Reducing duct leakage from 6.5% to 1.3% Appendix B: Hendron: 10% supply air leakage, ~6.5% to the outside Modera: Figure 6 ~80% reduction in leakage for Aeroseal in sections of a large office. Implication: reduce leakage (80%) from 6.5% to 1.3%. Price is a 15% discount over measure 127 because of efficiencies related to new homes vs. retrofits | 1-99 | 20 | 20 | AEO 2014 NEMS
92 | Move to include duct sealing in commercial codes | C: Duct Sealing (N) | Distribution | 5 | 5 | Commercial | HVAC | Ducts | New | Energy Savings (%) | 10% | 0% | Yes | $0.33/sq.ft of floor space |  |  | 0.33 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | All furnaces and A/C heating and cooling (i.e., ducts) in new commercial buildings | 20 | 2010 | Aeroseal website: http://www.aeroseal.com/commercial_duct_sealing.html; Modera 2005: Fixing Duct Leaks, ASHRAE Journal; Primary Source: Modera, M Fixing Duct Leaks in Commercial Buildings ASHRAE Journal June 2005 Aeroseal website. http://www.aeroseal.com/problem-we-solve/FAQ-commercial.html Other Supporting Sources: 13. Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. 289 (2011). | Expected & new equipment lifetime value are based on an assumption that these last 20 years. We do not have a good source to support this assumption. BTO Tool: Using average savings and cost & perormance to get to 97% duct efficiency from Hamilton and ACEEE sources Appendix B: Modera: 80% heating season duct efficiency (See Figure 2 and measured duct efficiency data cited throughout the article. 50% improvement is assumed over the 80% duct efficiency baseline. Price based on average of three Aeroseal case studies and estimated payback of 2.5 years ($0.33/ft2=$247*2.5 years/1879 ft2) | 3-3669 | 20 | 20 | AEO 2010 NEMS
93 | Launch campaign to encourage steam cleaning commercial A/C coils annually | C: Steam Clean AC Coils | Evaporator | 4 | 4 | Commercial | Heating & Cooling | A/C | All | Energy Savings (%) | 10% | 0% | Yes | 3000 |  |  | 0.2 | per square foot | 1 C/R: No FS: All electric to all electric | All commercial cooling, and heating with ASHPs | 15 | 2010 | SavetheWatts.com, National Steam Clean, Rejuvinair, Air Conditioning, Heating and Refrigeration News (achrnews.com) Primary Source: Checket-Hanks, B. "Contractor Offers Hope For PTAC IAQ". The Air Conditioning, Heating and Refrigeration NEWS, March 10, 2004 Rejuvinair website | BTO Tool: Assumed 15,000 sq.ft. building average Appendix B: Savings (10%) and cost estiamtes based on Manufacturer's website | 3-3616 | 15 | 15 | AEO 2010 NEMS
94 | Demonstrate and deploy thermal energy storage (including chilled water and ice) for central chiller systems | C: Cold Storage for Large Chillers | System | 3 | 4 | Commercial | Cooling | A/C | Central | Energy Savings (%) | 5% | 0% | Yes | ~$100/ton-hr; $20 - $100/ton-hr |  |  | 9600 | per unit; 20 tons, 8 hours per 15,000 sq.ft | 10 C: No FS: All fuels cooling (elec+NG) | All commercial cooling | 15 | 2013 | http://www.calmac.com/office/engineer.asp, www.pge.com/includes/docs/pdfs/about/edusafety/training/pec/inforesource/thrmstor.pdf; Thermal Energy Storage Strategies for Commercial HVAC Systems, PG&E Energy Efficiency Information Primary Source: Pacific Gas & Electric. "Thermal Energy Storage Strategies for Commercial HVAC Systems". PG&E, 1997 Calmac (Manufacturer) website | BTO Tool: Assume 20 tons cooling, 8 hours of capacity/ building; Range of cost due to type of thermal energy storage, whether chilled water or ice system Appendix B: Citation 1, Table page 12 provides cost and efficiency data. Calmac indicates "Operation at night with 20 degree lower condensing temperatures can improve energy efficiency typically by 2 to 8%." Assume 5% (average of 208%) savings, cost from 20 tons cooling, 8 hours of capacity/ building at $100/ton-hr | 3-3612 | 15 | 15 | AEO 2010 NEMS
95 | Launch campaign to encourage adoption of EER 10.8 room A/C's @ end of life | R: Energy Star Room A/C (EER 10.8) | System | 5 | 4 | Residential | Cooling | A/C | Room | EER (BTU/W-h) | 10.8 | 9.8 | Yes | Taken from TSD | 574.9 | 707.5 | 132.6 | per unit; 12 kBTU/hr for 1,000 sq.ft. | 1 C/R: No FS: All electric to all electric | All residential cooling using room A/Cs | 10 | 2010 | NREL Retrofit efficiency measures database Primary Source: Savings: First principles Cost: NREL retrofit measure database | BTO Tool: Assumed 20 MBU's | 1-12 | 10 | 10 | AEO 2014 NEMS
96 | Launch campaign to encourage adoption of max tech Room A/Cs | R: EER 13 Room AC | System | 5 | 2 | Residential | Cooling | A/C | Room | EER (BTU/W-h) | 13 | 9.8 | Yes | Took midpoint of installed cost reported by EIA and extrapolated based on existing EER and cost data. | 385 | 724 | 339 | per unit | 1 C/R: No FS: All electric to all electric | All residential cooling using room A/Cs | 10 | 2016 | 1) Costs: Used a more recent, not yet published version of: "Updated Building Sector Appliance and Equipment Costs and Efficiency." August 2013. EIA. http://www.eia.gov/analysis/studies/buildings/equipcosts/pdf/full.pdf. Room Air Conditioner Standards Rulemaking. http://www1.eere.energy.gov/buildings/appliance_standards/product.aspx/productid/41. Residentical Energy Consumption Survey (RECS) 2005. http://www.eia.gov/consumption/residential/data/2005/c&e/airconditioning/pdf/alltables1-11.pdf 2) Savings: First principles; Bouza |  | 1-12 | 10 | 10 | AEO 2014 NEMS
97 | Need to develop SEER 24 Central A/C in homes at end of life - TARGET | R: SEER 24 CAC* | System | 4 | 0 | Residential | Cooling | A/C | Central | SEER (BTU/W-h) | 24 | 12.225 | Yes | $710 beyond SEER 13 as per Navigant work; 13% cost premium for 24 vs. 21 SEER system estimated based on analysis of 2013$ equipment prices of SEER 13-18 heat pumps found at www.acwholesalers.com web site (accessed 1-17-2013) and installation costs as found in May 2002 DOE TSD for central heat pump & AC efficiency standard rulemaking ($2280 in 1998; inflated to 2013$ using CPI). | 4680 | 7322.4 | 2642.4 | per home; 3 ton cooling | 1 C/R: No FS: All electric to all electric | Total energy consumption by residential central air conditioning in single- and multi-family homes | 17 | 2016 | Navigant consulting, Web search (Westinghouse vs. SEER 13), www.acwholesalers.com; CAC & HP TSD; Peer reviewer expressed concerns over data quality because it was a manufacturer case study in an ideal climate (therefore reduced data quality from 5 to 4) Primary Source: Savings: first principles Cost: Navigant Consulting, personal communication | BTO Tool: Peer reviewer raised a question of additional energy use needed to control indoor humidity in variable speed CAC units. This should be explored in the future, or additional sources should be sought. | 1-13 | 17 | 17 | AEO 2014 NEMS
99 | Launch campaign to encourage adoption of whole house fans in existing buildings in temperate and north climates | R: Add whole house fan [E] | Use intensity | 5 | 3 | Residential | Cooling | Fan | Existing homes, temperate and north | Energy Savings (%) | 24.75% | 0% | Yes | 692 |  |  | 692 | per home; 3 ton cooling | 1 C/R: No FS: All electric to all electric | Central cooling in single family existing homes in very cold/cold, mixed-humid, and marine climates | 17 | 2010 | Web search ($292)+ 8 hours labor for retrofit at $50/hr Primary Source: Southface Energy Institiute & Oak Ridge National Laboratory FEMP Technology Fact Sheet: Whole House Fan. (1999) | BTO Tool: Assumed no A/C needed at night in temperate areas (1/3 of usage) Appendix B: Calculations based on information on page 1 of fact sheet, Assumes reduction of A/C use at night estimated at 25% of total annual load | 1-14 | 17 | 17 | AEO 2014 NEMS
100 | Launch campaign to encourage adoption of whole house fans in new buildings in temperate and north climates | R: Add whole house fan (N) | Use intensity | 2+ | 3 | Residential | Cooling | Fan | New homes, temperate and north | Energy Savings (%) | 24.75% | 0% | Yes | 392 |  | 392 | 392 | per home | 1 C/R: No FS: All electric to all electric | Central cooling in new homes in very cold/cold, mixed-humid, and marine climates | 17 | 2011 | Web search ($292)+ 2 hours labor for installation at $50/hr Primary Source: Southface Energy Institiute & Oak Ridge National Laboratory FEMP Technology Fact Sheet: Whole House Fan. (1999) | BTO Tool: This is in addition to "BAU" A/C choice Appendix B: Calculations based on information on page 1 of fact sheet, Assumes reduction of A/C use at night estimated at 25% of total annual load | 1-15 | 17 | 17 | AEO 2014 NEMS
102 | Develop a standard for adoption of variable speed motors in residential blowers | R: Variable Speed Blower | Distribution | 5 | 4 | Residential | Ventilation | Blower system | Central | Blower energy savings (%) | 51% | 0% | No | 296 |  |  | 296 | per unit | 1 C/R: No FS: All electric to all electric | Furnace Fans Pumps | 20 | 2010 | Lekov et. Al. ; Electricity and Natural Gas Efficiency Improvements for Residential Gas Furnaces in the U.S.; Residential HVAC Electronically Commutated Motor Retrofit Report Primary Source: Murray, M. & Fitzpatrick, S. Residential HVAC Electronically Commutated Motor Retrofit Report Table of Contents. Advanced Energy (2012) Other Supporting Sources: Franco, V., Lutz, J., Lekov, A. & Gu, L. Furnace Blower Electricity: National and Regional Savings Potential. Florida Solar Energy Center(2008) | BTO Tool: Averaged two source to get 45% savings Appendix B: "ECM motors represent a 51 percent full-load efficiency improvement over permanent split-capacitor (PSC) motors" "The three ECMs used in this study cost, on average, $296. The average motor installation cost was approximately $547.50." Only retrofit is cost effective, so using 51% savings, $296 cost | 1-44 | 20 | 20 | AEO 2014 NEMS
104 | Move to standardize variable speed motors in commercial HVAC compressors | C: Var-speed compressor in AC | Compressor | 5 | 4 | Commercial | Heating & Cooling | A/C | All | Energy Savings (%) | 25.3% | 0% | Yes | ~$1000, assumed for controller |  |  | 0.066667 | per square foot | 1 C/R: No FS: All electric to all electric | All commercial cooling, and heating with ASHPs | 15 | 2010 | "Potential electricity savings by variable speed control of compressor for air conditioning systems", Henry Nasution; Mat Nawi Wan Hassan | No notes | 3-3616 | 15 | 15 | AEO 2010 NEMS
105 | Encourage retro-commissioning of commercial buildings for all buildings (only HVAC is considered, and assumes no new equipment costs) | C: Retro-commissioning (HVAC only) | Controls | 5 | 4 | Commercial | HVAC | HVAC | All | Energy Savings (%) | 16% | 0% | Yes | $0.3/sq.ft per one time retro-commissioning | 0 | 0.3 | 0.3 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | All commercial HVAC energy use | 5 | 2011 | Costs and energy savings for buildings > 100,000 SF: Pg . 145,155, 158. "Building Commissioning: A Golden Opportunity for Reducing Energy Costs and Greenhouse Gas Emissions", Mills, E.; Energy Efficiency (2011) 4:145–173. |  | 3-3617 | 5 | 5 | AEO 2010 NEMS
109 | Move to standardize PSC motors in commercial blowers | C: Comm. PSC blowers | Distribution | 4 | 4 | Commercial | Ventilation | Blower system | Furnaces | Blower energy savings (%) | 14% | 0% | No | 15 |  |  | 15 | per unit; Assumed 1 per 1500 sq.ft | 1 C/R: No FS: All electric to all electric | All commercial ventilation | 20 | 2010 | Home energy magazine article | No notes | 3-3614 | 20 | 20 | AEO 2010 NEMS
110 | Standardize high efficiency circulator pumps in homes | R: Heating circulator pumps | Distribution | 5 | 3 | Residential | Heating/Cooling/Water | Circulation pumps | Boilers | Energy Savings (%) | 21.6% | 0% | No | $146-$359 with $146 showing up most frequently | $82-92 |  | 59 | per unit | 1 C/R: No FS: All electric to all electric | Furnace Fans Pumps | 20 | 2010 | Home energy magazine article; Assessment of New Circulator Pump Technology, EPRI 1020132, 11/15/2010; Multiple sources from online vendors such as Amazon, PexUniverse.com, Grainger, etc. Primary Source: Waide, P. & Brunner, C. Energy-Efficiency Policy Opportunities for Electric Motor-Driven Systems. International Energy Agency (2011). | Expected lifetime is assumed - we do not have a good source to support this assumption. Appendix B: Figure 27 and table 23 show savings of 55-63% improvement of existing system with new, optimized pump Cost from google search | 1-44 | 20 | 20 | AEO 2014 NEMS
111 | Increase deployment of high efficiency circulator pumps in commercial buildings | C: Efficient circulator pumps | Distribution | 4 | 5 | Commercial | Heating/Cooling/Water | Circulation pumps | Boilers | Energy Savings (%) | 60% | 0% | No | 75 |  |  | 0.05 | per unit; Assumed 1 per 1500 sq.ft | 1 C/R: No FS: All electric to all electric | All commercial circulator pumps | 20 | 2010 | Primary Source: pg. 58 quotes 80-90% improvement. Waide, P. & Brunner, C. Energy-Efficiency Policy Opportunities for Electric Motor-Driven Systems. International Energy Agency (2011). Other Supporting Sources: Byrne, Jeanne, "Motors Matter". Home Energy Magazine Online 1-7 (2000) | Expected lifetime is assumed - we do not have a good source to support this assumption.Appendix B: Page 58: An exemplary study of two optimal pump systems demonstrates that if all available state‐of‐the‐ art efficiency measures of a pump system are systematically applied, energy‐efficiency savings of 80% to 90% | 3-3642 | 20 | 20 | AEO 2010 NEMS
112 | Move to standardize condensers in natural gas residential furnaces | R: Condensing Gas Furnace | System | 5 | 4 | Residential | Heating | Furnace | All | Energy Savings (%) | 11% | 0% | Yes | $21/(kBtu/h) |  |  | 840 | per home; 40 kBTU/hr capacity | 2 C/R: No FS: All gas to all gas | Total residential heating energy use by natural gas furnaces in all homes. | 23 | 2011 | NREL Retrofit efficiency measures database; Weil-McLain |  | 1-46 | 23 | 23 | AEO 2014 NEMS
114 | Demonstrate and deploy sprayed mesh residential AC's | R: Sprayed mesh AC | Condenser | 4 | 3 | Residential | Cooling | A/C | All | Energy Savings (%) | 6% | 0% | Yes | 273.44 | 6545 | 6818.44 | 273.44 | per home; 3 tons of cooling | 1 C/R: No FS: All electric to all electric | Total residential cooling (CAC & ASHP) other than room A/Cs | 16 | 2013 | Friterm, table 1 cooling/power draw ratios,ecomesh; Assume 1.7 year payback as listed for other technologies plus 4 hours to retrofit; Condenser-Air Evaporative Pre-Cooler Test Protocol report for SoCal Edison (Nov 2012) Primary Source: Acul, H. Air Cooled Condensers And Their Effect On Energy. 1-13 (2008) Other Supporting Sources: Choi-Granade et. Al.; "Unlocking Energy Efficiency in the U.S. Economy"; McKinsey & Company (2009) | BTO Tool: Energy savings are based on a report that evaluated the effectiveness of direct, evaporative pre-cooling systems. Savings are also climate dependent, but 6% represents an average of 11% savings in favorable climates, and 1% savings in more humid climates. Appendix B: Impacts estimated from table on page 4, Increase COP from 3.03 to 3.71 | 1-21 | 16 | 16 | AEO 2014 NEMS
115 | Demonstrate and deploy sprayed mesh commercial AC's | C: Sprayed mesh AC | Condenser | 5 | 3 | Commercial | Cooling | A/C | All | COP | 3.71 | 3.03 | Yes | 918.75 |  |  | 3.2812 | per square foot; 1 ton per 280 sq.ft. | 1 C/R: No FS: All electric to all electric | Total commercial electric load of rooftop AC units (residential style) | 15 | 2013 | Friterm, table 1 cooling/power draw ratios Primary Source: Acul, H. Air Cooled Condensers And Their Effect On Energy. 1-13 (2008) Other Supporting Sources: Choi-Granade et. Al.; "Unlocking Energy Efficiency in the U.S. Economy"; McKinsey & Company (2009) | BTO Tool: 21 week payback 5 days a week 16 hours a day for 10 ton system to cool 10,000 sq. ft running at 70% power $0.25/kwh (England) Appendix B: Impacts estimated from table on page 4, Increase COP from 3.03 to 3.71 | 3-3671 | 15 | 15 | AEO 2010 NEMS
118 | Move to standardize improved motors in ceiling fans | R: Efficient Ceiling Fan Motors | System | 5 | 4 | Residential | MELs | Ceiling Fan | All | CFM/W | 272 | 100 | No | 86 |  | 86 | 86 | per unit | 1 C/R: No FS: All electric to all electric | Total energy use by residential ceiling fans | 14 | 2010 | Energy Star database for performance (http://downloads.energystar.gov/bi/qplist/ceiling_fan_only_prod_list.pdf?419d-5d10), Energy Star savings calculator for cost (http://www.energystar.gov/ia/business/bulk_purchasing/bpsavings_calc/Ceiling_Fan_Savings_Calculator_Consumer.xls?e8fd-5d0d) Primary Source: Environmental Protection Agency, "ENERGY STAR Ceiling Fan Product List", 2012 | BTO Tool: Reduced from 680, which was an extreme outlier in the Energy Star database. 272 cfm/W is at the upper end of products with multiple manufacturers. 150 cfm/W is Energy Star minimum. Appendix B: Represents second fastest of six speeds from one of the most efficient manufactrurers using a DC motor at 280 CFM/W Installed base estimated at typical 100 CFM/W 63% reducition possible at $86 premium | 1-6 | 14 | 14 | AEO 2014 NEMS
119 | Launch campaign to encourage adoption of duct insulation in existing homes | R: Duct Insulation (E) | Distribution | 5 | 4 | Residential | HVAC | Ducts | Retrofit | Energy Savings (%) | 20% | 0% | Yes | HES Baseline Value is $910/home |  | 910 | 910 | per home; 195 ft^2 of supply duct and ^240 ft^2 return duct for 1500 ft^2 home | 5 R: No FS: All fuels HVAC (heating+cooling, no separate ventilation component) | Existing homes lacking duct insulation | 20 | 2010 | Primary Source: Hendron, R., and Engebrecht, C. 2010. Building America House Simulation Protocols. DOE/GO-102010-3141. http://apps1.eere.energy.gov/buildings/publications/pdfs/building_america/house_simulation_revised.pdf NREL Residential Efficiency Measures Database. http://www.nrel.gov/ap/retrofits/measures.cfm?gId=2&ctId=16 Mills, E.. et al. 2007. "Home Energy Saver: Documentation of Calculation Methodology, Input Data, and Infrastructure." Lawrence Berkeley National Laboratory Report No. 51938. http://evanmills.lbl.gov/pubs/pdf/home-energy-saver.pdf | Expected & new equipment lifetime value are based on an assumption that these last 20 years. We do not have a good source to support this assumption. BTO Tool: Assumes no duct insulation Appendix B: Hendron: Supply duct surface area (ft2)= 0.27 × FFA, Return duct surface area (ft2)= 0.05 × Nreturns × FFA NREL: $1.3/ft2 and $1.1/ft2 for supply (R-8) and return (R-6) ducts respectively Mills: efficiencyducts = DF * HSE + (1− DF) *CSE Estimated cost based on insulating 195 ft2 of supply ducts in unconditioned space and (Hendron value for 1500 ft2 house) and $1.3/ft2 (NREL Retrofit Meausure Database) is $254. Insulating 240 ft2 of return ducts in unconditioned space using $1.1/ft2 is another $264, for a total of $518. Energy savings is derived from HES Pro assumptions for duct distribution efficiency using LBNL's ASHRAE 152 model. TDM Mtg 2: THis measure applies only to existing homes because IECC 2009 adopted by majority of states requires min duct insulation of R-6 for inner ducts, and R-8 for ducts located outside the home. | 1-100 | 20 | 20 | AEO 2014 NEMS
120 | Launch campaign to encourage adoption of duct insulation in existing commercial buildings | C: Duct Insulation (E) | Distribution | 5 | 4 | Commercial | HVAC | Ducts | Retrofit | Energy Savings (%) | 40% | 0% | Yes | 0.88 |  | 0.88 | 0.88 | per square foot | 7 C: No FS: All fuels heating and cooling | All commercial heating and cooling in existing buildings without insulated ducts | 20 | 2010 | Primary Source: Same as above | Expected & new equipment lifetime value are based on an assumption that these last 20 years. We do not have a good source to support this assumption. BTO Tool: 2000 ' of duct, 12"d/3 sqft/ft Appendix B: Savings assumed same as residential Cost assumptions: 2000 ' of duct, 12"d/3 sqft/ft. $2.2/ft2 of supply duct area. 15000 ft2 typical commercial buildng. | 3-3620 | 20 | 20 | AEO 2010 NEMS
121 | Launch campaign to encourage annual maintenance of heaters in homes | R: Heater Maintenance | Maintenance | 5 | 4 | Residential | Heating | Furnace/ boiler | All | Energy Savings (%) | 5% | 0% | Yes | ~$25 annual incremental cost, present value at 6% DF for 20 years |  | 300 | 300 | per home | 8 R: No FS: All fuels heating | All homes heating (including sectional/secondary) | 1 | 2010 | Choi-Granade et. al. (2009). "Unlocking Energy Efficiency in the U.S. Economy". McKinsey and Company | BTO Tool: Assumes regular maintenance underway; this is incremental tuning for efficiency Appendix B: Assumes regular maintenance underway; expert interviews provided cost and savings for incremental effort to maximize efficiency. $300 represents present value of $25 annual cost over equipment lifetime | 1-93 | 1 | 1 | AEO 2014 NEMS
122 | Demonstrate and deploy predictive control thermostats in all homes | R: Predictive Thermostats (NEST) | Controls | 5 | 3 | Residential | HVAC | Building controls | All | Energy Savings (%) | 10.47% | 0% | Yes | $250 per thermostat plus $120 for NEST installation (or assume $50 for 1/2 hour install) | 0 | 370 | 370 | per home | 5 R: No FS: All fuels HVAC (heating+cooling, no separate ventilation component) | Total residential central AC and heating energy consumption | 35 | 2013 | Savings: Cho, Energy Conservation and Management 44 (2003); Cost: Nest (http://www.nest.com/inside-and-out/) | BTO Tool: Savings of $282 off $2200 in most aggressive realistic scenario Appendix B: The results show that use of the predictive control strategy could save between 10% and 12% energy during the cold winter months. The energy savings are somewhat higher during mild weather conditions. | 1-101 | 35 | 35 | AEO 2014 NEMS
123 | Demonstrate and deploy predictive control thermostat in all commercial buildings | C: Predictive Thermostats | Controls | 5 | 3 | Commercial | HVAC | Building controls | All | Energy Savings (%) | 10.47% | 0% | Yes | 368 |  |  | 0.24533 | per square foot; 1 zone per 1,500 sq ft | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | All commercial HVAC energy use | 35 | 2013 | Savings: Cho, Energy Conservation and Management 44 (2003); Cost: Nest (http://www.nest.com/inside-and-out/) | Appendix B: The results show that use of the predictive control strategy could save between 10% and 12% energy during the cold winter months. The energy savings are somewhat higher during mild weather conditions. | 3-3617 | 35 | 35 | AEO 2010 NEMS
124 | Deploy programmable thermostats in existing homes | R: Programmable Thermostats | Controls | 5 | 4 | Residential | HVAC | Building controls | All | Energy Savings (%) | 3.75% | 0% | Yes | $90/thermostat; $50 incremental cost per thermostat |  |  | 50 | per home | 5 R: No FS: All fuels HVAC (heating+cooling, no separate ventilation component) | All heating and cooling in existing homes | 35 | 2010 | RECS 2009 survey analysis (46% have thermostats; 60% use for setback to save 200 HDD -> 5%), so 75% of 5% savings Primary Source: Energy Information Agency. "Residential Energy Consumption Survey, 2009". Department of Energy (2012) | BTO Tool: Installation cost assumes 30 minutes marginal labor (combined with other measures) Appendix B: RECS 2009 analysis of set back behavior and penetration of programmable thermostats included in spreadsheet | 1-102 | 35 | 35 | AEO 2014 NEMS
125 | Reduce over sizing in home heaters | R: Right Sized Heater | Use intensity | 3 | 4 | Residential | Heating | Heater | All | Energy Savings (%) | 5% | 0% | Yes | -100 |  |  | -100 | per home | 8 R: No FS: All fuels heating | Total residential heating in all homes | 18 | 2010 | SWAG Primary Source: Djunaedy, E., Van Den Wymelenberg, K., Acker, B., Thimmana, H. (n.d.). "Oversizing of HVAC System: Signatures and Penalties. Energy and Buildings" Energy and Buildings, In Press Florida Solar Energy Center, "Right-Size Heating and Cooling Equipment", Department of Energy (2002) NREL Measure Database (for cost per unit capacity) Other Supporting Sources: Choi-Granade et. Al.; "Unlocking Energy Efficiency in the U.S. Economy"; McKinsey & Company (2009) | Appendix B: Pg. 6: "estimated an energy savings of 0.2% for every 1% reduction in oversizing" Pg 1: "One Florida study showed a typical 9 percent increase in annual space cooling electricity usage for units that were oversized by 50 percent or more;nearly 40 percent of contractors indicated that they purposefully over-sized equipment", Assume 50% oversizing on average for cooling, 25% for heating | 1-47 | 18 | 18 | AEO 2014 NEMS
126 | Reduce over sizing in commercial heaters | C: Right Sized Heater | Use intensity | 3 | 4 | Commercial | Heating | Heater | All | Energy Savings (%) | 5% | 0% | Yes | -$10/kBtu/hr |  | -0.08 | -0.08 | per square foot | 9 C: No FS: All fuels heating | All commercial heating | 15 | 2010 | McKinsey report (based on residential) Primary Source: Djunaedy, E., Van Den Wymelenberg, K., Acker, B., Thimmana, H. (n.d.). "Oversizing of HVAC System: Signatures and Penalties. Energy and Buildings" Energy and Buildings, In Press Florida Solar Energy Center, "Right-Size Heating and Cooling Equipment", Department of Energy (2002) NREL Measure Database (for cost per unit capacity) Other Supporting Sources: Choi-Granade et. Al.; "Unlocking Energy Efficiency in the U.S. Economy"; McKinsey & Company (2009) | BTO Tool: Negative initial cost as smaller unit, assumes peak/average heating of 3:1, 1.9 Quads/year, 80 B sq.ft. Appendix B: Pg. 6: "estimated an energy savings of 0.2% for every 1% reduction in oversizing" Pg 1: "One Florida study showed a typical 9 percent increase in annual space cooling electricity usage for units that were oversized by 50 percent or more;nearly 40 percent of contractors indicated that they purposefully over-sized equipment", Assume 50% oversizing on average for cooling, 25% for heating | 3-3626 | 15 | 15 | AEO 2010 NEMS
127 | Launch campaign to encourage adoption of duct sealing in existing homes | R: Duct Sealing (E) | Distribution | 5 | 3 | Residential | HVAC | Ducts | Retrofit, furnaces | Energy Savings (%) | 10% | 0% | Yes | $0.33/sq.ft. | 0 | 638.22 | 638.22 | per home; 1,934 square foot of floor space (BED 2011) | 5 R: No FS: All fuels HVAC (heating+cooling, no separate ventilation component) | Existing homes with unsealed ducts | 20 | 2010 | 1) Energy savings from: a) http://www.aeroseal.com/what-we-do/introduction.html; http://www.aeroseal.com/problem-we-solve/FAQ-commercial.html; b) $0.40/sq.ft. from "Energy Savings Potential and RD&D Opportunities for Residential Building HVAC Systems. October 2012. http://www1.eere.energy.gov/buildings/pdfs/residential_hvac_research_opportunities.pdf | Expected & new equipment lifetime value are based on an assumption that these last 20 years. We do not have a good source to support this assumption. Appendix B: Aeroseal: $.33/ft2 based on measure 92. Average house assumption is 1500 ft2. Assumes twice the energy savings as new homes (Measure 91). | 1-103 | 20 | 20 | AEO 2014 NEMS
128 | Launch campaign to encourage adoption of duct sealing in existing commercial buildings | C: Duct Sealing (E) | Distribution | 5 | 3 | Commercial | HVAC | Ducts | Retrofit, furnaces | Energy Savings (%) | 20% | 0% | Yes | $0.33/sqft installation and materials; 0.075/sqft diagnostics |  |  | 0.405 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | All commercial heating and cooling in existing buildings with unsealed ducts | 20 | 2010 | Aeroseal website: http://www.aeroseal.com/commercial_duct_sealing.html Primary Source: Modera, M Fixing Duct Leaks in Commercial Buildings ASHRAE Journal June 2005 TIAX. Energy Impact of Commercial Building Controls and Performance Diagnostics?: Market Characterization , Energy Impact of Building Faults and Energy Savings Potential. Construction 413 (2005). | Expected & new equipment lifetime value are based on an assumption that these last 20 years. We do not have a good source to support this assumption. BTO Tool: Using average savings and cost & perormance to get to 97% duct efficiency from Hamilton and ACEEE sources. 7.5 cents/ft2 added for diagnostic testing (TIAX 2005) Appendix B: Modera: 80% heating season duct efficiency (See Figure 2 and measured duct efficiency data cited throughout the article. 7.5 cents/ft2 added for diagnostic testing (TIAX 2005). Nominal sealing cost is 33 cents/ft2 for consistency with Measure 92. Energy savings assumed to be double the savings in new homes from Measure 92. | 3-3621 | 20 | 20 | AEO 2010 NEMS
129 | Demonstrate and deploy household nighttime economizers | R: Night Economizer | Use Intensity | 5 | 3 | Residential | Cooling | Economizer | All | Energy Savings (%) | 10% | 0% | Yes | See incremental cost |  |  | 780 | per home | 1 C/R: No FS: All electric to all electric | Total energy consumption by residential central air conditioning in single-family homes | 16 | 2013 | Itron Inc., Kema, Inc. "California Energy Efficiency Potential Study" Pacific Gas & Electric (2008) | BTO Tool: Assumed $600 as per commercial for economizer + $180 for controls Appendix B: A-10: "The assumed savings for night economizer was 20% of the RASS household UEC for coastal regions and 10% of the UEC for inland regions." (Used 10% as majority of country is best represented as "inland" in this dataset) Price taken from web search | 1-16 | 16 | 16 | AEO 2014 NEMS
132 | Demonstrate and deploy low temperature heat pumps, climate zones 1 & 2 (no fuel switching) | R: Cold Climate HP, Coldest CZ | System | 5 | 2 | Residential | Heating | Heat pump | Cold climates | Energy Savings (%) | 23% | 0% | Yes | $3000 incremental cost | 3300 | 6300 | 3000 | per home; 3 tons | 1 C/R: No FS: All electric to all electric | Electric heating, proportion of cooling in coldest 2 climates | 18 | 2014 | 1) Savings and incremental cost: Sachs et al, 2009, "Emerging Energy-Saving HVAC Technologies and Practices for the Buildings Sector" 2) Base unit cost: EIA - Technology Forecast Updates – Residential and Commercial Building Technologies, September 2013 3) Assuming energy savings are reduced by roughly 10% between ASHP operating at 17 degF and below 0 degF (Product & Technology Review PTR #19 December 2007 Acadia Heat Pump, http://www.energyideas.org/documents/Factsheets/PTR/AcadiaHeatPump.pdf) Also, based on energy savings of CC ASHP in measure 778 (25%) (Sachs et al, 2009, "Emerging Energy-Saving HVAC Technologies and Practices for the Buildings Sector") | 1) Average between min and max lifetimes of 9 and 22 years for residential ASHP (EIA - Technology Forecast Updates – Residential and Commercial Building Technologies, September 2013) | 1-104 | 18 | 18 | AEO 2014 NEMS
133 | Demonstrate and deploy reverse cycle chiller (heat pump water heater) to heat water in multifamily homes. The RCC is a water heater which uses a refrigeration cycle with an air‐side evaporator and a water‐side condenser. | R: Reverse Cycle Chiller (multi family) | System | 5 | 2 | Residential | Water heating | Heat pump | Multi family homes | kWh/unit | 1000 | 2700 | No | $677/unit, based on a prototypical mid-rise multifamily building with 163 units and a total incremental project cost of $110,275 |  | 677 | 677 | per unit; 20 tons per building | 1 C/R: No FS: All electric to all electric | Total electric water heating in all multi-family homes | 13 | 2018 | Heller, J. & Cejudo, C. Reverse Cycle Chillers for Multifamily Buildings in the Pacific Northwest : Phase I Final Report. Bonneville Power Administration (2009) | BTO Tool: Analyzed for multi-family Appendix B: "The savings from this alternative design are about 1,700 kWh/yr per unit with an expected measure life of 15 years. This represents a simple payback of about 4.4 years at a retail electricity cost of $0.09/kWh." Reducing kWh/unit from 2,700 to 1,000 with indicated payback. | 1-55 | 13 | 13 | AEO 2014 NEMS
134 | Demonstrate and deploy reverse cycle chiller (heat pump water heater) to heat water in select commercial buildings. The RCC is a water heater which uses a refrigeration cycle with an air‐side evaporator and a water‐side condenser. | C: Reverse Cycle Chiller | System | 4 | 2 | Commercial | Water heating | Heat pump | Commercial buildings with high H2O requirements | kWh/100,000 sq. ft | 138723.4043 | 374553.1915 | No | $0.94/SF, based on prototypical mid-rise multifamily building of 117,500 SF and a total incremental cost of $110,275 |  | 0.94 | 0.94 | per square foot | 1 C/R: No FS: All electric to all electric | All electric commercial water heating | 13 | 2018 | Heller, J. & Cejudo, C. Reverse Cycle Chillers for Multifamily Buildings in the Pacific Northwest : Phase I Final Report. Bonneville Power Administration (2009) | Appendix B: Used same percent savings and cost as multi-family measure. This measure can be included in the UBER goal in the future if additional analyses were done on the technology. | 3-3627 | 13 | 13 | AEO 2010 NEMS
135 | Research, demonstrate, and deploy air-to-air heat exchangers in homes | R: Air-to-Air Exchangers | Use Intensity | 5 | 3 | Residential | Heating | HVAC | All | Energy Savings (%) | 6.813% | 0% | Yes | 1838 | 463 | 1375 | 912 | per home; 100 cfm air excahnge | 8 R: No FS: All fuels heating | Total residential heating in all homes | 18 | 2013 | Beopt default costs Primary Source: Hellevang, K. & Pedersen, C. Air-to-Air Heat Exchangers. North Dakota State University (2009) | BTO Tool: Exhaust ventilation and energy recovery ventilator Appendix B: Estimated from first principles using 3,000 HDD as U.S. average, 45 CFM as air handling treated to calculate maximum heating savings | 1-47 | 18 | 18 | AEO 2014 NEMS
138 | Demonstrate and deploy desiccant wheel A/C in commercial buildings in hot-humid climates | C: Desiccant wheel AC, hot-humid CZ | System | 5 | 4 | Commercial | Cooling | A/C | High-humidity regions | Energy Savings (%) | 25% | 0% | Yes | $5/cfm | 0.16667 | 0.5 | 0.33333 | per square foot | 15 C: FS: All fuel cooling (elec+gas) to all electric | Total cooling in hot, humid climates in all commercial buildings | 15 | 2013 | S.J. Slayzak and J.P. Ryan; Desiccant Dehumidification Wheel Test Guide (2000) Desroches, L.-B. et al. Max Tech and Beyond (2011) | Appendix B: "energy savings on building cooling systems are estimated to be approximately 25%" Adjusted 25% to 12.5% to incorporate baselien improvement in A/C since publication of original source | 3-3655 | 15 | 15 | AEO 2010 NEMS
139 | Demonstrate and deploy desiccant wheel A/C in homes in hot-humid climates | R: Desiccant wheel AC, hot-humid CZ | System | 5 | 4 | Residential | Cooling | A/C | High-humidity regions | Energy Savings (%) | 25% | 0% | Yes | $8/cfm |  |  | 720 | per home; assume 0.3 ACH, 1800 sq.ft | 1 C/R: No FS: All electric to all electric | Total cooling in hot-humid climates | 16 | 2013 | S.J. Slayzak and J.P. Ryan; Desiccant Dehumidification Wheel Test Guide (2000) Desroches, L.-B. et al. Max Tech and Beyond (2011) | Appendix B: "energy savings on building cooling systems are estimated to be approximately 25%" Adjusted 25% to 12.5% to incorporate baselien improvement in A/C since publication of original source | 1-17 | 16 | 16 | AEO 2014 NEMS
140 | Demonstrate and deploy chilled beams for heating and cooling in new commercial buildings, except two coldest climates | C: Chilled Beams (N), warm/moderate CZ | System | 5 | 4 | Commercial | Cooling | System | New commercial buildings | Energy Savings (%) | 20% | 0% | Yes | $8/sq.ft. |  |  | -1 | per square foot; 150 BTU/h/sq.ft | 7 C: No FS: All fuels heating and cooling | Total commercial heating and cooling in new buildings, except two coldest climates | 15 | 2011 | Roth, K., John, D., Zogg, R. & Brodrcik, J. Chilled Beam Cooling. ASHRAE Journal 84-86 (2007) Sachs, H..; Lin, W.; Lowenberger, A.; "Emerging Energy Savings HVAC Technologies and Practices for the Buildings Sector"; ACEEE (2009) | BTO Tool: Savings in building Vent, height can offset cost, assumed typical cost for 150 BTU/h @~$33/kBTU/h Appendix B: "a chiller dedicated for chilled beam cooling has a lower temperature lift and operates at a 15% to 20% higher efficiency than for an conventional system" Multiple sources provide 20% savings estimate; currently avilable technology provides price estimate at -$1/sq ft +/- $3/sqft | 3-3698 | 15 | 15 | AEO 2010 NEMS
141 | Demonstrate and deploy demand control ventilation in all commercial buildings | C: DCV | Use intensity | 5 | 4 | Commercial | Ventilation | Control | All | Energy Savings (%) | 20% | 0% | Yes | $617/zone, 5 zones, 3 RTUs |  | 0.17 | 0.17 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | All commercial HVAC energy use | 15 | 2012 | 1) pg. 92-96 of Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. Navigant Consulting (2011) 2) Cost of $617/zone or $0.17/SF from pg. 6 of Hong, T. Fisk, W. Assessment of Energy Savings Potential form the Use of Demand Control Ventilation Systems in General Office Spaces in California. LBNL. July 8, 2009. 3) Data confirmed by pg. 2&8, of Demand-Controlled Ventilation Using CO2 Sensors. Federal Technology Alert. DOE/EE-0293. March 2004. |  | 3-3617 | 15 | 15 | AEO 2010 NEMS
142 | Demonstrate and deploy displacement ventilation in new commercial buildings | C: Disp. Ventilation (N) | System | 5 | 2 | Commercial | Heating & Cooling | Ducts | New | Energy Savings (%) | 10% | 0% | Yes | See pumps/fans |  |  | 1 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | Total HVAC load in new commercial buildings | 20 | 2015 | Primary Source: Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. (2011) [Cost and efficiency values from page 118] Awbi, Energy Efficient Room Air Distribution ; Renewable Energy (15); Argon Air | BTO Tool: Applies to new commercial buildings only; all HVAC Appendix B: Technical Energy-Savings Potential: 0.17 Quads ~10% system energy savings. Costs from Argon Air estimate to install in new building | 3-3639 | 20 | 20 | AEO 2010 NEMS
143 | Demonstrate and deploy DOAS (dedicated outdoor air systems) with ERV (Energy Recovery Ventilation) in all commercial buildings | C: DOAS w/ ERV | Use intensity | 5 | 4 | Commercial | HVAC | System | Office buildings | Energy Savings (%) | 10%heating, 17% cooling over VAV | 0% | Yes | -2 years over VAV |  | 0.08 | 0.0825 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | Total commercial HVAC energy consumption in all office buildings | 15 | 2013 | PNNL technical support document 19341, MGAE Primary Source: BA Thornton; W Wang; Y Huang; MD Lane; B Liu; "Technical Support Document: 50% Energy Savings for Small Office Buildings" | BTO Tool: 2 years savings @$3.3B/year for all 80 B sq.ft (BEDB); 80/20 heating cooling split; 10%heating, 17% cooling over VAV Appendix B: Caclualted from data in chapter 5 | 4-3602 | 15 | 15 | AEO 2010 NEMS
144 | Demonstrate and deploy dual source heat pumps in homes in non-coldest climates, no fuel switching | R: Dual Source HP | System | 5 | 4 | Residential | Heating & Cooling | Heat pump | Climate zones 2-5 | Energy Savings (%) | 34.3% | 0% | Yes | $3000/ton ground | 4680 | 7560 | 2880 | per home; 3 ton total, 2 ton ground | 1 C/R: No FS: All electric to all electric | Electric heating, proportion of cooling not in coldest 2 climates | 18 | 2013 | FEMP Technology alert DOE/E-0220; savings and costs relative to ASHP. Ground loop from Navigant 2009 (Ground‐Source Heat Pumps: Overview of Market Status, Barriers to Adoption, and Options for Overcoming Barriers) $3000/ton for residential retrofit. Baseline cost from NREL Retrofit Measures Database. Primary Source: Hadley, D., Collins, T., Parkerk, S., Cornett, G. & Cavedo, F. Energy Savings from Dual-Source Heat Pump Technology Federal Energy Management Program E-0220 (2000) | BTO Tool: Savings over ASHP: 38% heating, 15% cooling. Cost of system based on 2/3 GSHP and 1/3 ASHP. Appendix B: "At the main U.S. Post Office facility in Valrico, three air- source heat pumps were retrofitted with the dual-source technology, reducing daily energy use by nearly 38%" Multiple case studies used for average of 34% savings from ASHP | 1-105 | 18 | 18 | AEO 2014 NEMS
146 | Demonstrate and deploy dual source heat pumps in commercial buildings in non-coldest climates, no fuel switching | C: Dual Source HP | System | 5 | 4 | Commercial | Heating & Cooling | Heat pump | Climate zones 2-5 | Energy Savings (%) | 34.3% | 0% | Yes | $7000/ton ground | 8.65 | 11.1542 | 2.5042 | per square foot; 40 ton total, 10 ton ground assumed for 15,000 sq.ft. buildings | 1 C/R: No FS: All electric to all electric | Electric space heating, proportion of cooling, excluding coldest climate | 15 | 2013 | FEMP Technology alert DOE/E-0220; savings relative to ASHP. Baseline cost from RS Means Assemblies Cost Data, 33rd Edition ($8.65 for 40 ton packaged rooftop heat pump, including ductwork and controls). ORNL Residential Retrofti Tech potential ($7000/ton for commercial retrofit) Primary Source: Hadley, D., Collins, T., Parkerk, S., Cornett, G. & Cavedo, F. Energy Savings from Dual-Source Heat Pump Technology Federal Energy Management Program E-0220 (2000) | BTO Tool: Savings over ASHP: 38% heating, 15% cooling Appendix B: "At the main U.S. Post Office facility in Valrico, three air- source heat pumps were retrofitted with the dual-source technology, reducing daily energy use by nearly 38%" Multiple case studies used for average of 34% savings from ASHP | 3-3738 | 15 | 15 | AEO 2010 NEMS
147 | Demonstrate and deploy improved ground coupling in GSHP in homes | R: Enhance ground HX effectiveness | Heat exchanger | 2+ | 1 | Residential | Heating & Cooling | Heat pump |  | Energy Savings (%) | 30% | 0% | Yes | Not on market |  |  |  | per unit | 1 C/R: No FS: All electric to all electric | Total residential geothermal heating and cooling | 18 | 2017 | ORNL Fact sheet |  | 1-176 | 18 | 25 | AEO 2014 NEMS
148 | Demonstrate and deploy improved ground coupling in GSHP in commercial buildings | C: Enhance Ground HX Effectiveness | Heat exchanger | 2+ | 1 | Commercial | Heating & Cooling | Heat pump |  | Energy Savings (%) | 30% | 0% | Yes | Not on market |  |  |  | per square foot | 1 C/R: No FS: All electric to all electric | Total commercial ground source heat pump (GSHP) load | 25 | 2017 | ORNL Fact sheet |  | 3-3631 | 25 | 25 | AEO 2010 NEMS
149 | Demonstrate 50% more efficient building designs with no capital cost increase | C: 50% whole building savings, same capital cost | System | 5 | 2 | Commercial | All End Uses | System | New | Energy Savings (%) | 50% | 0% | No | Immediate payback |  | 0.14286 | 0.14286 | per square foot | 60 C: No FS: All fuels/end-uses | All energy consumption in new buildings | 40 | 2015 | NREL Commercial Buildings team | BTO Tool: Represents R&D effort to improve building designs | 3-3633 | 40 | 40 | AEO 2010 NEMS
152 | Demonstrate and deploy attic radiant barrier in existing homes | R: Attic Radiant Barrier, 4% (E) | Roof | 5 | 3 | Residential | HVAC | Roof/ attic insulation | Pre-2010 homes heating and Cooling lost through attic | Energy Savings (%) | 4.286% | 0% | Yes | $0.12/sq.ft | 152.712 | 0 | 152.712 | per home | 36 R: No FS: Roof specific | Total heating and cooling lost through attics in homes built before 2010 | 30 | 2013 | Next generation troofs.pdf; itron pdf Primary Source: Miller, W. & Kosny, J. Next-Generation Roofs and Attics for Homes. ACEEE Summer Study on Energy Efficiency in Buildings 180-195 (2008) | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: Assumed 2/7ths of white roof impact of 15%; 30x30 2 story house with 30% pitched roof Appendix B: Analyzed savings for ducts and attic laods scaled to national average using existing stock as base | 1-106 | 30 | 30 | AEO 2014 NEMS
153 | Replace all commercial lighting with LEDs | C/I: LED (replace all) | System | 5 | 4 | Commercial/Industrial | Lighting | Lamp | All | lumens/watt | 95 | 68 | Yes | Standard and efficient unit costs are first costs; incremental cost includes relamping an maintenance calculations. | 97.5 | 498.05 | 358.05 | per luminaire | 1 C/R: No FS: All electric to all electric | All lighting in all types of commercial and industrial buildings | 5 | 2013 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 3-3446 | 5 | 13 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
154 | Replace all residential lighting with LEDs | R: LED (replace all) | Lamp | 5 | 4 | Residential | Lighting | Lamp | All | lumens/watt | 76 | 26 | Yes | Standard and efficient unit costs are first costs; incremental cost includes relamping an maintenance calculations. | 2.88 | 25.34 | -28.97 | per lamp | 1 C/R: No FS: All electric to all electric | Total lighting energy consumption in all homes | 2 | 2013 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization 4) Daily operating hours from the PNNL: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/2012_residential-lighting-study.pdf | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 1-73 | 2 | 43 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
155 | Demonstrate and deploy radiant flooring systems in new homes | R: Radiant Heat (N) | Use intensity | 5 | 3 | Residential | Heating | Radiant floor | New | Energy Savings (%) | 9.5% | 0% | Yes | $10/sq.ft. | 3000 | 10000 | 7000 | per home; 1,000 square feet | 5 R: No FS: All fuels HVAC (heating+cooling, no separate ventilation component) | Forced hot air systems in new homes | 20 | 2012 | http://www.radiantec.com/why/technical-explanation.php Primary Source: Watson, Richard D. Advantages of radiant heat. Fine Homebuilding June-July 1992. http://www.radiantec.com/why/technical-explanation.php Robert Hendron, Ed Hancock; Greg Barker; Paul Reeves. 2006. An Evaluation of Affordable Prototype Houses at Two Levels of Energy Efficiency. NREL/CP-550-38774. Joseph D'agnese. 2009. Radiant Floor Heating. This Old House magazine. http://www.thisoldhouse.com/toh/article/0,,1548320,00.html | BTO Tool: Assumed 1000 sq.ft. heated (i.e., portion of house) vs. $3000 installed for ducts, "When applied to the sizing of a radiant system, conventional heat-loss analysis often includes a reduction in design temperature from 70°F to 65°F and a 10% to 25% reduction in building air infiltration, infiltration, stratification and glass heat loss. The average 65°F radiant comfort temperature with 59°F day/night setback should reduce building heat load by 25% to 35% over convective systems.", Richard D. Watson, research chairman of the ASHRAE Radiant Heating and Cooling Technical Committee Appendix B: Watson: Assumed 1000 sq.ft. heated at $10/ft2 vs. $3000 installed for ducts, "The average 65°F radiant comfort temperature with 59°F day/night setback should reduce building heat load by 25% to 35% over convective systems." Hendron: Radiant vs forced air in two similar houses indicated about 3% heating energy savings, to achieve equivalent mean radiant temperature, plus additional savings for water pump vs air handler fan, and for reduced infiltration. 9.5% is the geometric mean of the two studies. D'agnese: "Hot-water radiant costs more to install than other types of heating systems—from $6 to $15 per square foot depending on the method, whether you're starting from scratch or retrofitting, and where you live." Assumed 1000 sq.ft. heated at $10/ft2 vs. $3000 installed for ducts, | 1-107 | 20 | 80 | AEO 2014 NEMS
156 | Move to standardize improved duct routing in residential codes | R: Duct Routing (N) | Distribution | 5 | 4 | Residential | HVAC | Ducts | New | Duct efficiency | 80% | 67% | No | 0 |  |  | 0 | per home | 5 R: No FS: All fuels HVAC (heating+cooling, no separate ventilation component) | Forced hot air systems in new homes | 20 | 2010 | BTP Technology Fact Sheet Primary Source: Southface Energy Institute, FEMP Technology Alert: Air Distribution System Design, 2003 | Expected & new equipment lifetime value are based on an assumption that these last 20 years. We do not have a good source to support this assumption. Appendix B: Southface: "The efficiency of air distribution systems has been found to be 60-75% or less; Properly designed and installed duct systems can have efficiencies of 80% or more for little or no additional cost." Savings estimate is 16%=1-0.675/0.8 | 1-107 | 20 | 20 | AEO 2014 NEMS
157 | Move to standardize improved duct routing in commercial codes | C: Duct Routing (N) | Distribution | 5 | 4 | Commercial | HVAC | Ducts | New | Duct efficiency | 80% | 67% | No | 0 |  |  | 0 | per square foot | 7 C: No FS: All fuels heating and cooling | All furnaces and A/C heating and cooling (i.e., ducts) in new commercial buildings | 20 | 2010 | BTP Technology Fact Sheet Primary Source: Southface Energy Institute, FEMP Technology Alert: Air Distribution System Design, 2003 | Expected & new equipment lifetime value are based on an assumption that these last 20 years. We do not have a good source to support this assumption. Appendix B: Southface: "The efficiency of air distribution systems has been found to be 60-75% or less; Properly designed and installed duct systems can have efficiencies of 80% or more for little or no additional cost." Savings estimate is 16%=1-0.675/0.8 | 3-3669 | 20 | 20 | AEO 2010 NEMS
161 | Demonstrate and deploy minisplit heat pumps in homes | R: Minisplits | System | 5 | 4 | Residential | Heating & Cooling | Heat pump | All heating and cooling | Energy Savings (%) | 40% | 0% | Yes | ACEEE claims 30% price premium | 4680 | 6084 | 1404 | per home; 3 tons capacity (3 indoor units for mini-split) | 1 C/R: No FS: All electric to all electric | Total electric heating and cooling in all homes | 20 | 2012 | ACEEE; BOA report; NREL measure database for standard A/C cost Primary Source: Geraghty, K., Baylon, D. & Davis, B. Residential Ductless Mini-Split Heat Pump Retrofit Monitoring. Bonneville Power Administration (2009). Desroches, L.-B. et al. Max Tech and Beyond, Appendix F. Lawrence Berkeley National Laboratory (2011). | Appendix B: Geraghty: Table 4 suggests 44% savings for heating; Table 6- total savings of 28% Price from google seach suggests ~30% price premium | 1-108 | 20 | 20 | AEO 2014 NEMS
162 | Move to standardize variable air volume (VAV) ventilation | C: Move from CAV to VAV | System | 5 | 4 | Commercial | HVAC | System | Large office buildings; assembly rooms, auditoriums, and lecture halls; large retail buildings and shopping malls; movie theaters; restaurants, bars and nightclubs; banks; outpatient areas in hospital; and hotel atriums or lobbies. | Energy Savings (%) | 25% | 0% | No | 400 |  |  | 0.26667 | per square foot | 1 C/R: No FS: All electric to all electric | All constant air volume (CAV) ventilation in all commercial buildings | 20 | 2013 | Estimated incremental cost and energy savings were calculated by Phil based on detailed NEMS data tables and Indoor Air Quality Building Education and Assessment Model (I-BEAM). Energy Information Administration. http://www.epa.gov/iaq/largebldgs/i-beam/text/hvac.html#F6.1 |  | 3-3632 | 20 | 20 | AEO 2010 NEMS
168 | Research, demonstrate, and deploy homes that meet Passivhaus specifications | R: Ultra-efficient design (e.g., Passivhaus) | System | 5 | 3 | Residential | All End Uses | System | Limited | Energy Savings (%) | 66% | 0% | No | 12.7% increase in first cost | 102.9412 | 116.0147 | 23532.3529 | per home (1800 sq. ft.) | 59 R: No FS: All fuels/end-uses | Total residential energy consumption in all new homes | 30 | 2013 | Passivehouse.us | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: Zillow gives 1700 sq. ft. home at $220,000 w/ lot at $45,000 | 1-1 | 30 | 30 | AEO 2014 NEMS
171 | Move to include building commissioning in new commercial buildings (data for bldgs>100,000SF, taken as max cost & savings for the market for all new bldgs) | C: Commissioning (N) | Maintenance | 5 | 5 | Commercial | Building | Whole building | new | Energy Savings (%) | 13% | 0% | Yes |  | 0 | 1.16 | 1.16 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | Total HVAC load in new commercial buildings | 5 | 2010 | "Building Commissioning: A Golden Opportunity for Reducing Energy Costs and Greenhouse Gas Emissions", Mills, E.; Energy Efficiency (2011) 4:145–173 Other Supporting Sources: Mills, E., Friedman, H., Powell, T., Bourassa, N., Claridge, D., Haasl, T., & Piette, M. A. (2004). “The cost-effectiveness of commercial-buildings commissioning: A meta-analysis of energy and non-energy impacts in existing buildings and new construction in the United States.” Lawrence Berkeley National Laboratory Report No.56637 http://cx.lbl.gov/2004-assessment.html. | BTO Tool: 5 years of persistent savings Appendix B: Table 3 indicates total primary energy savings in new buildigns of 13% | 3-3639 | 5 | 5 | AEO 2010 NEMS
180 | Increase deployment of Energy Star 2011 CFLs for residential general use lighting in place of incandescents and halogen | R: Energy Star CFLs | Lamp | 5 | 5 | Residential | Lighting | Lamp | Incandescent and halogen | lumens/watt | 55 | 15 | Yes | Typical residential lamp provides 800 lumens. First cost of a CFL is estimated at $3.4/klm, while an incandescent is $0.6/klm. | 1.2 | 2.72 | -7.05 | per lamp | 1 C/R: No FS: All electric to all electric | Total residential incandescent and halogen General Service Lamp (GSL) Medium Screw Bulb (MSB) lighting | 2 | 2010 | 1) 2010 U.S. Lighting Market Characterization; 2012 Energy Savings Potential of SSL 2) Daily operating hours from the PNNL: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/2012_residential-lighting-study.pdf | 1) Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". 2) Base and efficient unit performance were slightly adjusted to match EIA Tech Forecast, the costs were not changed because this change was very small. 3) Base unit performance more closely reflects incadescent bulbs, however, halogen is not significantly higher in efficacy, typically 14.7-20.1 lum/watt. The market for these is significantly smaller. | 1-180 | 2 | 17 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
181 | Research, develop, and demonstrate daylight-responsive dimming (Photosensor-Based Lighting Controls) in commercial buildings | C: Perimeter Zone Day Lighting | Controls | 5 | 4 | Commercial | Lighting | Lighting controls | All | Energy Savings (%) | 40% | 0% | Yes | See existing & efficient costs | 0 | 184.9315 | 184.9315 | per fluorescent lamp | 1 C/R: No FS: All electric to all electric | All commercial fluorescents in a perimeter zone | 5 | 2013 | Cost from PNNL 2005, K-12 Schools AERG (draft) Primary Source: Brambley, M. et al. Advanced sensors and controls for building applications: Market assessment and potential R&D pathways. Energy 156 (2005).at <http://citeseerx.ist.psu.edu/viewdoc/download?doi=10.1.1.111.8772&amp;rep=rep1&amp;type=pdf> | BTO Tool: Used average of $1.60 per sq-ft for 80 billion square feet, and $3.79 for K-12 Schools AERG. Assumes dimmable ballasts must be installed. Assumes 3080 fluorescent lamps per 211,000 ft2 (0.0146 lamps/ft2) based on the K-12 Schools AERG. Appendix B: PNNL page 2.23: "A report by the EPA (2001) suggests that daylit offices can achieve up to 35%-40% savings, and that other daylit spaces (classrooms, grocery stores, and retail outlets) can achieve 40%-60% savings." and used $1.60 per sq-ft for 80 billion square feet | 3-3471 | 5 | 5 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
182 | LEDs for holiday lights | R/C: LED Holiday Lights | System | 5 | 4 | Residential and Commercial | Lighting | Lighting | Holiday Lights | Energy Savings (%) | 70% | 0% | Yes | First cost for one string of LED holiday lights is estimated at $8, while incandescent mini lights are $2 | 38 | 8 | -30 | per string | 1 C/R: No FS: All electric to all electric | Total energy use by residential decorative light strings | 3 | 2013 | Energy.gov LED Lighting - Holiday Lights, http://energy.gov/energysaver/articles/led-lighting | For standard unit cost derivation, see Lighting Measures_Relamp and Labor Costs 07 01 2013 spreadsheet (created by Mary) in 2013 TDM Mtg Folder-Lighting | 1-160 | 3 | 86 | Other
184 | Increase deployment of replacement of incandescent lighting with CFLs for commercial lighting | C: CFLs | Lamp | 5 | 5 | Commercial | Lighting | Lamp | Incadescent | lumens/watt | 53 | 9.6 | Yes | Typical A-type lamp provides 800 lumens. First cost of a CFL is estimated at $3.4/klm, while an incandescent is $0.6/klm. | 1.2 | 2.72 | -7.05 | per lamp | 1 C/R: No FS: All electric to all electric | All commercial incandescent | 0.36 | 2010 | 2010 U.S. Lighting Market Characterization; 2012 Energy Savings Potential of SSL | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 1-2735 | 0.36 | 2.6 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
185 | Demonstrate and deploy dimmable instant start ballasts in commercial and industrial lighting | C/I: Dimmable Instant-Start Ballasts | Ballasts | 5 | 2 | Commercial/Industrial | Lighting | Lighting ballast | Fluorescents | Energy Savings (%) | 15% | 0% | Yes | 31.19 | 10.89 | 31.19 | 20.3 | per ballast | 1 C/R: No FS: All electric to all electric | All commercial linear fluorescent lighting (T-12, T-8, T-5) | 5 | 2016 | Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005). | BTO Tool: Compares to $12.87 for Rapid-Start and $8.91 for Instant-Start Appendix B: Table 3-13: Technical Potential Energy Savings of Dimmable Instant-Start Ballasts and Table 3-14: Ballast Price, by Type | 3-3431 | 5 | 5 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
188 | Residential and commercial fluorescent lighting ballast standard, effective in 11/2011 with compliance date of 11/2014. | C/R: Electronic Ballast Standard (2014) | Ballasts | 5 | 5 | Residential and Commercial | Lighting | Lighting ballast | Fluorescents / Magnetic ballasts | Energy Savings (%) | 6.97% | 0% | Yes | Costs per ballast | 7.32 | 7.45 | 0.13 | per ballast; 2 lamps in stock per ballast | 1 C/R: No FS: All electric to all electric | All residential and commercial fluorescent lighting (GSL medium screw CFL MSB, CFL Reflector, T12, T8, T5, and other miscellaneous fluorescent lamps). | 5 | 2014 | Navigant Consulting & Pacific Northwest National Laboratory Final Rule Technical Support Document Energy Conservation Program for Consumer Products and Certain Commercial And Industrial Equipment: Fluorescent Lamp Ballasts. Department of Energy (2011) | Matthew Walker (NCI): "Electronic ballast is going to be the norm for most shipments already; 7% savings is the impact of the 2011 ballast rulemaking, will be effective in Nov 2014. At this point you are looking for improved electronics, not so much an elec to mag switch." | 1-75 | 5 | 5 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
190 | Demonstrate elimination of constant electrode heating resulting in more efficient commercial and industrial ballasts | C/I: Elimination of Constant Electrode Heating | Ballasts | 5 | 2 | Commercial/Industrial | Lighting | Lighting ballast | Fluorescents | Energy Savings (%) | 5% | 0% | No | 31.19 | 10.89 | 31.19 | 20.3 | per unit | 1 C/R: No FS: All electric to all electric | Rapid-Start/Dimming Ballasts, Comm/Industrial | 23 | 2016 | Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005). | BTO Tool: Compares to $12.87 for Rapid-Start and $8.91 for Instant-Start Appendix B: Page 38: "With the elimination of constant electrode heating, these values would decline to 37 watts and 38 watts, respectively, correlating to a 5% decrease in energy consumption. A 5% decrease in energy consumption would result in energy savings of 0.01 quad per year." and Table 3-16: Ballast Price, by Type Lifetime is based on recent rulemaking TSD Life Cycle Cost Analysis Chapter. | 3-3415 | 23 | 23 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
193 | Deploy HID ceramic arc tubes to replace mercury vapor (MV) and quartz metal halide (MH) lamps in all sectors | C/R/I/O: Ceramic HID Arc Tube to replace MV & quartz MH | Lamp | 3 | 2 | Commercial/Industrial/Outdoor/Residential | Lighting | Lamp | MV and MH | lumens/watt | 67.5 | 56 | No | 38 | 35 | 38 | 3 | per lamp | 1 C/R: No FS: All electric to all electric | All residential mercury-vapor and metal halide HID lighting | 23 | 2016 | Navigant 2005 Lighting Market Characterization II; Navigant 2002 Lighting Market Characterization I | BTO Tool: Compares to Quartz Metal Hallide at $35 Lifetime is based on recent rulemaking TSD Life Cycle Cost Analysis Chapter. | 1-161 | 23 | 23 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
195 | Deploy HID dimmable ballasts in commercial, industrial, and outdoor HID and fluorescent lighting | C/I/O: HID Dimmable Ballasts to replace HID and Fluorescents | Ballasts | 5 | 3 | Commercial/Industrial/Outdoor | Lighting | Lighting ballast | HIDs/Fluorescents | Energy Savings (%) | 15% | 0% | No | 223 | 98 | 223 | 125 | per ballast | 1 C/R: No FS: All electric to all electric | HIDs and Fluorescents - Dimmable Ballasts (Comm/Indust/Outd) | 20 | 2013 | Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005). | BTO Tool: approximately $125 more than a 400-watt CWA ballast (Advance Transformer, 2003). Appendix B: Table 3-45: Technical Potential Energy Savings of HID Dimmable Ballasts and page 84: "A cost estimates for a400-watt electronic ballast is $223, approximately $125 more than a 400-watt CWA ballast (Advance Transformer, 2003)." Lifetime is based on recent rulemaking TSD Life Cycle Cost Analysis Chapter. | 3-3420 | 20 | 20 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
200 | Demonstrate HID instant restrike to enable HIDs to have larger market share over incandescent and halogen lamps in commercial and industrial applications | C/I: HID Instant Restrike | Ballasts | 5 | 2 | Commercial/industrial | Lighting | Lighting ballast | Incandescent/Halogen with similar reqs for color rendering | lumens/watt | 85 | 24.8 | No | 25 |  |  | 92.5926 | per lamp | 1 C/R: No FS: All electric to all electric | Incandescents/Halogen for HID instant restrike (Comm/Indus) | 0.36 | 2016 | Navigant 2005 Lighting Market Characterization II | BTO Tool: Range from $16-$33 | 3-3424 | 0.36 | 0.36 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
202 | Research HID novel gas as a replacement to incandescents in commercial lighting | C: HID Novel Gas (e.g. Cesium) | Lamp | 5 | 1 | Commercial | Lighting | Lamp | Incandescent | lumens/watt | 45 | 24.8 | No | 41 | 13.68 | 41 | 101.1852 | per lamp | 1 C/R: No FS: All electric to all electric | Incandescent | 0.36 | 2018 | Navigant 2005 Lighting Market Characterization II | BTO Tool: Compares to $26.38 metal halide; $0.98 incandescent, A type | 3-3425 | 0.36 | 0.36 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
204 | Standardize high efficiency ballasts in fluorescent lights in commercial and residential buildings | C/R: High-efficiency ballasts | Ballasts | 5 | 4 | Residential and Commercial | Lighting | Lighting ballast | Fluorescents | Electricity consumption (W/ballast) | 48.5 | 54.5 | Yes | 25 | 16 | 25 | 9 | per ballast | 1 C/R: No FS: All electric to all electric | All residential and commercial fluorescent lighting (GSL medium screw CFL MSB, CFL Reflector, T12, T8, T5, and other miscellaneous fluorescent lamps). | 5 | 2010 | Universal Lighting Technologies http://www.unvlt.com/literature/flyers/he-el_flyer.pdf; http://www.unvlt.com/literature/brochures/ultim8_brochure.pdf Primary Source: Universal Lighting Technologies, "Triad High Efficiency System". Manufacturer (2011) | BTO Tool: 2 Lamp 120/277 volt instant start high efficiency Maxlite for F28T8 fluorescents Appendix B: Differencey between Triad and standard electric balast averaged between 0.78 and 0.88 ballast factors | 1-75 | 5 | 5 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
206 | Deploy wireless occupancy sensors and corresponding wireless lighting snap-on relay in commercial buildings | C: Wireless Lighting Occ. Sensor System | Controls | 5 | 4 | Commercial | Lighting | Lighting controls | All | Energy Savings (%) | 13% | 0% | Yes | $175/controller, $.08/ft2 from K-12 Schools (AERG); $24/controller, $0.014/ft2 (NCI) | 0 | 0.05 | 0.05 | per square foot; one controller per 4 luminaires | 1 C/R: No FS: All electric to all electric | All commercial lighting, per square foot stock | 5 | 2010 | 1) Pg. 173 from Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005). 2) Costs obtain from pg. 121, NREL. 2011. Advanced Energy Retrofit Guide for K-12 Schools (Draft). EERE Report DOE/GO-102011-3467. Project Lead: Robert Hendron 3) Pg 2.21 from Brambley, M. et al. Advanced sensors and controls for building applications: Market assessment and potential R&D pathways. Pacific Northwest National Laboratory (2005). |  | 3-3456 | 5 | 5 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
208 | Decrease cost & deploy indirect, active solar water heating with gas back up to commercial buildings (no fuel switching) | C: Solar WH Ind Act, Gas BU | System | 5 | 4 | Commercial | Water Heating | Solar WH: indirect, active | All | Energy Savings (%) | 61% | 0 | Yes | 103.61/sqft compressed 50% as per roadmap |  | 24710.985 | 24710.985 | per unit; 477 square feet absorber | 2 C/R: No FS: All gas to all gas | Total energy consumption by all commercial gas storage water heaters | 13 | 2013 | Itron, Inc.; "California Center for Sustainable Energy Solar Water Heating Pilot Program" (3/2011) Federal Energy Management Program, "Solar Water Heating with Low-Cost Plastic Systems" (1/2012) Other Supporting Sources: Hudon, Burch "Solar Water Heating Roadmap" (in preperation) | BTO Tool: 3% end use penalty for 40W pump (scaled to 2 % for 20W design) Appendix B: Thorough analysis of multiple sources; represents aggregate savings net of parasitic loads Costs represent program targets informed by roadmap (in preperation) | 3-3561 | 13 | 13 | AEO 2010 NEMS
209 | Demonstrate and deploy integrated white LED package for residential and commercial lighting | C/R: Integrated White LED Package | Lamp | 5 | 3 | Commercial/Residential/Industrial | Lighting | Lamp | All | Quads consumed | 2.8 | 8.3 | No | 40 | 15 | 40 | 25 | per lamp | 1 C/R: No FS: All electric to all electric | Total residential and commercial lighting | 3 | 2007 | Navigant 2005 Lighting Market Characterization II -- assumes access to 20% of sockets in lighting market | BTO Tool: A single high-brightness LED element from Luxeon costs about $8; this does not include the added costs of drive electronics, system package, and distributor mark ups. | 1-182 | 3 | 3 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
210 | Efficient power supplies (aggregated other measures) | C/R: Improved power supplies | Other | 5 | 2 | Residential and Commercial | MELs | Desktop PCs | All | Energy Savings (%) | 25% | 0% | No | 32 |  |  | 32 | per unit | 1 C/R: No FS: All electric to all electric | Total energy use by residential desktop PCs | 4 | 2015 | TIAX 2004 | BTO Tool: Incremental cost | 1-40 | 4 | 4
211 | Max tech desktop (combining other measures) | C: Max tech desktop | Computer | 5 | 2 | Commercial | MELs | Desktop PCs | All | Energy Savings (%) | 80% | 0% | No | See existing & efficient costs | 490 | 882.625 | 392.625 | per unit | 1 C/R: No FS: All electric to all electric | Total energy use by residential desktop PCs | 4 | 2015 | TIAX 2007, 2004, ACEEE 2009 Primary Source: Roth, K.W., Mckenney, K., Ponoum, R. & Paetsch, C. Residential Miscellaneous Electric Loads: Energy Consumption Characterization and Savings Potential. Energy 197 (2007). Other Supporting Sources: Cost data are from google searches of commercially available appliances | BTO Tool: Sum of all desktop related measures Appendix B: Table 4-20: Personal Computers Summary | 1-40 | 4 | 4 | AEO 2010 NEMS
212 | Research, demonstrate and deploy low-wattage HID lighting as replacement to incandescent | C/R: Low-Wattage HID | Lamp | 5 | 2 | Residential and Commercial | Lighting | Lamp | All | lumens/watt | 85 | 24.8 | No | 40 | 0.8 | 6.6667 | 5.8667 | per lamp | 1 C/R: No FS: All electric to all electric | Total residential and commercial incandescent lighting (MSB, reflectors, and other) | 0.36 | 2015 | Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005). Other Supporting Sources: Cost data are from google searches of commercially available appliances | Appendix B: Table 3-26: Technical Potential Energy Savings of Low-Wattage MH Lamps. "The GE ceramic MH lamp has an efficacy of 85 lm/W, and would replace a miniature halogen lamp that has an efficacy of 21 lm/W" | 1-181 | 0.36 | 0.36 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
213 | Demonstrate and deploy Metal Halide Electronic Ballasts for use in commercial, industrial and outdoor lighting | C/I/O: Metal Halide Electronic Ballasts | Ballasts | 5 | 3 | Commercial/Industrial/Outdoor | Lighting | Lighting ballast | HIDs | Energy Savings (%) | 25% | 0% | No | 140 | 80 | 140 | 60 | per ballast | 1 C/R: No FS: All electric to all electric | MH (C,I,O) | 23 | 2010 | Navigant 2005 Lighting Market Characterization II | BTO Tool: Over a ten-year period, the electronic pulse-start ballast system results in cost savings of 36% over a probe-start magnetic probe-start ballast system and 17% over a magnetic pulse-start ballast system. Lifetime is based on recent rulemaking TSD Life Cycle Cost Analysis Chapter. | 3-3422 | 23 | 23 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
215 | Demonstrate and deploy LED PARs as replacement for incandescent reflectors in residential, commercial, industrial and outdoor lighting | R/C/I/O: PAR LEDs | Lamp | 5 | 4 | Commercial/Industrial/Outdoor | Lighting | Lamp | Incandescent and halogen reflector lamps | lumens/watt | 67 | 15 | Yes | Standard and efficient unit costs are first costs; incremental cost includes relamping an maintenance calculations. | 4.7 | 39.5 | -12.2 | per lamp | 1 C/R: No FS: All electric to all electric | All residential, commercial, industrial and outdoor reflector lamps | 2 | 2013 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 1-162 | 2 | 23 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
216 | Display innovative power management for desktop PCs and TVs | R: Display Power Management | Computer | 5 | 2 | Residential | MELs | TVs, computers | All | Energy Savings (%) | 20% | 0% | No | See incremental cost |  |  | 0.8 | per unit | 1 C/R: No FS: All electric to all electric | All commercial and residential computers and TVs for power management | 4 | 2018 | Personal communication: Nordman, LBNL (12/2010) | Appendix B: 20% savings, very low costs relative to savings, usually several orders of magnitude difference (using benefit/cost ratio of 100) | 1-89 | 4 | 4 | AEO 2014 NEMS
218 | Deploy hard-wired occupancy sensors to reduce energy use for commercial lighting | C: Hard-wired lighting occupancy sensors | Controls | 5 | 4 | Commercial | Lighting | Lighting controls | All | Energy Savings (%) | 13% | 0% | Yes | Installed costs estimated from main source at 0.034; alternate at $0.11/ft2 - $0.56/ft2 | 0 | 0.335 | 0.335 | per square foot | 1 C/R: No FS: All electric to all electric | All commercial lighting, per square foot stock | 5 | 2010 | PNNL 2005 Primary Source: Leach, M., Hale, E., Hirsch, A. & Tocellini, P. Grocery Store 50 % Energy Savings Technical Support Document Grocery Store 50 % Energy Savings Technical Support Document. 174 (2009). Other Supporting Sources: Brambley, M. et al. Advanced sensors and controls for building applications: Market assessment and potential R&D pathways. Pacific Northwest National Laboratory (2005). | BTO Tool: Estimated at 1-5 year simple payback, 10-55% market penetration; Partial requirement in ASHRAE 2010 Appendix B: Energy savings assumed the same as Measure 206. Cost of $0.36/ft2 based the Grocery Store TSD. | 3-3456 | 5 | 5 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
219 | Demonstrate and deploy off-grid luminaires for outdoor lighting | O: Solar outdoor lighting | System | 5 | 2 | Outdoor | Lighting | Lighting: lamp | All | Energy Savings (%) | 100% | 0% | No | See incremental cost |  |  | 80.03 | per luminaire | 1 C/R: No FS: All electric to all electric | All lighting, Outdoor | 8 | 2013 | Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005). Other Supporting Sources: Cost data are from google searches of commercially available appliances | Appendix B: Page 193: "Off-grid luminaires would affect energy consumption in the outdoor stationary sector, essentially taking it 100% off grid, reducing energy used from 0.6 quad (NCI, 2002) to 0 quad (technical potential energy savings, primary energy)." | 3-3428 | 8 | 8 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
220 | Deploy personal controls over lighting in commercial buildings | C: PDA lighting controls | Controls | 5 | 4 | Commercial | Lighting | Lighting controls | Office, fluorescent/incandescent | Energy Savings (%) | 25% | 0% | Yes | See incremental cost |  |  | 57 | per ballast; 4 lamps per luminaire | 1 C/R: No FS: All electric to all electric | Fluorescent/Incandescent, Commercial office | 3.87 | 2010 | Navigant 2005 Lighting Market Characterization II |  | 3-3429 | 3.87 | 3.87 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
221 | Deploy personal controls over lighting in residential buildings | R: PDA lighting controls | Controls | 4 | 4 | Residential | Lighting | Lighting controls | Fluorescent/incandescent | Energy Savings (%) | 5% | 0% | Yes | $2500/home |  |  | 2500 | per home | 1 C/R: No FS: All electric to all electric | Total lighting energy consumption in all homes | 5 | 2010 | Navigant 2005 Lighting Market Characterization II | Lifetime is based on recent rulemaking TSD Life Cycle Cost Analysis Chapter. | 1-73 | 5 | 5 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
222 | Move from standardized T-12 lighting to T-8 in commercial, industrial and outdoor lighting | C/I/O: T-12 to T-8 Standard (2014) | System | 5 | 5 | Commercial/Industrial/Outdoor | Lighting | Lamp | T12 Fluorescents | lumens/watt | 90 | 78 | No | Ballast Retail Price(2012): T-12 - $16.47; T-8: $17.67; Lamp Retail Price (2012): T-12 - $12.9; T-8 $7.06. Two lamps per ballast, hence incremental cost is calculated to be the (ballast+2lamps)/2 | 14.7 | 12.37 | -2.33 | per lamp | 1 C/R: No FS: All electric to all electric | T12 Fluorescents, C/I/O | 5 | 2010 | FLB Final Rule TSD, Chapter 5, pg. 5-23 | A new standard goes into effect in 2014, which basically eliminates all T-12 lamps. | 3-3430 | 5 | 5 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
223 | Deploy spectrally enhanced lighting to commercial buildings | C: Spectrally Enhanced Lighting | Luminaire | 5 | 3 | Commercial | Lighting | Lamp | Fluorescents | Quads consumed | 1.97 | 2.37 | Yes | 4.95 | 3 | 4.95 | 1.95 | per lamp | 1 C/R: No FS: All electric to all electric | All commercial linear fluorescent lighting (T-12, T-8, T-5) | 5 | 2010 | Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005). | BTO Tool: Non spectrally-enhanced is $3 Appendix B: Table 5-3: Price of Lamps, Spectrally Enhanced vs. Non-Spectrally Enhanced | 3-3431 | 5 | 5 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
224 | Increase deployment of solid state lighting (SSL) signage fixtures in commercial lighting | C: SSL Signs | System | 5 | 5 | Commercial | Lighting | Lighting: lamp | Commercial Signs | Quads consumed | 0.012 | 0.112 | No | -1854.86 |  |  | -1854.86 | per sign | 1 C/R: No FS: All electric to all electric | All energy consumption of all types of commercial signs | 15 | 2010 | Primary Source: Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005). Other sources: Navigant 2008 Energy Savings LEDs Niche Apps. 3) Lifetime: 15 years from Niche LIghting Final Report. NCI. 2008. pg. 26 | Table 6-6: Summary Table for Utilization: Fixtures, "Monochromatic LEDs exhibit 80-90% energy savings over neon in signage fixtures." | 3-3432 | 15 | 15 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
226 | More efficient set-top boxes: Service Provider Pays (SPP) | R: Set-Top Box | Standby | 5 | 5 | Residential and Commercial | MELs | Set-top boxes | All | Energy Savings (%) | 25% | 0% | No | See incremental cost |  |  | 0.5 | per unit | 1 C/R: No FS: All electric to all electric | Total energy use by residential set-top boxes | 5 | 2010 | Personal communication: Nordman, LBNL (12/2010) | Appendix B: 25% savings, very low costs relative to savings, usually several orders of magnitude difference (using benefit/cost ratio of 100) | 1-84 | 5 | 5
229 | Replace commercial lighting with OLEDs - TARGET | C: OLEDs, SSL Program Goal (2020)* | System | 5 | 0 | Commercial | Lighting | Luminaire | All | lumens/watt | 190 | 67 | Yes | The DOE SSL Program goal is for OLED luminaires to reach a first cost of $50/klm by 2020. It is expected that there will be little to no change to commercial/industrial conventional lighting. This is estimated at a weighted average of $20/klm. Assume a 5000 lumen output is typical for commercial/industrial products. | 97.5 | 85 | -55 | per luminaire | 1 C/R: No FS: All electric to all electric | All lighting in all types of commercial and industrial buildings | 5 | 2020 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 3-3446 | 5 | 13 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
232 | Deploy switch-based occupancy sensors/fixture with a controller in residential buildings | R: Lighting Occ. Sensor/Fixture + ctrl | Controls | 5 | 4 | Residential | Lighting | Lighting controls | All | Energy Savings (%) | 10% | 0% | Yes | 44 | 0.56 | 44 | 5.43 | per sensor; one unit per 8 bulbs | 1 C/R: No FS: All electric to all electric | Total lighting energy consumption in all homes | 5 | 2010 | Navigant Consulting U . S . Lighting Market Characterization Volume II: Energy Efficient Lighting Technology Options. Energy II, 286 (2005). Other Supporting Sources: Cost data are from google searches of commercially available appliances | BTO Tool: Average for existing fluorescent fixtures: $78 Appendix B: Page 108: "Typical LED drive electronics operate at efficiencies in the range of 75% to 85%. For comparison, the most efficient ballasts for fluorescent lamps operate at a little better than 90% efficiency, with single digit losses (Lightfair, 2003)." Technical potential is very small, so finding an exact efficiency improvement less than 15% is not a priority. Lifetime is based on recent rulemaking TSD Life Cycle Cost Analysis Chapter. | 1-73 | 5 | 20 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
233 | Audio/video inter-device power control | R: Audio/video inter-device power control | Use intensity | 5 | 2 | Residential | MELs | Audio/video | all | Energy Savings (%) | 10% | 0% | Yes | See incremental cost |  |  | 0.1 | per unit | 1 C/R: No FS: All electric to all electric | Total residential audio/video power control energy use | 7 | 2014 | Personal communication: Nordman, LBNL (12/2010) | Appendix B: 10% savings, very low costs relative to savings, usually several orders of magnitude difference (using benefit/cost ratio of 100) | 1-94 | 7 | 7 | AEO 2014 NEMS
234 | Increase deployment of efficient pool pump motors, pipe design and fittings, and filter selection in residential pools | R: Improved Pool Pump System Design | System | 5 | 5 | Residential | MELs | Pool pump | All | Energy Savings (%) | 63% | 0% | No | See incremental cost |  |  | 79 | per unit | 1 C/R: No FS: All electric to all electric | Total energy use by residential pool pumps | 10 | 2010 | 1) Pacific Gas & Electric, Sempra Energy; "Codes and Standards Enhancement Initiative: Draft Report Residential Swimming Pools", (2007) 2) Roth, K.W., Mckenney, K., Ponoum, R. & Paetsch, C. Residential Miscellaneous Electric Loads: Energy Consumption Characterization and Savings Potential. Tiax (2007) | Appendix B: Table 23 (savings), Table 25 (cost, but designs 2 to 1 only), using 63% savings, $79 extra cost | 1-78 | 10 | 10 | AEO 2014 NEMS
240 | Residential Sector Energy Efficient Ethernet (IEEE 802.3az) | R: EE Ethernet (802.3az) | System | 5 | 5 | Residential | MELs | Ethernet | all | Energy Savings (%) | 12% | 0% | Yes | See incremental cost |  |  | 0.03 | per unit | 1 C/R: No FS: All electric to all electric | Total commercial and residential energy use by energy efficient ethernet | 4 | 2010 | 1) 12% savings updated according to pg. 9-175 of Lanzisera, Nordman, Brown. LBNL. ACEEE Summer Study on Energy Efficiency of Buildings. 2010. http://www.aceee.org/files/proceedings/2010/data/papers/2195.pdf | Appendix B: Very low costs relative to savings, usually several orders of magnitude difference (using benefit/cost ratio of 100) | 1-77 | 4 | 4 | AEO 2014 NEMS
248 | Increase deployment of infrared toaster ovens | R: Infrared toaster | System | 5 | 3 | Residential | MELs | Toaster Oven | All | Energy Savings (%) | 20% | 0% | No | 125 | 88 | 125 | 37 | per unit | 1 C/R: No FS: All electric to all electric | Total energy use by residential toaster ovens | 7 | 2010 | TIAX 2007 | Expected lifetime is assumed - we do not have a good source to support this assumption.BTO Tool: Compares to $88 for non-infrared Kenmore, same capacity | 1-185 | 7 | 7 | AEO 2014 NEMS
250 | Introduce minimum active power standard for new residential TVs | R: Introduce TV Active Power Standard | System | 5 | 5 | Residential | MELs | TVs | All | Energy Savings (%) | 50% | 0% | No | See existing & efficient costs | 170 | 180 | 10 | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by residential TVs | 5 | 2010 | TIAX 2007 Primary Source: Roth, K.W., Mckenney, K., Ponoum, R. & Paetsch, C. Residential Miscellaneous Electric Loads: Energy Consumption Characterization and Savings Potential. Energy 197 (2007). Other Supporting Sources: Cost data are from google searches of commercially available appliances | Appendix B: Page 4-100, last sentence and Table 4-96 | 1-85 | 5 | 5 | AEO 2014 NEMS
252 | Distribution transformers standard effective in 2013, with compliance date of 2016. | C: Distribution Transformers Standard (2016) | Parasitic | 5 | 3 | Commercial | MELs | All distribution transformers | All | Energy Savings (%) | 9.901% | 0% | No | Cost is a weighted average baed on MVA capacity shipped in 2009 from 2013 TSD. No cost data was found for dry type low voltage transformers, hence only the medium voltage cost was considered (market likely includes low and medium dry-type DT in addition to liquid DT). | 38024.5009 | 39061.0703 | 1036.5694 | per MVA | 1 C/R: No FS: All electric to all electric | All types of distribution transformers in all commercial buildings (mmBTUs, site) | 32 | 2016 | TSD 2013 | This measure will be obsolete once the market is updated to AEO 2014. | 3-3441 | 32 | 32 | AEO 2010 NEMS
269 | Residential/commercial televisions that meet Energy Star specifications. % energy savings was obtained from 2011 Energy Star specifications. | R/C: Energy Star TVs | System | 5 | 4 | Residential | MELs | TVs | All | kWh/yr | 130.086 | 197.246 | Yes | Not available; derived based on a 3 year payback. |  |  | 30.3907 | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by residential TVs | 10 | 2011 | 1) Baseline consumption obtained from NCI MEL report. 2013. http://www.eia.gov/analysis/studies/demand/miscelectric/pdf/miscelectric.pdf 2) Improved performance obtained from Energy Star Program Requirements v5.3, effective in 09/30/2011. http://www.energystar.gov/sites/default/files/specs//private/Televisions_Program_Requirements_V5_3.pdf |  | 1-85 | 10 | 10 | AEO 2014 NEMS
272 | PC network presence proxying | C: PC Network Presence | Use intensity | 5 | 2 | Commercial | MELs | PC devices | All | Energy Savings (%) | 30% | 0% | Yes | See incremental cost |  |  | 0 | per unit | 1 C/R: No FS: All electric to all electric | All commercial and residential standby power losses | 7 | 2015 | Personal communication with Nordman (LBNL) on Dec 15, 2010 | Appendix B: 30% savings, very low costs relative to savings, usually several orders of magnitude difference (using benefit/cost ratio of 100) | 1-2739 | 7 | 7 | AEO 2010 NEMS
275 | Deploy restructured laboratory fume hoods with automatic sash closure. This technology has an automatic sash closure system on a VAV hood that is controlled by an occupancy sensor. | C: Auto Sash Fume Hoods | System | 5 | 4 | Commercial | MELS | Fume hoods | All | Energy Savings (%) | 50% | 0% | No |  |  |  | 5100 | per unit | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | Total energy use by fume hoods | 10 | 2013 | 1) Pg. 5&7 of the Advanced Technologies for High Performance Laboratory Fume Hoods Scoping Report. Craig Wray, Paul Mathew. Lawrence Berkeley National Laboratory. November 30, 2012. * Cost calculated from page 5 of the report, where cost of standard CAV unit is $11,000. A standard VAV adds $2000 per hood, and for a 12" valve and controller and $300-$600 for a VAV blower. An automated sash costs an additional $2,500-$2,700 per unit including IR sensors and closure control. Therefore, incremental cost of VAV with auto closure over a standard CAV was estimated to be $2000+$2,600+$500 = $5,100. 2) Federal to commercial scaling of 26.8% based on Federal lab space square footage of 175.5 mil SF, and 654 mil SF of total lab space in the US (Craig Wray, LBNL). To check with CBECs: commercial other building types category SF, which includes labs is 2,043 mil SF. |  | 3-3442 | 10 | 10 | AEO 2010 NEMS
281 | Introduce standby standards for residential electric appliances | R: 1W Standby | Standby | 5 | 5 | Residential | MELs | MELs | All | Standby energy used, TWh/yr | 50 | 150 | No | See incremental cost |  |  | 0 | per unit | 1 C/R: No FS: All electric to all electric | Total residential standby power losses | 5 | 2013 | Choi-Granade, C. e. (2009). Unlocking Energy Efficiency in the U.S. Economy. McKinsey & Company. | Appendix B: Page 49: "A standby standard could reduce standby consumption by roughly two-thirds, yielding 90 - 110 TWh in savings." Judy Reich/NCI: "Examples of residential appliances in the U.S. which may consume less than 1 W in standby include those with electromechanical controls or that shut off the display and become “inactive” after the end of the cycle. Cooking products generally include a clock, which makes it hard to meet a 1-W standard, but it can be done. However, manufacturers aren’t doing it yet because there are no performance standards for conventional cooking products. In general, DOE will not be regulating a specific standby power standard for residential appliances because EISA requires an integrated metric (i.e., active + standby mode energy use) unless it is technically infeasible to combine them. Therefore, the only residential appliance that has a prescriptive standby power standard so far is microwave ovens. These will have a 1-W standby standard that comes into effect in 2016, but at this time very few meet this level. I’m not aware of ENERGY STAR implementing a standby power qualification criterion for any of the residential products I’m familiar with." | 1-87 | 5 | 5 | AEO 2014 NEMS
282 | Introduce standby standards for commercial electric appliances | C: 1W Standby | Standby | 5 | 5 | Commercial | MELs | MELs | All | Standby energy used, TWh/yr | 45 | 135 | No | See incremental cost |  |  | 0.50803 | per unit | 1 C/R: No FS: All electric to all electric | Total standby power energy loss in all commercial buildings | 5 | 2013 | Choi-Granade, C. e. (2009). Unlocking Energy Efficiency in the U.S. Economy. McKinsey & Company. | Cost and energy savings from pg. 49 of the McKinsey Unlocking Energy Efficency in the US Economy Report: "A standby standard could reduce standby consumption by roughly two-thirds, yielding 90 - 110 TWh in savings." & "..\Downloads\US_energy_efficiency_full_report.pdf" | 3-3450 | 5 | 5 | AEO 2010 NEMS
287 | Small motors, beyond standards | C/R: Small motors, max tech | System | 5 | 4 | Residential and Commercial | MELs | Motors | All | Energy Savings (%) | 92% | 62% | No | TSD | 243 | 402 | 159 | per unit | 1 C/R: No FS: All electric to all electric | Total residential, commercial and industrial small motors (not in other analyzed products) | 12 | 2013 | MTAB Report, Appendix A Motors; TSD Primary Source: Department of Energy, Small Electric Motors Final Rule Technical Support Document (2010) Desroches, L.-B. et al. Max Tech and Beyond (2011) | Appendix B: Highest efficiency level in 2010 TSD (and MTAB pg. 44 Fig. 2) represents increasing small motor efficiency from 62% (ave. installed base" to best available (92%) | 1-163 | 12 | 12
288 | Deploy variable speed motors in place of single-speed motors in multiple residential & commercial applications | C/R: Motors in other products | System | 5 | 4 | Residential and Commercial | MELs | Motors | All | Energy Savings (%) | 30% | 0% | No | See incremental cost |  |  | 175 | per unit | 1 C/R: No FS: All electric to all electric | Total energy use by variable speed drive (VSD) motors in A/C, refrigeration, washing machines, and freezers | 12 | 2010 | MTAB Report, Appendix A Motors | BTO Tool: Taken form blowers and refrigerators | 1-157 | 12 | 12
289 | Deploy best practice energy management for data centers | C: Data center energy management | Use Intensity | 4 | 4 | Commercial | MELs | Data Centers | All | Energy Savings (%) | 40% | 0% | No | 20% capital reduction possible; Assume 30% operating cost increase (software, management, etc.). | 100000000 | 80000000 | -14000000 | per data center | 1 C/R: No FS: All electric to all electric | Total energy use by data centers (OYP: it seems this is electricity consumption/IT equipment consumption only, but need to verify the market against a reliable source) | 4 | 2010 | 1) Pg. 9-10, Report to Congress on Server and Data Center Energy Efficiency Public Law 109-431. US EPA. Energy Star Program. August 2, 2007. 2) Costs vary. The cost estimates were generated by Phil. | Appendix B: Combination of virtuatlization, power management, and CADE-related utilization management measures: 70% with a resultant decrease in IT infrastructure and maintenance personnel cost. "As noted above, all of these potential cost increases are expected be much less than the value of lifetime energy savings and avoided site infrastructure costs from more efficient products, often with a very short payback period, so the more efficient systems have a lower total cost of ownership (TCO). In general, however, it is not possible to draw general conclusions about the additional cost of energy-efficient products because there is significant variation among product types, the efficiency strategies applied vary among products, and the rapid pace of change in technology makes it difficult to collect cost data." pg. 69, EPA Report to Congress on Server and Data Center Energy Efficiency 2007. | 3-3445 | 4 | 4 | AEO 2010 NEMS
291 | Adjusts time between defrost cycles based on need (time of last cycle, humidity sensor, number of door openings) in residential refrigerators | R: Refrig. Adaptive Defrost | Parasitic | 5 | 4 | Residential | Refrigeration | Rfrg/Frz | Retrofits, New | Energy Savings (%) | 3.5% | 0% | Yes | $8 (including control cost) |  |  | 8 | per unit | 1 C/R: No FS: All electric to all electric | All residential refrigerators and freezers | 17 | 2010 | DOE TSD, http://www.aps.com/main/services/business/WaysToSave/BusWaysToSave_59.html, web search for comparing products, article (http://www.rdmag.com/New-To-Market/2010/06/Manufacturing-Thermal-Green-refrigerator-controller-helps-conserve-wasted-energy/ Primary Source: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation | BTO Tool: Updated based solely on TSD 12/11 Appendix B: "energy consumption can be reduced by three to four percent with adaptive defrost" "DOE used an incremental cost of $8 in the energy analysis for adaptive defrost ($0 if electronics onboard)" used $8 contoller cost, average of 3-4% savings range provided | 1-92 | 17 | 17 | AEO 2014 NEMS
292 | Improve supermarket compressor rack in new systems by using compressor modulation | C: Supermarket Compressor Racks Modulation | Compressor | 5 | 3 | Commercial | Refrigeration | Compressor Racks | Supermarket | Energy Savings (%) | 5% | 0% | No | 19008 |  |  | 19008 | per unit | 1 C/R: No FS: All electric to all electric | All supermarket compressor racks | 15 | 2010 | Table 5-9, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | BTO Tool: Baseline compressor rack = 5 compressors sharing 350,000 BTU/hr load at medium temp | 3-3501 | 15 | 15 | AEO 2010 NEMS
293 | Encourage supermarket owners to add doors to display cases | C: Display Cases + Doors | Heat loss (non-envelope) | 5 | 4 | Commercial | Refrigeration | Display Cases | New, Retrofits | Energy Savings (%) | 30% | 0% | Yes | 1-2 year payback for retrofits. Incremental cost to retrofit estimated at $400/LF, including installation costs |  |  | 400 | per LF | 1 C/R: No FS: All electric to all electric | All energy use by supermarkets' medium temperature refrigerated display cases without doors | 10 | 2010 | http://supermarketnews.com/technology/new_tests_support_1004/; http://www.aps.com/main/services/business/WaysToSave/BusWaysToSave_59.html; http://arstechnica.com/science/news/2011/10/redesign-improves-energy-efficiency-of-supermarket-cold-food-cases.ars ATE 31: 3055 Primary Source: Garry, M; "New Tests Support Doors on Cases", Supermarket News 10/4/2010 Garry, M; "Fresh & Easy Installs Case Doors in 35 Stores" Supermarket News 9/20/2011; NCI Internal Report & Market Study | BTO Tool: Note: changing jets, etc. gets you 25% accordin to multiple papers from AME Appendix B: Multiple examples cited incicating (+/-) small change in sales, ~30% energy savings, ~3-5 year paybacks quoted Using 30% savings and ~ 4 year payback and no statistically significant proof of sales impact | 3-3544 | 10 | 10 | AEO 2010 NEMS
294 | Use efficient DC condenser fans (ECM motors) in new commercial refrigeration equipment. This will be ubiquitous - the DOE standard compliance date is 2017, published in March 2014. | C: Refrig. Efficient Condenser Fans, Standard, 2017 | Condenser | 5 | 4 | Commercial | Refrigeration | Walk-Ins, Food Prep Table, Reach-Ins, Bev Merchandiser, Ice Machine | Supermarket | Energy Savings (%) | 8% | 0% | No | $23-66 |  |  | 44.5 | per unit | 1 C/R: No FS: All electric to all electric | All commercial high efficiency compressor and condenser fans | 10 | 2010 | Table 5-13,14,17,19,20,22,24,26,27, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | No notes | 3-3509 | 10 | 10 | AEO 2010 NEMS
295 | Improve expansion valves and control technology in new commercial walk-in refrigerators | C: Controls and expansion valves in walk in refrig | Compressor | 5 | 4 | Commercial | Refrigeration | Walk-In Cooler | Supermarket | Energy Savings (%) | 16% | 0% | No | $348; payback 0.3-0.7 yrs |  |  | 348 | per unit | 1 C/R: No FS: All electric to all electric | Walk-In Coolers, Supermarkets | 11 | 2010 | Table 5-13, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | BTO Tool: Floating head pressure takes advantage of lower lift temps available at lower ambient temps | 3-3503 | 11 | 11 | AEO 2010 NEMS
296 | Deploy display cases with advanced air curtains for containing cold air | C: Advanced Display case air curtains | Heat loss (non-envelope) | 5 | 1 | Commercial | Refrigeration | Display Cases | Supermarket | Energy Savings (%) | 7.5% | 0% | Yes | 1-2 year payback for retrofits |  |  | 150 | per unit | 1 C/R: No FS: All electric to all electric | Display Cases, Supermarkets | 10 | 2016 | Table 6-1, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment |  | 3-3504 | 10 | 10 | AEO 2010 NEMS
298 | Add fan to freezer compressors in new residential upright freezers | R: Add fans to upright freezer | Condenser | 5 | 3 | Residential | Refrigeration | Upright Freezer | New | Energy Savings (%) | 8% | 0% | Yes | 1.449 | 0 | 1.449 | 1.449 | per unit | 1 C/R: No FS: All electric to all electric | Total energy use by all residential upright freezers | 17 | 2013 | p. 5-53 and Table 5-A.3.7, DOE TSD Primary Source: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation | BTO Tool: Updated based solely on TSD 12/11 Appendix B: All data taken from TSD and supporting engineering and national impact estimates | 1-45 | 17 | 17 | AEO 2014 NEMS
301 | Standardize Max Tech option for commercial ice machines | C: Max Tech Ice Machine | System | 5 | 2 | Commercial | Refrigeration | Ice Machine | Food Service Establishments | Energy Savings (%) | 23% | 0% | No | 334 |  |  | 334 | per unit | 1 C/R: No FS: All electric to all electric | All commercial ice machines | 8.5 | 2015 | Table 5-24, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment Primary Source: DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment (http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_refrig_report_10-09.pdf) Other Supporting Sources: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation | BTO Tool: Includes: thicker insulation, brushless DC condenser fan, high eff compressor, reduced meltage, reduced evap thermal cycling, and high eff fan blades Appendix B: Table 5-24, line 8, page 152 | 3-3520 | 8.5 | 8.5 | AEO 2010 NEMS
303 | Install intelligent defrost controls in commercial reach-in and walk-in freezers. | C: Defrost Controls in Freezers | Parasitic | 3 | 3 | Commercial | Refrigeration | Walk-In Freezer, Reach-In Frz | Supermarket, Restaurants | Energy Savings (%) | 3% | 0% | Yes | $63-138 |  |  | 103 | per unit | 1 C/R: No FS: All electric to all electric | All commercial freezers | 12 | 2013 | Table 5-14,19, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment |  | 3-3506 | 12 | 12 | AEO 2010 NEMS
306 | National campaign to retire older refrigerators at 14 years instead of 18 years | R: Accel. Retire pre-2010 fridges | Use Intensity | 5 | 4 | Residential | Refrigeration | Rfrg/Frz | Retirements | kWh/yr reduction per unit | 435 | 1165 | Yes | 81 |  |  | 81 | per unit | 1 C/R: No FS: All electric to all electric | All residential refrigerators eligible for early retirement | 17 | 2010 | TSD, ENERGY STAR market data, http://www.energystar.gov/ia/partners/manuf_res/downloads/Refrigerator_Market_Profile_2009.pdf Primary Source: Department of Energy, "New Opportunities Multiply Savings:Refrigerator Market Report, 2009", 2009 Other Supporting Sources: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation | Appendix B: 730 kWh of savings off a base of 1165 kWh (i.e., 63%) $134 of economic costs of early retirement | 1-79 | 17 | 17 | AEO 2014 NEMS
308 | Reduction or elimination of heaters due to gas-filled glass doors in commercial walk-in refrigeration systems | C: Anti-Sweat Heater Controls | Parasitic | 3 | 4 | Commercial | Refrigeration | Walk-In Cooler, Walk-In Frz |  | Energy Savings (%) | 4% | 0% | Yes | 627 |  |  | 627 | per unit | 1 C/R: No FS: All electric to all electric | All walk-in coolers and freezers | 15 | 2010 | Table 5-13,14, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment |  | 3-3508 | 15 | 15 | AEO 2010 NEMS
310 | Use high efficiency compressors in new commercial refrigeration equipment (variable-speed, etc.) | C: High Efficiency Refrig. Compressor | Compressor | 5 | 3 | Commercial | Refrigeration | Walk-Ins, Food Prep Table, Reach-Ins, Bev Merchandiser, Ice Machine | Supermarket, Restaurants | Energy Savings (%) | 10% | 0% | No | $22-$662 |  |  | 342 | per unit | 1 C/R: No FS: All electric to all electric | All commercial high efficiency compressor and condenser fans | 10 | 2013 | Table 5-13,14,17,19,20,22,24, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment |  | 3-3509 | 10 | 10 | AEO 2010 NEMS
313 | Use high efficiency condensers in new supermarket refrigeration equipment | C: High Efficiency Rack System Condenser in Supermarket Refrigeration | Condenser | 5 | 4 | Commercial | Refrigeration | Supermarket Condensers | Supermarket | Energy Savings (%) | 28% | 0% | No | $5000; payback 0.9-2.1 yrs |  |  | 5000 | per unit | 1 C/R: No FS: All electric to all electric | All supermarket condensers | 10 | 2010 | Table 5-10, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | No notes | 3-3511 | 10 | 10 | AEO 2010 NEMS
314 | Encourage use of best practices in design of commercial refrigeration systems | C: Refrig. best practice and designs | System | 2+ | 2 | Commercial | Refrigeration | Rfrg/Frz | All | Energy Savings (%) | 15% | 0% | Yes | 0 |  |  | 0 | per unit | 1 C/R: No FS: All electric to all electric | All supermarket refrigeration systems (cond, comp, walk-ins, & display) | 12 | 2015 | Table 6-1, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | BTO Tool: Est. Time to Commercialization: <5 yrs | 3-3507 | 12 | 12 | AEO 2010 NEMS
316 | Use high efficiency fan blades in new commercial refrigeration equipment | C: High Efficiency Fan Blades in refrig. | Evaporator | 5 | 4 | Commercial | Refrigeration | Food Prep Table, Reach-In Rfgr/Frz, Walk-Ins, Bev Machines, Ice Machines | Supermarket, Restaurants | Energy Savings (%) | 5.5% | 0% | Yes | $2-80 |  |  | 41 | per unit | 1 C/R: No FS: All electric to all electric | All commercial high efficiency compressor and condenser fans | 10 | 2010 | Table 5-13,14,17,19,20,22,24 DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | No notes | 3-3509 | 10 | 10 | AEO 2010 NEMS
317 | Use brushless DC motors in new compressors for commercial refrigeration equipment | C: Brushless DC Compressor Motor | Compressor | 5 | 3 | Commercial | Refrigeration | Food Prep Table, Reach-In Rfgr/Frz, Bev Machines, Vending Machines | Various | Energy Savings (%) | 9% | 0% | No | 63 |  |  | 63 | per unit | 1 C/R: No FS: All electric to all electric | All commercial compressors (DC) | 15 | 2013 | Table 5-17,19,20,22,26,27, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment Primary Source: DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment (http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_refrig_report_10-09.pdf) Other Supporting Sources: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation | Appendix B: Average of energy savings and installed cost premium of high efficiency compressors from tables 5-17, 5-19, 5-20, 5-22, 5-26, 5-27 | 3-3512 | 15 | 15 | AEO 2010 NEMS
318 | Use enhanced evaporator coils in new supermarket display cases | C: Display Cases Enhanced Evaporator Coil | Evaporator | 5 | 4 | Commercial | Refrigeration | Open Display Cases (Medium-Temp), Glass Door Display Cases | Supermarket | Energy Savings (%) | 3% | 0% | No | $94-$355 |  |  | 224.5 | per unit | 1 C/R: No FS: All electric to all electric | Display Cases, Supermarkets | 10 | 2010 | Table 5-6,7,8, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | BTO Tool: Increased Fin Pitch and Surface Area | 3-3504 | 10 | 10 | AEO 2010 NEMS
319 | More efficient anti-sweat heating, vinyl/composite frame, and high-performance glass in display cases | C: Refrig. Display case glass doors | Heat loss (non-envelope) | 5 | 4 | Commercial | Refrigeration | Glass Door Display Cases | Supermarket | Energy Savings (%) | 40% | 0% | No | 1435-1825 |  |  | 1630 | per unit | 1 C/R: No FS: All electric to all electric | Display Cases, Supermarkets | 10 | 2010 | Table 5-7,8, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | BTO Tool: higher # for low temp | 3-3504 | 10 | 10 | AEO 2010 NEMS
320 | Deploy brushless DC evaporator and condenser fan motors in new residential refrigerator-freezers | R: Brushless fan motors in all refrig. | Parasitic | 5 | 4 | Residential | Refrigeration | Rfrg/Frz | New | Energy Savings (%) | 7.56% | 0% | Yes | 1.449 | 0 | 1.449 | 1.449 | per unit | 1 C/R: No FS: All electric to all electric | All residential refrigerators and freezers | 17 | 2010 | Table 2.2.1 and p. 5-51, DOE TSD; Byrne motor article suggests condenser fans and evaporator fans represent ~6% of national motor consumption each, compared to compressors | BTO Tool: Evap and condenser are ~12% of rfrg energy usage, see addl measures tab; so 12% of 63% is savings potential; Primary Manufacturer: Matsushita | 1-92 | 17 | 17 | AEO 2014 NEMS
323 | Use advanced controllers in new refrigeration system installs | C: Advanced refrigeration controllers | Controls | 5 | 4 | Commercial | Refrigeration | Refrigeration controls | Supermarket | Energy Savings (%) | 20% | 0% | No | $90,000; payback 1.7-3.8 yrs |  |  | 90000 | per unit | 1 C/R: No FS: All electric to all electric | All supermarket display cases, compressors, and condensers | 10 | 2010 | Table 5-11, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | BTO Tool: Baseline supermarket = energy usage of 2.037 million kWh/yr, with 60 display cases, compressor racks and four condensers | 3-3513 | 10 | 10 | AEO 2010 NEMS
326 | Use brushless DC motors in evaporators for all commercial refrigeration equipment. ECM evaporator fan motors will be almost ubiquitous starting in 2017 (compliance date) based on DOE standards published in March 2014. | C: Refrig. Evap. B-less DC Motors Standard 2017 | Evaporator | 5 | 5 | Commercial | Refrigeration | Rfrg/Frz | Various | Energy Savings (%) | 17% | 0% | No | $23-171 |  |  | 98 | per unit | 1 C/R: No FS: All electric to all electric | All commercial refrigeration equipment, except compressor racks and supermarket condensers | 12 | 2010 | Table 5-6,7,8,13,14,17,19,20,22,26,27, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment Primary Source: Navigant Consulting Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Final Report. Department of Energy (2009) | BTO Tool: ECM fan motor = brushless DC Appendix B: Tables 5-8,13,14,17,19,20,22,26,27 Averaged cost and savings over equipment in indicated tables | 3-3515 | 12 | 12 | AEO 2010 NEMS
327 | Use hot gas devices for anti-sweat applications in new display cases, etc. | C: Hot Gas Anti-Sweat | Parasitic | 5 | 3 | Commercial | Refrigeration | Walk-In Freezer, Reach-Ins, Food Prep Table | Supermarket, Restaurants | Energy Savings (%) | 14% | 0% | No | $80-414 |  |  | 127 | per unit | 1 C/R: No FS: All electric to all electric | All energy use by walk-In freezers, reach-ins, and food preparation table | 13 | 2011 | Table 5-14,17,19,20, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | No notes | 3-3517 | 13 | 13 | AEO 2010 NEMS
329 | Use hot gas devices for defrost applications in new display cases, etc. | C: Hot Gas Defrost | Parasitic | 5 | 3 | Commercial | Refrigeration | Walk-In Freezer, Reach-In Frz | Supermarket | Energy Savings (%) | 6% | 0% | No | 104-165 |  |  | 119.5 | per unit | 1 C/R: No FS: All electric to all electric | All commercial freezers | 12.5 | 2011 | Table 5-14,19, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | No notes | 3-3506 | 12.5 | 12.5 | AEO 2010 NEMS
330 | Place condenser external to unit in new equip | C: Refrigeration: external heat rejection | Condenser | 5 | 3 | Commercial | Refrigeration | Walk-In Freezer | Supermarket | Energy Savings (%) | 10% | 0% | No | $1003; payback 4.4-10.1 yrs |  |  | 1003 | per unit | 1 C/R: No FS: All electric to all electric | All walk-in freezers | 11 | 2010 | Table 5-14, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | BTO Tool: Increased installation costs (included) | 3-3514 | 11 | 11 | AEO 2010 NEMS
331 | Encourage use of refrigerators without ice makers | R: Remove icemakers from refrig. | Parasitic | 5 | 3 | Residential | Refrigeration | Rfrg/Frz | Units w/ ice makers | kWh/yr/refrigerator - W-hr/cycle; max 9 cycles per day | 512.56 | 596 | Yes | See incremental cost |  |  | -110 | per unit | 1 C/R: No FS: All electric to all electric | All residential primary refrigerators with icemakers | 17 | 2010 | also Meier (1997), Energy and Buildings; Meier A. Energy Use of Ice Making in Domestic Refrigerators. Lawrence Berkeley National Laboratory Report No. LBL-31976, 1995. Primary Source: Meier, A. Martinex, M; "Energy Use of Icemaking in Domestic Refrigerators", LBNL-39183 (1996) | BTO Tool: Use 7-26% more power than units with no ice maker; Comparison b/t 2 LG top-mount models; **energy use reported same!** Appendix B: "The refrigerators' gross electricity use increased about IO%, or 100 kWh/yr, due to operation of the automatic icemaker...The net energy difference, i.e., after subtracting the energy needed to make ice manually, is roughly 55 kWh/yr" 55 kWh/year corresponds to ~ 9.5% of today's typical refrigerator of 585 kWh/year; current Kenmore icemaker kit priced at $110 (6/12) | 1-80 | 17 | 17 | AEO 2014 NEMS
333 | Deploy most efficient ice makers in commercial applications | C: Max Tech Ice Makers | Parasitic | 5 | 2 | Commercial | Refrigeration | Rfrg/Frz | Hospitals, Restaurants, Hotels | Energy Savings (%) | 15% | 0% | No | 2 year payback |  |  | 140 | per unit; 706 lbs/day | 1 C/R: No FS: All electric to all electric | All commercial ice machines | 8.5 | 2014 | http://www.cee1.org/resrc/facts/com-ice-fx.pdf; http://www.energystar.gov/index.cfm?fuseaction=find_a_product.showProductGroup&pgw_code=CIM Primary Source: Consortium for Energy Efficiency (2007), "Commercial Ice Makers" (http://www.cee1.org/resrc/facts/com-ice-fx.pdf) Other Supporting Sources: ENERGY STAR, "Commercial Ice Machines", http://www.energystar.gov/index.cfm?fuseaction=find_a_product.showProductGroup&pgw_code=CIM | BTO Tool: ENERGY STAR can save 1200 kWh per year over other units, or about $110/yr on electricity Appendix B: "The average annual energy use of a 500 lb./day air-cooled ice-maker is 5,000 kWh with a potential increase in efficiency of 15 percent (less than a two-year payback)." | 3-3520 | 8.5 | 8.5 | AEO 2010 NEMS
334 | Improve compressor efficiency in new residential refrigerators & freezers | R: Compressor Improvements | Compressor | 5 | 3 | Residential | Refrigeration | Rfrg/Frz | New | Energy Savings (%) | 14% | 0% | No | 14.02 |  | 14.02 | 14.02 | per unit | 1 C/R: No FS: All electric to all electric | All residential refrigerators and freezers | 17 | 2013 | See calculation in additional market data tab; Tables 5-A.3.2 (and .4, .6) (and also p.5-46), DOE (2009): Preliminary TSD, EE Program for Consumer Products, Refrigerators, Refrigerator-Freezers, and Freezers Primary Source: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation | BTO Tool: Represents TSD estimate of moving from EER ~5.2-5.5 to ~6.1-6.5 Appendix B: Tables 5-A.3.2 (and .4, .6) (and also p.5-46) Averaged maximum compressor improvements over all refrgerator types | 1-92 | 17 | 17 | AEO 2014 NEMS
338 | Refrigerator rulemaking: Residential refrigerator standards were amended/effective in 09/2011 with compliance date in 09/2014. | R: All Refrig. Standard, 2014 | System | 5 | 5 | Residential | Refrigeration | Rfrg/Frz | All | Energy Savings (%) | 24.5% | 0% | No | 1.449 | 0 | 1.449 | 1.449 | per unit | 1 C/R: No FS: All electric to all electric | All residential refrigerators and freezers | 17 | 2014 | TSD Primary Source: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation | This measure will be obsolete once the market is updated based on AEO 2014 projections. BTO Tool: Uses product clases 1-7 as proxy for all Appendix B: All data taken from TSD and supporting engineering and national impact estimates | 1-92 | 17 | 17 | AEO 2014 NEMS
339 | Deploy and standardize Max Tech refrigerator | R: Max tech refrigerator | System | 5 | 2 | Residential | Refrigeration | Rfrg/Frz | New | Energy Savings (%) | 35% | 0% | No | See incremental cost |  |  | 290.41 | per unit | 1 C/R: No FS: All electric to all electric | All residential refrigerators' energy consumption | 17 | 2014 | Combined 4 other sources "in parallel" Primary Source: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation | BTO Tool: Combine 320, 338, 340, 378, and 383 Appendix B: All measure tables drawn from engineering and national impact analysis from TSD and supporting material | 1-81 | 17 | 17 | AEO 2014 NEMS
340 | Use of high efficiency evaporator fans in new residential refrigerators | R: Improved Evaporator Fan Efficiency in refrig | Evaporator | 5 | 3 | Residential | Refrigeration | Rfrg/Frz | New | Energy Savings (%) | 7% | 0% | Yes | 4-year payback |  |  | 17.9076 | per unit | 1 C/R: No FS: All electric to all electric | All residential refrigerators and freezers | 17 | 2012 | http://www.homeenergy.org/article_preview.php?id=21&article_title=Motors_Matter | BTO Tool: See Additional Market Data tab for efficiency and cost calculations | 1-92 | 17 | 17 | AEO 2014 NEMS
341 | Improve insulation in new reach-in, etc. commercial refrigeration equipment | C: Improved Insulation in refrig | Heat loss (non-envelope) | 5 | 4 | Commercial | Refrigeration | Reach-Ins, Beverage Merchandiser, Open Display Cases, Glass Door Display Cases | Supermarket, Restaurants | Energy Savings (%) | 3% | 0% | Yes | $76-$1429 |  |  | 331 | per unit | 1 C/R: No FS: All electric to all electric | All reach-ins, beverage merchandisers, and display cases | 13 | 2013 | Table 5-19,20,22,6,7,8, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | No notes | 3-3519 | 13 | 13 | AEO 2010 NEMS
342 | Increased insulation thickness for residential freezers and compact refrigerators | R: Increased freezer insulation | Heat loss (non-envelope) | 5 | 4 | Residential | Refrigeration | Rfrg/Frz | New | Energy Savings (%) | 1.5% | 0% | Yes | See incremental cost |  |  | 28.44 | per unit; 25 ft^3 | 1 C/R: No FS: All electric to all electric | Total energy use by residential freezers and compact refrigerators | 17 | 2013 | DOE (2009) TSD; see calculation on Addl Markets Tab Primary Source: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation | BTO Tool: See Addl Market tab for cost calc; before, Used 5% of $1000 as estimate; assumed same reduction as commercial Appendix B: Table 5-A.3.10, 11, 13, 14 Averged data to get 10% savings improvement, $37 cost | 1-91 | 17 | 17 | AEO 2014 NEMS
344 | Replace lighting with LEDs in remote-condensing commercial refrigeration equipment | C: Refrig. Retrofit Lights to LEDs | Parasitic | 5 | 4 | Commercial | Refrigeration | Display Cases, Vending Machines, Beverage Merchandisers, and Walk-In Coolers | Retrofit | Energy Savings (%) | 7% | 0% | No | 975 |  |  | 975 | per unit | 1 C/R: No FS: All electric to all electric | All commercial medium temperature and remote condensing display cases where lights can be retrofitted | 10 | 2007 | 1) TSD for commercial refrigeration, Engineering Analysis Chapter 3. See Additional Data Tab for savings/cost calculation; Only Remote Condensing units can be retrofitted, and there are different potential energy savings with a LED retrofit. For an open display case, the potential energy savings are 6%, and for a display case with doors, the energy savings are 18%. Using Table 10.2.4 from the commercial refrigeration TSD, calculated a weighted average for potential energy savings of commercial refrigerators capable of an LED retrofit. 2) Example: Geolights: http://geolights.com/products_detail.php?id=117 3) Costs obtained from calculations derived by Phil. 4) http://www.lrc.rpi.edu/programs/solidstate/pdf/freezerlighting-finalreport.pdf | Only Remote Condensing units can be retrofitted, and there are different potential energy savings with a LED retrofit. For an open display case, the potential energy savings are 6%, and for a display case with doors, the energy savings are 18%. Using Table 10.2.4 from the commercial refrigeration TSD, calculated a weighted average for potential energy savings of commercial refrigerators capable of an LED retrofit. See details in supporting spreadsheet for measure #344. | 3-3500 | 10 | 10 | AEO 2010 NEMS
345 | Replace lighting with LEDs in residential refrigerators | R: Refrigerator LED lighting | Parasitic | 5 | 4 | Residential | Refrigeration | Rfrg/Frz | All | Energy Savings (%) | 0.9% | 0% | Yes | 7.99 |  |  | 7.99 | per unit; 25 Lumens | 1 C/R: No FS: All electric to all electric | All residential standard size refrigerators | 17 | 2007 | LEDLight.com, "Standard Appliance LED Light Bulb ", http://www.ledlight.com/standard-appliance-led-light.aspx | BTO Tool: Assume lighting is 0.6% of refrigerator energy use (60W, 10min/day); Incremental cost (from press release) and energy savings (from ENERGY STAR search )are unclear, as LEDs are bundled with other "extra" features Appendix B: "Plastic assembly so it is more durable than a regular light bulb and it only consumes 1/10 the power so it is more energy efficient" and current price is listed at $7.99 each 90% reduction applied to refrigerator lighting load: ~1% | 1-82 | 17 | 17 | AEO 2014 NEMS
347 | Use of no or low heating elements to eliminate sweating on doors | C: Low-heat door anti-sweating | Parasitic | 5 | 3 | Commercial | Refrigeration | Walk-Ins | Supermarket | Energy Savings (%) | 13.5% | 0% | Yes | 876 |  |  | 876 | per unit | 1 C/R: No FS: All electric to all electric | All walk-in coolers and freezers | 15 | 2013 | Table 5-13,14, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | BTO Tool: higher # for Frz | 3-3508 | 15 | 15 | AEO 2010 NEMS
348 | Demonstrate and deploy magnetic refrigeration in homes | R: Magnetocaloric refrigeration | System | 5 | 1 | Residential | Refrigeration | Rfrg/Frz | New | Energy Savings (%) | 25% | 0% | No |  |  |  | 2293.6957 | per unit | 1 C/R: No FS: All electric to all electric | All residential refrigerators and freezers | 17 | 2019 | based on Torregrosa-Jaime, B., Payá, J., Corberan, J., Malvicino, C., Di Sciullo, F., ICE Project: Mobile Air-Conditioning System Based on Magnetic Refrigeration, Technical Paper 2013-01-0238, 2013, doi:10.4271/2013-01-0238 and Torregrosa-Jaime, B., Vasile, C., Risser, M., Muller, C., Corberan, J., Payá, J., Application of Magnetocaloric Heat Pumps in Mobile Air-Conditioning, Technical Paper 2013-01-0239, 2013, doi:10.4271/2013-01-0239; --> cost based on presentation during the conference is 500 euros ~ $653 for a 2.3 kW system ==> assume a typical home requires 3 TR ==> cost premium = 3*3.517/2.3*500 | BTO Tool: DQ 0: Dropped given feedback from ORNL: research reseearch is indicating this isn't very promissing | 1-92 | 17 | 17 | AEO 2014 NEMS
355 | Use non-electric devices for anti-sweat applications in walk-in coolers, etc. | C: Non-Electric door anti-sweat | Parasitic | 5 | 2 | Commercial | Refrigeration | Walk-In Cooler |  | Energy Savings (%) | 6% | 0% | Yes | $1244; payback 2.9-6.7 yrs |  |  | 1244 | per unit | 1 C/R: No FS: All electric to all electric | Walk-In Coolers, Supermarkets | 15 | 2015 | Table 5-13, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | No notes | 3-3503 | 15 | 15 | AEO 2010 NEMS
356 | Demonstrate and deploy linear oil-free compressor applicable to all residential refrigerators and freezers | R: Oil-Free Linear Compressor in Refrig and Freezers | Compressor | 5 | 3 | Residential | Refrigeration | Rfrg/Frz | New | Energy Savings (%) | 25% | 0% | Yes | $20 million over 5 years |  |  | 50 | per unit; net of space savings value | 1 C/R: No FS: All electric to all electric | All residential refrigerators and freezers | 17 | 2016 | 1) TSD, LG product website (11/12), http://www.acr-news.com/news/news.asp?id=2231, 2) http://www.applianceassistant.com/news/AM091610.html 3) Primary Source: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, 4) Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation 5) http://docs.lib.purdue.edu/cgi/viewcontent.cgi?article=2363&context=icec 6) http://docs.lib.purdue.edu/cgi/viewcontent.cgi?article=1786&context=icec | Price delta is <=$250; value of marginal space added is ~$100-$300, using $50 as the price. EER 7.5 from table 3.3.10; cost estimated form web search for existing products with value added for internal refrigerator space. NCI: Several entities have simulated and designed oil free linear compressors, but no one has presented one to the market yet. Embraco claims to be working on this very goal, and they claim that introduction of such a product is a few years away. However, I'd guess this technology is a bit further away than that. | 1-92 | 17 | 17 | AEO 2014 NEMS
358 | Reduce thermal cycling of evaporator in new commercial ice machines | C: Ice Mach, Reduce Evaporator Thermal Cycling | Evaporator | 5 | 3 | Commercial | Refrigeration | Ice Machine | Food Service Establishments | Energy Savings (%) | 5% | 0% | No | $25; payback 0.7-1.5 yrs |  |  | 25 | per unit | 1 C/R: No FS: All electric to all electric | All commercial ice machines | 8.5 | 2010 | Table 5-24, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment (http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_refrig_report_10-09.pdf) Other Supporting Sources: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation | BTO Tool: Baseline: Self-Contained, Air-Cooled, 5248 kWh/yr Appendix B: Table 5-24, page 152, line 6, "Reduced Evaporator Thermal Cycling | 3-3520 | 8.5 | 8.5 | AEO 2010 NEMS
359 | Reduce ice meltage during harvest in commercial ice machines | C: Reduced Meltage During Harvest in ice machine | Use Intensity | 5 | 3 | Commercial | Refrigeration | Ice Machine | Food Service Establishments | Energy Savings (%) | 4% | 0% | Yes | $110; payback 3.2-7.3 yrs |  |  | 110 | per unit | 1 C/R: No FS: All electric to all electric | All commercial ice machines | 8.5 | 2010 | Table 5-24, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment (http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_refrig_report_10-09.pdf) Other Supporting Sources: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation | BTO Tool: Baseline: Self-Contained, Air-Cooled, 5248 kWh/yr Appendix B: Table 5-24, page 152, line 5, "Reduced Meltage During Harvest" | 3-3520 | 8.5 | 8.5 | AEO 2010 NEMS
363 | Use proximity sensors in new beverage merchandisers | C: Beverage Merchandisers Lighting Proximity Sensors | Controls | 5 | 4 | Commercial | Refrigeration | Beverage Merchandiser |  | Energy Savings (%) | 35% | 0% | No | $100; payback 0.7-1.6 |  |  | 100 | per unit | 1 C/R: No FS: All electric to all electric | All commercial beverage merchandisers | 15 | 2010 | Table 5-22, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | BTO Tool: Baseline: One Door, 2527 kWh/yr | 3-3521 | 15 | 15 | AEO 2010 NEMS
369 | Demonstrate thermoacoustic method for residential refrigerators | R: Thermoacoustic Refrigeration | System | 5 | 1 | Residential | Refrigeration | Rfrg/Frz | Portable Applications | Energy Savings (%) | 15% | 0% | No | See existing & efficient costs | 2199 | 3748.75 | 1549.75 | per unit | 1 C/R: No FS: All electric to all electric | All residential refrigerators and freezers | 17 | 2019 | Table 6-1, Navigant Consulting Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Final Report. Department of Energy (2009) | BTO Tool: Est. Time to Commercialization: >10 yrs Appendix B: performance average of table 6-1, cost | 1-92 | 17 | 17 | AEO 2014 NEMS
377 | Use most cost effective insulation thickness in commercial walk-ins | C: Walk-in wall insulation | Heat loss (non-envelope) | 5 | 4 | Commercial | Refrigeration | Walk-Ins | Supermarket | Energy Savings (%) | 2% | 0% | Yes | $322-592 |  |  | 457 | per unit | 1 C/R: No FS: All electric to all electric | All walk-in coolers and freezers | 15 | 2013 | Table 5-13,14, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | BTO Tool: higher for frz | 3-3508 | 15 | 15 | AEO 2010 NEMS
378 | Use vacuum insulated panels for all residential refrigeration | R: VIP in refrigerators | Heat loss (non-envelope) | 5 | 3 | Residential | Refrigeration | Rfrg/Frz | New | Energy Savings (%) | 19% | 0% | Yes | 1.449 | 0 | 1.449 | 1.449 | per unit; 22 ft^3 | 1 C/R: No FS: All electric to all electric | All residential refrigerators and freezers | 17 | 2013 | TSD; http://www.appliancemagazine.com/new_products.php?article=4971&zone=204&first=1 LG Korea: http://www.lg.com/global/sustainability/environment/greener-products/products-application/refrigerator.jsp | BTO Tool: For cost, assumed outer dimensions, 2.6x2.7x5.6 ft; LG model: Total monthly power consumption 32.9Kwh/month (27% efficiency improvement in comparison with competitor model SRM716YIWL) | 1-92 | 17 | 17 | AEO 2014 NEMS
380 | Improve supermarket compressor rack in new systems by using vapor injection economizer for low temperature supermarket compressors | C: Vapor Injection Economizer for Low Temp Supermarket Compressors | Compressor | 5 | 3 | Commercial | Refrigeration | Compressor Racks | Supermarket | Energy Savings (%) | 4% | 0% | No | 19008 |  |  | 19008 | per unit | 1 C/R: No FS: All electric to all electric | All supermarket compressor racks | 15 | 2010 | Table 5-9, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | BTO Tool: Baseline compressor rack = 5 compressors sharing 350,000 BTU/hr load at medium temp | 3-3501 | 15 | 15 | AEO 2010 NEMS
381 | Deploy advanced white roofs to commercial buildings in the hottest climate zones (4&5) with SR 0.75 | C: Cool Roofs, Hot CZ, 0.75 SR | Roof | 5 | 4 | Commercial | HVAC | Roof/ attic insulation | All A/C | Energy Savings (%) | 24.02% | 0% | Yes | Cost premium of $0.31/SF of roof area |  | 0.10333 | 0.10333 | per square foot; 3 floors/building average | 10 C: No FS: All fuels cooling (elec+NG) | All commercial cooling in the hottest 2 climates | 40 | 2013 | 1) Savings from pg. 2 Sleiman, Mohamad. Kirchstetter, Thomas.Gilbert, Haley. Preble, Chelsea. Accelerated aging method to mimic changes in solar reflectance of roofing materials. LBNL. July 18, 2012. 2) Cost in source is .31/sqft of roof area. Use average of 3 floors per building to get cost/ total floor space (from CBECS). Non-residential Cool Roof Cost Summary. Architectural Energy Corporation. February 8, 2012. Table 1. http://www.coolrooftoolkit.org/wp-content/uploads/2012/07/CEC-Non-Res-Cool-3) 3) Duro Last. Energy Efficient Roofing, Inc. http://www.fseer.com/DuroLastFacts.aspx 4) Data reviewed and submitted by experts from Fraunhofer Center for Sustainable Energy Systems during peer review. | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 3-3611 | 40 | 40 | AEO 2010 NEMS
382 | Use variable speed compressors in select new commercial refrigeration equipment | C: VSCs for Refrigeration | Compressor | 5 | 4 | Commercial | Refrigeration | Compressors | Various | Energy Savings (%) | 20% | 0% | No | $138-$201 |  |  | 86 | per unit | 1 C/R: No FS: All electric to all electric | All commercial compressors (DC) | 15 | 2010 | Tables 5-17,19,20,22,26,27, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment Primary Source: Department of Energy, "Energy Conservation Program: Energy Conservation Standards for Residential Refrigerators, Refrigerator-Freezers, and Freezers" Federal Register (9/2010) and supporting documentation | BTO Tool: Max Tech report: 5% Appendix B: Arthur D. Little reported savings of approximately 25 % compared to single-speed motor systems in 1999; Tecumseh Products Company demonstrated that energy savings of 15% An average of the estimates of this cost increase provided by the manufacturers weighted by manufacturer market share is near $56; an additional $30 for addition of an electronic control system Using average of two studies: 20% at $86 cost | 3-3512 | 15 | 15 | AEO 2010 NEMS
383 | Use variable speed compressors in residential refrigerators | R: VSCs for Refrigeration | Compressor | 5 | 4 | Residential | Refrigeration | Rfrg/Frz | New | Energy Savings (%) | 20% | 0% | Yes | 8-year payback |  |  | 93.96 | per unit | 1 C/R: No FS: All electric to all electric | All residential refrigerators and freezers | 17 | 2010 | DOE TSD; http://www.homeenergy.org/article_preview.php?id=21&article_title=Motors_Matter | BTO Tool: Max Tech report gives 9% for sectoral savings; 20% energy savings; Improves motor efficiency (permanent magnets), increases operating effectiveness (less fluid heated or cooled), and reduces cycling losses; Necessitates use of brushless DC fan motors to capture efficiency gains Primary Manufacturer: Embraco Calculated from Table 3 in article; Total National Potential Energy Savings (kWh/yr) * payback (yr) * energy cost ($/kWh) / # fridges (AEO 2010) | 1-92 | 17 | 17 | AEO 2014 NEMS
384 | Use variable speed evaporator fans (using ECM fan motors) in select new commercial refrigeration equipment | C: Refrig. Var Speed Evaporator Fan | Evaporator | 5 | 4 | Commercial | Refrigeration | Walk-In Cooler, Walk-In Frz | Supermarket | Energy Savings (%) | 4.5% | 0% | No | 138 |  |  | 138 | per unit | 1 C/R: No FS: All electric to all electric | All walk-in coolers and freezers | 11 | 2010 | Table 5-13, 14, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment | BTO Tool: 4% for Frz, 5% for Cooler | 3-3508 | 11 | 11 | AEO 2010 NEMS
387 | Launch campaign to encourage building sealing in homes | R: Reduce Infiltration (25%) | Infiltration | 5 | 4 | Residential | HVAC | Infiltration control | Single family | Energy Savings (%) | 25% | 0% | Yes | 300 |  | 300 | 300 | per home; 30x40 home, 2 stories, 10' per story | 40 R: No FS: Infiltration specific | Total heating and cooling lost through infiltration in all homes | 30 | 2010 | NREL measure database | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: Based on contractor interview | 1-109 | 30 | 30 | AEO 2014 NEMS
388 | Move to 2x4+1" sheathing in residential codes | R: Code: 2x4 + 1" sheathing | Walls | 5 | 4 | Residential | HVAC | Walls | New buildings | R-value | 17.1 | 11.1 | Yes | $0.28/sq-ft | 0 | 728 | 728 | per home; 30x40 home, 2 stories, 10' per story | 34 R: No FS: Wall specific | Total heating and cooling lost through walls in new single/multi/mobile homes | 30 | 2010 | http://www.toolbase.org/Technology-Inventory/walls/structural-insulated-sheathing | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: 30x40' 2-story house assumed. Represents moving average wall construction to indicated R-value | 1-120 | 30 | 30 | AEO 2014 NEMS
389 | Move to 2x4+ radiant barrier in residential codes | R: Code: 2x4 + radiant | Walls | 5 | 4 | Residential | HVAC | Walls | New buildings | R-value | 18.1 | 11.1 | Yes | $0.19/sq-ft |  | 494 | 494 | per home; 30x40 home, 2 stories, 10' per story | 34 R: No FS: Wall specific | Total residential heating and cooling lost through walls in all homes | 30 | 2010 | http://www.toolbase.org/Technology-Inventory/walls/structural-insulated-sheathing | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: 30x40' 2-story house assumed | 1-177 | 30 | 30 | AEO 2014 NEMS
390 | Move to 2x6 (advanced framing, 24" OC + R-19) construction in residential codes | R: R-19 Code: 2x6, 24" On Center Framing | Walls | 5 | 4 | Residential | HVAC | Walls | New buildings | R-value | 19.6 | 11.1 | Yes | $0.00/sq-ft |  | 0 | 0 | per home; 30x40 home, 2 stories, 10' per story | 34 R: No FS: Wall specific | Total heating and cooling lost through walls in new single/multi/mobile homes | 30 | 2010 | NREL technology fact sheet 26449.pdf Primary Source: NAHB Research Center; Southface Energy Institute; Oark Ridge National Laboratory; National Renewable Energy Laboratory; "Technology Fact Sheet: Advanced Framing" (2000 | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: Assumes 24" studs and no increase in window/door cost for equivalent cost. Represents moving average wall construction to indicated R-value Appendix B: "Fully implementing advanced framing techniques can result in materials cost savings of about $500-$1000 (for a 1,200-2,400-square-foot house, respectively), labor cost savings of between 3 and 5 percent, and annual heating and cooling cost savings of up to 5 percent." Scaleed up 5% whole-building savings to share of wall load | 1-120 | 30 | 30 | AEO 2014 NEMS
396 | Insulate crawl spaces to R-17 in all homes | R: R-17 Crawl Spaces | Basement | 5 | 3 | Residential | HVAC | Basement | Existing single family | R-value | 17 | 4 | Yes | $0.19/sq.ft. |  | 228 | 228 | per home; 30x40 home, 2 stories, 10' per story | 38 R: No FS: Foundation specific | Total heating and cooling energy lost through crawl space foundation in all homes | 30 | 2012 | http://www.radiantguard.com/how-to-install-radiant-barrier.aspx Primary Source: Savings: First principles (market and baseline drawn from RECs analysis) Cost: NREL measure database | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 1-110 | 30 | 30 | AEO 2014 NEMS
397 | Continue better buildings program targeting 25% whole-home consumption | R: Better buildings (25%)* | Whole building | 5 | 0 | Residential | All End Uses | Whole building | Existing homes | Energy Savings (%) | 25% | 0% | Yes | $2.8B leveraged, 80% assumed mat & labor; $485M program |  |  | 10000 | per home | 59 R: No FS: All fuels/end-uses | Total residential energy consumption by existing (pre-2010) single-family homes | 30 | 2014 | EERE website | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 1-2 | 30 | 30 | AEO 2014 NEMS
398 | Launch campaign to encourage "drill-and-fill" insulation in existing single family homes (FOA TARGET) | R: "Drill & Fill" pre-70's* | Walls | 5 | 0 | Residential | HVAC | Walls | Single family | R-value | 15 | 6 | Yes | $2.50/sq-ft; UPDATED TO BE FOA TARGET: R >= 8 and Cost of $0.08/SF per R-Value | 0 | 3120 | 3120 | per home; 30x40 home, 2 stories, 10' per story | 34 R: No FS: Wall specific | Total heating and cooling energy lost through walls in all single family homes built before 1970 | 30 | 2014 | Savings: first principles. Cost: NREL retrofit measure database | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 1-111 | 30 | 30 | AEO 2014 NEMS
399 | Research, demonstrate, and deploy dynamic windows in new commercial buildings | C: Dynamic Windows (N) (MYP2025)* | Windows | 5 | 0 | Commercial | HVAC | Windows | New | Energy Savings (%) | 38.34% | 0% | Yes | $18/sqft vs. $10 for IGU; target: $8 incremental cost | 3.6 | 6.48 | 2.88 | per square foot; wall: floor space of .9, window fill ratio of 0.4 | 33 C: No FS: Window (cond+rad) specific | Total commercial solar heat gain cooling + total commercial conductive window loss in new commercial buildings | 40 | 2025 | Lee, E.S., Yazdanian, M. & Selkowitz, S.E. The Energy-Savings Potential of Electrochromic Windows in the US Commercial Buildings Sector. Building 1-42 (2004). Cost: Personal communication - manufacturers and experts Other Supporting Sources: Arasteh, D.; Selkowitz, S.; Apte, J.; "Zero Energy Windows"; 2006 ACEEE Summer Study on Energy Efficiency in Buildings | 1) Cost: RFI 2013 PNNL: 2025 DOE Roadmap target premium of $5-$10/sq.ft.; current (2010) cost with VIP: $50/sq.ft. 2015 DOE Roadmap incremental cost target is $20/sq.ft. 2) Energy savings: SHGF improvement, 50% of time from 0.47 to 0.09 (40% (includes 50% of the time) decrease in cooling losses); and increase in R value from 1.86 to 3.45 (46% improvement in heating and cooling losses). Weighted average for % improvement in performance is approximated based on heating and cooling AEO market consumption estimates in the year 2010 and component window loads from additional data tab. | 3-3635 | 40 | 40 | AEO 2010 NEMS
400 | Research, demonstrate, and deploy dynamic windows in new homes | R: Dynamic Windows (N)(MYP2025)* | Windows | 5 | 0 | Residential | HVAC | Windows | New | Energy Savings (%) | 51.37% | 0% | Yes | $18/sqft vs. $10 for IGU; target: $8 incremental cost | 1920 | 3996 | 2076 | per home; wall: floor space of .9, window fill ratio of 0.4; 222 ft^2 of window area (BED 2011) | 30 R: No FS: Window (cond+rad) specific | Total heating and cooling energy lost through windows in all new homes due to conduction and radiation | 30 | 2025 | Program Primary Source: Arasteh, D.; Selkowitz, S.; Apte, J.; "Zero Energy Windows"; 2006 ACEEE Summer Study on Energy Efficiency in Buildings Other Supporting Sources: Lee, E.S., Yazdanian, M. & Selkowitz, S.E. The Energy-Savings Potential of Electrochromic Windows in the US Commercial Buildings Sector. Building 1-42 (2004). Cost: Personal communication - manufacturers and experts | 1) Cost: RFI 2013 PNNL: 2025 DOE Roadmap target premium of $5-$10/sq.ft.; current (2010) cost with VIP: $50/sq.ft. 2015 DOE Roadmap incremental cost target is $20/sq.ft. 2) Energy Savings: SHGF improvement, 50% of time from 0.47 to 0.09 (40% decrease in cooling losses); and increase in R value from 1.61 to 3.45 (53% improvement in heating and cooling losses). Weighted average for % improvement in performance is approximated based on heating and cooling AEO market consumption estimates in the year 2010 and component window loads from additional data tab. | 1-155 | 30 | 30 | AEO 2014 NEMS
401 | Research, demonstrate, and deploy dynamic windows in existing homes | R: Dynamic Windows (E)(MYP2025)* | Windows | 5 | 0 | Residential | HVAC | Windows | Retrofit | Energy Savings (%) | 51.37% | 0% | Yes | $18/sqft vs. $10 for IGU; target: $8 incremental cost | 1920 | 3996 | 2076 | per home; wall: floor space of .9, window fill ratio of 0.4; 222 ft^2 of window area (BED 2011) | 30 R: No FS: Window (cond+rad) specific | Total heating and cooling energy lost through windows in homes built pre-2010 due to conduction and radiation (use for dynamic windows that would not cause reduction in heat gain during winter) | 30 | 2025 | Program Primary Source: Arasteh, D.; Selkowitz, S.; Apte, J.; "Zero Energy Windows"; 2006 ACEEE Summer Study on Energy Efficiency in Buildings Other Supporting Sources: Lee, E.S., Yazdanian, M. & Selkowitz, S.E. The Energy-Savings Potential of Electrochromic Windows in the US Commercial Buildings Sector. Building 1-42 (2004). Cost: Personal communication - manufacturers and experts | 1) Cost: RFI 2013 PNNL: 2025 DOE Roadmap target premium of $5-$10/sq.ft.; current (2010) cost with VIP: $50/sq.ft. 2015 DOE Roadmap incremental cost target is $20/sq.ft. 2) Energy Savings: SHGF improvement, 50% of time from 0.47 to 0.09 (40% decrease in cooling losses); and increase in R value from 1.61 to 3.45 (53% improvement in heating and cooling losses). Weighted average for % improvement in performance is approximated based on heating and cooling AEO market consumption estimates in the year 2010 and component window loads from additional data tab. | 1-156 | 30 | 30 | AEO 2014 NEMS
402 | Research, demonstrate, and deploy dynamic windows in existing commercial buildings | C: Dynamic Windows (E)(MYP2025)* | Windows | 5 | 0 | Commercial | HVAC | Windows | Retrofit | Energy Savings (%) | 38.34% | 0% | Yes | $18/sqft vs. $10 for IGU; target: $8 incremental cost | 3.6 | 6.48 | 2.88 | per square foot; wall: floor space of .9, window fill ratio of 0.4 | 33 C: No FS: Window (cond+rad) specific | Total commercial solar heat gain cooling + total commercial conductive window loss in existing building (use for dynamic windows where heat gain during winter is not affected) | 40 | 2025 | Program Primary Source: Lee, E.S., Yazdanian, M. & Selkowitz, S.E. The Energy-Savings Potential of Electrochromic Windows in the US Commercial Buildings Sector. Building 1-42 (2004). Cost: Personal communication - manufacturers and experts Other Supporting Sources: Arasteh, D.; Selkowitz, S.; Apte, J.; "Zero Energy Windows"; 2006 ACEEE Summer Study on Energy Efficiency in Buildings | 1) Cost: RFI 2013 PNNL: 2025 DOE Roadmap target premium of $5-$10/sq.ft.; current (2010) cost with VIP: $50/sq.ft. 2015 DOE Roadmap incremental cost target is $20/sq.ft. 2) Energy savings: SHGF improvement, 50% of time from 0.47 to 0.09 (40% (includes 50% of the time) decrease in cooling losses); and increase in R value from 1.86 to 3.45 (46% improvement in heating and cooling losses). Weighted average for % improvement in performance is approximated based on heating and cooling AEO market consumption estimates in the year 2010 and component window loads from additional data tab. | 3-3634 | 40 | 40 | AEO 2010 NEMS
405 | Develop integrated roofing package for new homes in non-hot climates using phase change materials (PCM) for R-75 equivalent | R: R-75 PCM Roof, non-hot CZ (N) | Roof | 5 | 2 | Residential | HVAC | Roof/ attic insulation | New homes | R-value | 75 | 38 | Yes | $1.30/sq-ft |  | 1801.3328 | 1801.3328 | per home; 30x40 home, 2 stories, 10' per story | 36 R: No FS: Roof specific | Total heating and cooling energy lost through attics in all new homes in all non-hot climates | 40 | 2018 | Miller, W. & Kosny, J. Next-Generation Roofs and Attics for Homes. ACEEE Summer Study on Energy Efficiency in Buildings 180-195 (2008) | No notes | 1-112 | 40 | 40 | AEO 2014 NEMS
406 | Implement R-11 basement insulation in all homes | R: Basement, +R-11 | Basement | 5 | 3 | Residential | HVAC | Basement | Existing single family | R-value | 15 | 4 | Yes | $0.46/sq-ft | 0 | 1196 | 1196 | per home; 30x40 home, 2 stories, 10' per story | 38 R: No FS: Foundation specific | Total heating and cooling energy lost through basements in all homes | 30 | 2012 | Savings: First principles (market and baseline drawn from RECs analysis). Cost: NREL measure database | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Appendix B: R-15 is effective total assmely thermal resistance after adding R-11 insulation | 1-113 | 30 | 30 | AEO 2014 NEMS
410 | Implement R-60 attic insulation in poorly insulated home attics | R: Poorly Ins. Attics, +R-60 [E] | Roof | 5 | 4 | Residential | HVAC | Roof/ attic insulation | Existing homes | R-value | 64 | 4 | Yes | $2.10/sq-ft | 0 | 5460 | 5460 | per home; 30x40 home, 2 stories, 10' per story | 36 R: No FS: Roof specific | Total heating and cooling energy loss through attics in all homes with poorly insulated attics | 30 | 2010 | Primary Source: Savings: first principles increasing R-value. Cost: NREL measure database | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Appendix B: Increase from R-4 assembly to R-60 | 1-187 | 30 | 30 | AEO 2014 NEMS
411 | Implement R-60 attic insulation in well insulated home attics | R: Well Ins. Attics, +R-41 [E] | Roof | 5 | 4 | Residential | HVAC | Roof/ attic insulation | Existing homes | R-value | 64 | 23 | Yes | $1.50/sq-ft | 0 | 3900 | 3900 | per home; 30x40 home, 2 stories, 10' per story | 36 R: No FS: Roof specific | Total heating and cooling energy loss through attics in all homes with moderately insulated attics | 30 | 2010 | Savings: first principles increasing R-value. Cost: NREL measure database | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Appendix B: Increase from R-23 assembly to R-60 | 1-186 | 30 | 30 | AEO 2014 NEMS
414 | Launch campaign to encourage cool coating choices for homes in hot climates | R: Cool Paint Color | Use Intensity | 4 | 3 | Residential | HVAC | Paint | Hot climates | Energy Savings (%) | 4% | 0% | Yes | $0.10/SF |  | 280 | 280 | per home; 30x40 home, 2 stories, 10' per story | 1 C/R: No FS: All electric to all electric | Total cooling in all homes in hot climates | 15 | 2013 | HES pro runs, ORNL CoolWall report Primary Source: Tom Petrie, Jerry Atchley, Phil Childs, and André Desjarlais; "Energy Savings for Stucco Walls Coated with Cool Colors" ORNL (12/2007) Other Supporting Sources: Additional support by running HES Pro in multipl climate zones to verify savings | BTO Tool: 2-3% savings in moderate climates as well, these are ignored; Model says 15%, gave back 33% for shading, dirt, etc. Appendix B: "Savings are 4-9% compared to non-IR reflecting walls" DQ was lowered slightly upon request of the TDM at the first meeting. | 1-33 | 15 | 15 | AEO 2014 NEMS
415 | Launch campaign to encourage cool coating choices for comm. Buildings in hot climates | C: Cool Paint Color | Use Intensity | 4 | 3 | Commercial | HVAC | Paint | Hot climates | Energy Savings (%) | 6% | 0% | Yes | Cost premium of $0.31/SF of wall area (based on cool coating for #381 cool roofs cost) |  |  | 0.34444 | per square foot; floor to wall ratio of 0.9 | 10 C: No FS: All fuels cooling (elec+NG) | All commercial cooling in the hottest 2 climates | 15 | 2013 | 1) Tom Petrie, Jerry Atchley, Phil Childs, and André Desjarlais; "Energy Savings for Stucco Walls Coated with Cool Colors" ORNL (12/2007) 2) Additional support by running HES Pro in multiple climate zones to verify savings. 3) Incremental cost of cool coating has not been developed yet, but it is assumed to be the same as the cost for cool roofs coating. Data reviewed and submitted by experts from Fraunhofer Center for Sustainable Energy Systems during peer review. | BTO Tool: 2-3% savings in moderate climates as well, these are ignored; Model says 15%, gave back 33% for shading, dirt, etc. Appendix B: "Savings are 4-9% compared to non-IR reflecting walls". DQ was lowered slightly upon request of the TDM at the first meeting. | 3-3611 | 15 | 15 | AEO 2010 NEMS
419 | Move to standardize advanced wall construction techniques in new homes | R: Adv. Framing in Codes (N) | Walls | 5 | 4 | Residential | HVAC | Walls | Consumption | R-value | 14.6 | 11.1 | Yes | -750 |  |  | -750 | per home | 34 R: No FS: Wall specific | Total heating and cooling lost through walls in new single/multi/mobile homes | 30 | 2010 | http://www.energysavers.gov/your_home/designing_remodeling/index.cfm/mytopic=10090 Primary Source: National Assocation of Home Builders, Southface Energy Institiute & Oak Ridge National Laboratory ADVANCED WALL FRAMING. U.S. Department of Energy (2000). Other Supporting Sources: Straube, J. & Smegal, J. Building America Special Research Project: High-R Walls Case Study Analysis. Building Science 68 (Somerville, MA, 2009). | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: http://www.energysavers.gov/your_home/designing_remodeling/index.cfm/mytopic=10090 Appendix B: "Advanced framing techniques can result in materials cost savings of [$500-$1000], labor cost savings of [3-5%], and annual heating and cooling cost savings of up to 5 percent." Savings includes material cost only; average (4%) heating and cooling sclaed up from full building to walls portion | 1-120 | 30 | 30 | AEO 2014 NEMS
421 | Research and demonstrate R-10 windows in homes | R: R-10 Windows | Windows | 5 | 2 | Residential | HVAC | Windows | All | R-value | 10 | 1.61 | Yes | $15/sq.ft. premium | 0 | 3330 | 3330 | per home; 222 ft^2 of window area (BED 2011) | 28 R: No FS: Window conduction specific | Total heating and cooling lost through windows due to conduction in all homes | 30 | 2025 | Southwall, Alpeninc, PNNL Lost Opportunities Primary Source: 6. Apte, J. & Arasteh, D. Window-Related Energy Consumption in the US Residential and Commercial Building Stock. Buildings 1-38 (Berkeley, CA, 2006). Personal communication: various window experts Other Supporting Sources: Arasteh, Dariush; Selkowitz, Steve; Apte, Josh; LaFrance, Marc. Energy Impacts of Today’ s Window Stock | BTO Tool: Does not include system benefits Appendix B: See tables 4 and 7 for use and savings Calculated from first principles; costs from NREL bottom-up VIG build | 1-114 | 30 | 30 | AEO 2014 NEMS
422 | Research and demonstrate R-10 windows in commercial buildings | C: R-10 Windows | Windows | 5 | 2 | Commercial | HVAC | Windows | All | R-value | 10 | 1.86 | Yes | $29/sq.ft. premium | 0 | 10.6632 | 10.6632 | per square foot; wall: floor space of .9, window fill ratio of 0.4 | 31 C: No FS: Window conduction specific | Total window conductive loss in all commercial buildings | 40 | 2025 | Southwall, Alpeninc, PNNL Lost Opportunities Primary Source: 6. Apte, J. & Arasteh, D. Window-Related Energy Consumption in the US Residential and Commercial Building Stock. Buildings 1-38 (Berkeley, CA, 2006). Personal communication: various window experts Other Supporting Sources: Arasteh, Dariush; Selkowitz, Steve; Apte, Josh; LaFrance, Marc. Energy Impacts of Today’ s Window Stock | BTO Tool: Does not include system benefits Appendix B: See tables 4 and 7 for use and savings Calculated from first principles; costs from NREL bottom-up VIG build | 3-3637 | 40 | 40 | AEO 2010 NEMS
423 | Deploy and move to standardize residential door R-values | R: R-7 Doors | Doors | 5 | 4 | Residential | HVAC | Doors | All | R-value | 7.1429 | 1.8182 | No | 90 |  | 90 | 90 | per unit | 46 R: No FS: Door specific | Total heating and cooling lost through doors in all homes | 30 | 2010 | Lowe's, NREL database Primary Source: Savings: First principles (market and baseline drawn from RECs analysis) Cost: NREL measure database |  | 1-115 | 30 | 30 | AEO 2014 NEMS
425 | Launch campaign to encourage addition of sheathing and insulation when replacing siding in existing homes | R: Sheathing & Insulation [E] | Walls | 5 | 4 | Residential | HVAC | Walls | Single EOL retrofit w/ siding | R-value | 20 | 6 | Yes | $6.70/sq-ft | 10250 | 17420 | 7170 | per home; 2,600 sq.ft. wall space | 34 R: No FS: Wall specific | Total heating and cooling lost through walls in homes built before 2010 | 30 | 2010 | NREL measure database | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 1-126 | 30 | 30 | AEO 2014 NEMS
426 | Increase deployment of home wrap on new homes | R: Building Wrap (N) | Infiltration | 5 | 5 | Residential | HVAC | Infiltration control | New | Energy Savings (%) | 13% | 0% | Yes | $748/2000 sq-ft home inflated to 2011 |  | 1040.5644 | 1040.5644 | per home | 40 R: No FS: Infiltration specific | Total heating and cooling lost through infiltration in all new homes | 30 | 2010 | Program Primary Source: Architectural Energy Company, "Impact of Title 24 Residential Air Leakage Reduction Credit on Water-Resistive Barriers in California Homes", 2006 | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: Uses two layer/ double ply with tape cost Appendix B: Blower door testing indicated that the replacement of two layers of Grade D building paper with a spun-bonded polyolefin housewrap reduced the SLA by an average of 13% (Wilcox, 2001). | 1-116 | 30 | 30 | AEO 2014 NEMS
427 | Increase deployment of building wrap on new commercial buildings | C: Building Wrap (N) | Infiltration | 5 | 5 | Commercial | HVAC | Infiltration control | New | ACH | 0.015 | 0.038 | Yes | $1.40/sq-ft |  | 1.26 | 1.26 | per square foot; wall: floor space of .9, window fill ratio of 0.4 | 41 C: No FS: Infiltration specific | Total heating and cooling lost through infiltration in new commercial buildings | 40 | 2010 | NREL 46100 building research Primary Source: Elaine Hale, Matthew Leach, Adam Hirsch, and Paul Torcellini, "General Merchandise 50% Energy Savings Technical Support Document"; NREL/TP-550-46100 September 2009 | BTO Tool: Peer Review Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Note: There are some possible ways to drive cost to $3.40/SF. Appendix B: The air barrier is assumed to reduce the envelope infiltration from 0.038 to 0.015 ACH… The cost of the air barrier is estimated at $1.40/ft2 of exterior wall area. MTG2: A few market barriers present. | 3-3670 | 40 | 40 | AEO 2010 NEMS
431 | Move to standardize vestibules on commercial buildings | C: Vestibules | Doors | 5 | 4 | Commercial | Building | Doors | All | ACH | 0.158 | 0.253 | Yes | 5853 |  | 0.7804 | 0.7804 | per square foot; two vestibules per 15,000 sq. ft. | 41 C: No FS: Infiltration specific | No vestibule infiltration | 40 | 2010 | 1) pg. 47. Elaine Hale, Matthew Leach, Adam Hirsch, and Paul Torcellini, "General Merchandise 50% Energy Savings Technical Support Document"; NREL/TP-550-46100 September 2009. 2) http://www.hortondoors.com/content.aspx?cid=1232 | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Appendix B: reduce the front door infiltration from 0.253 to 0.158 ACH. The cost... replacing two, 8-ft tall sliding doors with a total surface area of 120 ft2 with four, 7-ft tall sliding doors and adding 30 linear feet of interior walls: $5,853 | 3-3640 | 40 | 40 | AEO 2010 NEMS
432 | Demonstrate and deploy whole-building designs for new homes | R: New home (40%)* | Whole building | 5 | 0 | Residential | All End Uses | Whole building | New homes | Energy Savings (%) | 40% | 0% | Yes | See incremental cost |  | 150000 | 3615 | per home | 59 R: No FS: All fuels/end-uses | Total residential energy consumption in all new homes | 30 | 2014 | BeOPT/ OPT Eplus | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: Assumes 1 year energy modeler/ architect time to design home to capture natural resources; assume leveraged across 10,000 homes; additional cost of home at $2/sq ft | 1-1 | 30 | 30 | AEO 2014 NEMS
433 | Demonstrate and deploy 40% whole-building designs for new commercial buildings | C: New building (40%)* | Whole building | 5 | 0 | Commercial | HVAC/Lighting | Whole building | New buildings | Energy Savings (%) | 40% | 0% | Yes |  |  | 9.5 | 9.5 | per unit | 60 C: No FS: All fuels/end-uses | All energy consumption in new buildings | 40 | 2014 | Extrapolated based on 50% TSD Opt-E-Plus runs | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 3-3633 | 40 | 40 | AEO 2010 NEMS
434 | Adjusts washer operation and washing conditions based on soil load, etc., in coin-op class commercial washers | C: CW Soil Sensors | Use Intensity | 4 | 3 | Commercial | Washing & Drying | Single-Load, Top- and Front-Loading Clothes Washer | Coin Laundries, Mulit-Family Common Areas | Energy Savings (%) | 10% | 0% | Yes | 56.75 |  |  | 100 | per unit; 3.8 ft^3 capacity | 48 C: No FS: All fuels WH to all fuels WH | Total water heating energy use by single load coin operated washers | 7.1 | 2013 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf | BTO Tool: Compare LG MODEL #:WM0642HW with GE MODEL #:WCVH6600HMS; see http://www.lowimpactliving.com/products/Appliances/Washing-Machines-%28laundry%29/310; part number 617804 from Siemens WM14S890GB = 37 GBP Appendix B: Table 8-23, page 257, see "adaptive control system" | 3-3523 | 7.1 | 7.1 | AEO 2010 NEMS
435 | Adjusts washer operation and washing conditions based on soil load, etc., in residential washers | R: CW Soil Sensors | Use Intensity | 5 | 3 | Residential | Washing & Drying | Single-Load, Top- and Front-Loading Clothes Washer | Home | Energy Savings (%) | 10% | 0% | Yes | 56.75 |  |  | 100 | per unit; 3.8 ft^3 capacity | 47 R: No FS: All fuels WH to all fuels WH | Total water heating energy use by residential clothes washers | 11 | 2013 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf | BTO Tool: Assumed same as commercial; ; part number 617804 from Siemens WM14S890GB = 37 GBP Appendix B: Table 8-23, page 257, see "adaptive control system" | 1-56 | 11 | 11 | AEO 2014 NEMS
436 | Deploy improved agitator design to reduce hot water usage in coin-op commercial washers | C: Advanced Agitation CW | Spin Cycle | 5 | 3 | Commercial | Washing & Drying | Clothes Washer: Single-Load, Top-Loading | Coin Laundries, Mulit-Family Common Areas | Energy Savings (%) | 15% | 0% | Yes | Not availalble |  |  |  | per unit | 48 C: No FS: All fuels WH to all fuels WH | Total water heating energy use by top loading coin operated washers | 7.1 | 2013 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf | BTO Tool: GE Hydromotion™ uses no agitator Appendix B: Table 8-23, page 257, see "advanced agitation" | 3-3524 | 7.1 | 7.1 | AEO 2010 NEMS
437 | Implement ozone laundry systems as a retrofit that dissolve ozone in cold water to reduce hot water usage in any multi-load/washer-extractor clothes washers. | C: Multi-load CW Ozone Laundry Systems | System | 5 | 4 | Commercial | Washing & Drying | Multi-Load Clothes Washers | On Premises Laundry (Hotels, Hospitals, Universities, Prisons) | Energy Savings (%) | 89% | 0% | No | $10,000-$12,000 for a small system, and $5000 for installation and shipping; and $45,000 plus $10,000 for installation and shipping for the largest capacity system. |  | 35500 | 35500 | per unit | 48 C: No FS: All fuels WH to all fuels WH | Total water heating energy use by multi-load washers | 15 | 2010 | 1) Tables 8-24 and 8-25, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf 2) Savings confirmed in Pg. 10 of Cold Facts EcoTex. Clear Water Tech 2013. 3) Typical cost of an ozone system is an average between the smallest and the largest capacity systems, and includes shipping and installation from pg.21 of Riesenberger, James. PBMP - Commercial Laundry Facilities. Koeller and Company. This is a system that is installed as an addition/retrofit to any washer-extractor/multi-load washer system. | Tim Sutherland/NCI: Ozone systems are readily available on the market (deployment level 4). Energy savings is well understood, although savings at each specific site may vary due to the unique washing needs of the site. Energy savings (% over today's base) The 89% energy savings here is a best-case scenario. In reality, savings at each site will vary depending on the specific laundry needs of each site. We don't have a citable source yet for a lower number (our ozone study will be complete this summer), but just realize that 89% is an ambitious upper bound. A more realistic number is probably around 75% on average. Note that the larger ozone systems can often be used on multiple washers (typically up to 4 washers for the largest systems, or 2 washers for medium-size systems). | 3-3526 | 15 | 15 | AEO 2010 NEMS
438 | Increase deployment of improved design tunnel washers for even less hot water use | C: Advanced Tunnel Washers | System | 5 | 3 | Commercial | Washing & Drying | Tunnel Washer | Off Site and Industrial Facilities | Energy Savings (%) | 60% | 0% | No | See incremental cost |  |  | 1200000 | per unit | 48 C: No FS: All fuels WH to all fuels WH | Total energy use by commercial tunnel washers (assuming all WH energy use) | 11 | 2010 | Tables 8-26 and 8-27, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf | BTO Tool: http://www.americanlaundrynews.com/article.cfm?articleId=17886 Appendix B: Table 8-27, page 259, see "advanced tunnel washer" | 3-3527 | 11 | 11 | AEO 2010 NEMS
440 | Deploy sensors and controls to detect size of load and adjust water level appropriately in commercial clothes washers | C: CW - Auto Fill Control | Use Intensity | 5 | 3 | Commercial | Washing & Drying | Single-Load, Top-Loading Clothes Washer | Coin Laundries, Mulit-Family Common Areas | Energy Savings (%) | 15% | 0% | Yes | See incremental cost |  |  | 20 | per unit | 48 C: No FS: All fuels WH to all fuels WH | Total water heating energy use by top loading coin operated washers | 7.1 | 2011 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Control is available in residential units; approximate cost based on replacement of water level control sensor for *residential* unit | BTO Tool: Available in residential units; approximate cost based on replacement of water level control sensor for *residential* unit Appendix B: Table 8-23, page 257, see "automatic fill control" | 3-3524 | 7.1 | 7.1 | AEO 2010 NEMS
441 | Deploy automatic sprayer shutoff sensors that detect the presence of dish racks in conveyor-type commercial dishwashers | C: DW Auto Sprayer Shutoff | Sprayer | 5 | 3 | Commercial | Washing & Drying | Conveyor Dishwashers | Restaurants | Energy Savings (%) | 50% | 0% | Yes | $9192 in energy savings in one year | 20000 | 24000 | 4000 | per unit | 48 C: No FS: All fuels WH to all fuels WH | Total water heating energy use by conveyor type dishwashers | 20 | 2011 | Tables 4-11,4-21, and 4-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances Primary Source: Hobart Cle Warewasher Opti-Rinse, http://www.hobartcorp.com/products/warewashing/conveyor-type/cle-warewasher/ | BTO Tool: Hobart Cle Warewasher Opti-Rinse, http://www.hobartcorp.com/products/warewashing/conveyor-type/cle-warewasher/ Appendix B: "Exclusive Opti-Rinse™ technology for 50% less energy and water usage than comparable models" | 3-3534 | 20 | 20 | AEO 2010 NEMS
442 | Replace conventional dry cleaning with liquid CO2 in new systems | C: Carbon Dioxide Dry Cleaning | System | 5 | 3 | Commercial | Washing & Drying | Dry Cleaning System | Dry Cleaners | Energy Usage, BTU/100lbs | 13700000 | 22300000 | No | See incremental cost |  |  | 97500 | per unit | 55 C: No FS: Dry Cleaning Energy Use | Total dry cleaning energy use | 15 | 2011 | Figure 8-33, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances | BTO Tool: http://www.epa.gov/dfe/pubs/garment/lcds/micell.htm | 3-3528 | 15 | 15 | AEO 2010 NEMS
444 | Deploy economical heat exchanger in existing commercial standard capacity dryers | C: CD Exhaust Heat Recovery | Use Intensity | 3 | 3 | Commercial | Washing & Drying | Standard-Capacity Clothes Dryer | Retrofit | Energy Savings (%) | 45% | 0% | Yes | 0.4-1.25 yr payback |  |  | 200 | per unit | 52 C: No FS: All clothes dryer (elec+NG) to all clothes dryer (elect+NG) | Total energy use by single load coin operated dryers | 11 | 2012 | Tables 8-32, 8-36, Navigant Consulting; "Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances" (2009) | BTO Tool: http://rototherm.net/art_01.html; assume 1 million dryers; Appendix B: Tables 8-32 & 8-36 | 3-3529 | 11 | 11 | AEO 2010 NEMS
448 | Replace residential gas clothes dryers with modulating gas clothes dryers | R: Modulating Gas Dryer | Use Intensity | 2+ | 2 | Residential | Washing & Drying | Standard-Capacity Clothes Dryer | All | Energy Savings (%) | 15% | 0% | No | Assumed 5 year payback |  | 23.9231 | 23.9231 | per unit | 2 C/R: No FS: All gas to all gas | Total energy use by all natural gas clothes dryers | 12 | 2015 | Tables 8-32, 8-35, 8-36, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost assumes 5-year payback of savings of $6.09 per year | BTO Tool: High performance residential prototype (TIAX/DOE 2005); assume cost is twice residential Appendix B: Table 8-36, page 272, see "modulating gas burner" | 1-41 | 12 | 12 | AEO 2014 NEMS
450 | Increase adoption of residential heat pump clothes dryers | R: HP Clothes Dryer | System | 5 | 2 | Residential | Washing & Drying | Standard-Capacity Clothes Dryer | All | Energy Savings (%) | 50% | 0% | No | See existing & efficient costs | 455 | 879 | 424 | per unit | 1 C/R: No FS: All electric to all electric | Total energy use by all electric clothes dryers | 12 | 2015 | Market Cost: AHAM-2 Direct Final Rule (2011) TSD, Chapter 8, Table 8.2.9 Lifetime: AHAM-2 Direct Final Rule (2011) TSD, Chapter 8, Table 8.2.39 (http://www.regulations.gov/#!documentDetail;D=EERE-2007-BT-STD-0010-0053). Market Consumption and Stock: AHAM-2 Direct Final Rule (2011) TSD, Residential Clothes Dryer National Impact Analysis Spreadsheet (http://www.regulations.gov/#!documentDetail;D=EERE-2007-BT-STD-0010-0054). Market consumption is calculated as the product of market stock and per unit annual energy consumption in 2030. | http://www.eskimo.com/~nanook/future/2007/04/heat-pump-dryers.html; Available in Europe but twice cost and twice drying time; 41% energy savings for delicate, 31% savings for medium, 44% for large loads; High performance Resi HP prototype (TIAX, 2005). Table 8-36, page 272, see "heat pump". | 1-42 | 12 | 12 | AEO 2014 NEMS
451 | Increase deployment of commercial low-temp door type dishwashers: to include reduced water heating needs; low-flow sprayers, redesigned tanks, wall insulation | C: Low-temp door DW | System | 5 | 5 | Commercial | Washing & Drying | Door-Type Low-Temp Dishwasher | Schools, Restaurants, Hospitals, Catering Business | Energy Savings (%) | 36% | 0% | No | $2000; Payback: 1.5-2.5 yrs |  |  | 2000 | per unit | 61 Manual | Total energy use by low temperature dishwashers (with doors) | 15 | 2010 | Tables 4-22 (pg.104) and 4-8, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf |  | 3-3535 | 15 | 15 | AEO 2010 NEMS
452 | Increase deployment of commercial high-temp door type dishwashers: to include reduced water heating needs; low-flow sprayers, redesigned tanks, wall insulation | C: High-temp door DW | System | 5 | 5 | Commercial | Washing & Drying | Door-Type High-Temp Dishwasher | Schools, Restaurants, Hospitals, Catering Business | Energy Savings (%) | 33% | 0% | No | $2100; Payback: 1.5-2.6 yrs |  |  | 2100 | per unit | 61 Manual | Total energy use by high temperature dishwashers (with doors) | 15 | 2010 | Tables 4-22 (pg.104) and 4-8, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf |  | 3-3536 | 15 | 15 | AEO 2010 NEMS
453 | Increase deployment of commercial low-temp conveyer type dishwashers: to include reduced water heating needs; low-flow sprayers, redesigned tanks, wall insulation, auto sprayer shutoff, waste heat recovery | C: Low-temp conveyor DW | System | 5 | 5 | Commercial | Washing & Drying | Conveyor Low-Temp Dishwasher | Hotels, Large Restaurants, Schools, Universities, Hospitals | Energy Savings (%) | 30% | 0% | No | $3-4k; Payback: 2-4 yrs |  |  | 3500 | per unit | 61 Manual | Total energy use by conveyor low temperature dishwashers | 20 | 2010 | Tables 4-22 (pg.104) and 4-8, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf |  | 3-3537 | 20 | 20 | AEO 2010 NEMS
454 | Increase deployment of commercial high-temp conveyer type dishwashers: to include reduced water heating needs; low-flow sprayers, redesigned tanks, wall insulation, auto sprayer shutoff, waste heat recovery | C: High-temp conveyor DW | System | 5 | 5 | Commercial | Washing & Drying | Conveyor High-Temp Dishwasher | Hotels, Large Restaurants, Schools, Universities, Hospitals | Energy Savings (%) | 30% | 0% | No | $3-4k; Payback: 1.5-2.5 yrs |  |  | 3500 | per unit | 61 Manual | Total energy use by conveyor high temperature dishwashers | 20 | 2010 | Tables 4-22 (pg.104) and 4-8, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf |  | 3-3538 | 20 | 20 | AEO 2010 NEMS
455 | Highest efficiency standard-sized residential dishwashers defined as level 5 in 05/2012 rulemaking TSD | R: Max tech DW (L5 of 5) | System | 5 | 3 | Residential | Dishwashing | Dishwasher | New | Energy Usage, kWh/yr | 180 | 355 | No | 1800 | 400 | 2099 | 1699 | per unit | 50 R: No FS: Dishwashing and its associated water heating energy use | All residential dishwashing and its water heating energy use | 19 | 2013 | Standards rulemaking TSD published in 05/2012 | Standards rulemaking TSD published in 05/2012: 1) Standard sized dishwashers manufactured after 01/2010 shall not exceed 355 kwh/year (includes WH) and 6.5 gal/cycle; compact size, 260 kwh/year and 4.5 gal/cycle. 2) Standard sized dishwashers manufactured after 06/2013 shall not exceed 307 kwh/year (includes WH) and 5 gal/cycle; compact size, 222 kwh/year and 3.5 gal/cycle. 3) Energy Star level effective 01/2012 is set at 295 kwh/year and 4.25 gal/cycle for standard DW; and 222 kwh/year and 3.5 gal/cycle for compact DW. 4) Most DW are standard-sized: 99% of the market. Market split between compact vs standard-sized DW? Does water use directly correlate to WH energy consumption (presumably not all water is heated... is it close enough that I can do % difference?) | 1-90 | 19 | 19 | AEO 2014 NEMS
456 | Deploy temperature and humidity sensors to reduce cycle time in commercial clothes dryers | C: CD: Impr. Cycle Termination | Use Intensity | 5 | 3 | Commercial | Washing & Drying | Standard-Capacity Clothes Dryer | New | Energy Savings (%) | 15% | 0% | Yes | 21 |  |  | 21 | per unit | 52 C: No FS: All clothes dryer (elec+NG) to all clothes dryer (elect+NG) | Total energy use by single load coin operated dryers | 11 | 2013 | Tables 8-32, 8-36, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost estimated from part currently in use in residential units. |  | 3-3529 | 11 | 11 | AEO 2010 NEMS
457 | Deploy automatic temperature and humidity termination sensors to reduce cycle time in residential clothes dryers | R: Clothes Dryer: Impr. Cycle Termination | Use Intensity | 2+ | 5 | Residential | Washing & Drying | Standard-Capacity Clothes Dryer | New | Energy Savings (%) | 12% | 0% | Yes | 21 | 500 | 521 | 21 | per unit | 51 R: No FS: All clothes dryer (elec+NG) to all clothes dryer (elect+NG) | Total energy use by all electric and natural gas clothes dryers | 12 | 2013 | 1) Cost: According to James Battaglia (NCI), no known credible estimates for the cost of improved automatic termination. Cost is approximated by Phil Pharese as the price of replacement temperature sensors. 2) Energy Savings: ENERGY STAR Market & Industry Scoping Report – Residential Clothes Dryers. November 2011 (http://www.energystar.gov/ia/products/downloads/ENERGY_STAR_Scoping_Report_Residential_Clothes_Dryers.pdf). Lifetime: AHAM-2 Direct Final Rule (2011) TSD, Chapter 8, Table 8.2.39 (http://www.regulations.gov/#!documentDetail;D=EERE-2007-BT-STD-0010-0053). 3) Market Consumption and Stock: AHAM-2 Direct Final Rule (2011) TSD, Residential Clothes Dryer National Impact Analysis Spreadsheet (http://www.regulations.gov/#!documentDetail;D=EERE-2007-BT-STD-0010-0054). Market consumption is calculated as the product of market stock and per unit annual energy consumption in 2030. 4) Tables 8-32, 8-36, page 272, see "improved cycle termination" Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf | Temp sensors are used in basically all dryers at this point. Moisture sensors are used in a good portion of dryers. This measure could also involve better control strategies for sensing dryness or using different types of sensors altogether (e.g., humidity sensors). ENERGY STAR is currently developing a performance specification based on DOE's recently adopted optional test procedure for dryers (10 CFR 430 subpart B appendix D2) which directly measures the effectiveness of automatic termination. http://www.energystar.gov/products/specs/clothes_dryers_specification_version_1_0_pd. Almost all clothes dryers use temperature sensors, while about 20-25% of dryers use moisture sensing controls (http://www.energystar.gov/products/specs/sites/products/files/D1_V1_Spec.pdf). Test procedure for directly measuring the effects of automatic cycle termination (10 CFR 430, subpart B, appendix D2) is not currently required for use. | 1-43 | 12 | 12 | AEO 2014 NEMS
459 | Demonstrate and deploy improved drum design for single-load commercial clothes washers | C: CW Improved Drum Design | Spin Cycle | 4 | 3 | Commercial | Washing & Drying | Clothes Washer: Single-Load, Top- and Front-Loading | Coin Laundries, Mulit-Family Common Areas | Energy Savings (%) | 20% | 0% | Yes | Assumed 3 year payback |  | 640.666 | 640.666 | per unit | 52 C: No FS: All clothes dryer (elec+NG) to all clothes dryer (elect+NG) | Total energy use by single load coin operated dryers | 7.1 | 2013 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost assumes 3-year payback from annual savings of $246 | BTO Tool: Reduce cycle time, improve wash performance, reduce mass, increase spin speed Appendix B: Table 8-23, page 257, see "improved drum design" | 3-3529 | 7.1 | 7.1 | AEO 2010 NEMS
460 | Deploy sprayers with smaller size holes to improve efficiency of residential dishwashers | R: DW: Impr. Hydraulic Efficiency | Sprayer | 5 | 4 | Residential | Dishwashing | All Dishwashers | New | Energy Savings (%) | 25% | 0% | Yes | No incremental cost |  |  | 0 | per unit | 1 C/R: No FS: All electric to all electric | Total dishwashing energy use, not including water heating consumption | 19 | 2010 | Dries, John, (2008), "Improving Dishwasher Efficiency", http://www.appliancemagazine.com/editorial.php?article=1978 | BTO Tool: Reduce spray hole diameters for higher pressure jets; assumed 5% cost reduction off average of top 5 froogle hits Appendix B: "Assuming that the upper and lower spray-arms operate the same amount of time, the average power consumption of this wash system went from 208 to 155 W, a reduction in overall power consumption of 25%, while improving the hydraulic washing power of the dishwasher—all without any increase to product cost or complexity. " | 1-173 | 19 | 19 | AEO 2014 NEMS
461 | Improved water extraction in commercial clothes washers to reduce drying time | C: CW: Improved Water Extraction | Spin Cycle | 5 | 4 | Commercial | Washing & Drying | Clothes Washer: Single-Load, Top- and Front-Loading | Coin Laundries, Mulit-Family Common Areas | Energy Savings (%) | 25% | 0% | Yes | Assumed 3 year payback |  | 800.8325 | 800.8325 | per unit | 52 C: No FS: All clothes dryer (elec+NG) to all clothes dryer (elect+NG) | Total energy use by single load coin operated dryers | 7.1 | 2010 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost assumes 3-year payback based on annual savings of $308.06 | BTO Tool: May be approaching practical limits Appendix B: Table 8-23, page 257, see "improved water extraction" | 3-3529 | 7.1 | 7.1 | AEO 2010 NEMS
462 | Improved water extraction in residential clothes washers to reduce drying time | R: CW: Improved Water Extraction | Spin Cycle | 5 | 4 | Residential | Washing & Drying | Clothes Washer: Single-Load, Top- and Front-Loading | Coin Laundries, Multi-Family Common Areas | Energy Savings (%) | 25% | 0% | Yes | Assumed 3 year payback |  | 58.4191 | 58.4191 | per unit | 51 R: No FS: All clothes dryer (elec+NG) to all clothes dryer (elect+NG) | Total energy use by all electric and natural gas clothes dryers | 11 | 2010 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost assumes 3-year payback based on annual savings of $25.69 | BTO Tool: May be approaching practical limits Appendix B: Table 8-23, page 257, see "improved water extraction" | 1-43 | 11 | 11 | AEO 2014 NEMS
463 | Increase motor efficiency in single-load commercial clothes washers | C: Single-load CW motor | Motor | 5 | 3 | Commercial | Washing & Drying | Clothes washers: Single-Load, Top- and Front-Loading | Coin Laundries, Mulit-Family Common Areas | Energy Savings (%) | 10% | 0% | Yes | Not availalble |  |  |  | per unit | 1 C/R: No FS: All electric to all electric | Total machine energy use by single load coin operated washers | 7.1 | 2010 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf | Appendix B: Table 8-23, page 257, see "increased motor efficiency" | 3-3530 | 7.1 | 7.1 | AEO 2010 NEMS
466 | Add condensing heat exchanger from exhaust air to intake air in commercial single-load dryers | C: CD Condensing single load | System | 5 | 2 | Commercial | Washing & Drying | Standard-Capacity Clothes Dryer | New | Energy Savings (%) | 14% | 0% | Yes | Assumed 5 year payback |  | 747.4437 | 747.4437 | per unit | 52 C: No FS: All clothes dryer (elec+NG) to all clothes dryer (elect+NG) | Total energy use by single load coin operated dryers | 11 | 2015 | Tables 8-32, 8-36, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost assumes 5-year payback based on annual savings of $172.51 | BTO Tool: Heat exchanger from exhaust air to intake air Appendix B: Table 8-36, page 272, see "inlet air preheat, condensing mode" | 3-3529 | 11 | 11 | AEO 2010 NEMS
467 | Add condensing heat exchanger from exhaust air to intake air in standard residential dryers - NOT FEASIBLE TECHNOLOGY | R: Condensing clothes dryer | System | 5 | 2 | Residential | Washing & Drying | Standard-Capacity Clothes Dryer | New | Energy Savings (%) | 14% | 0% | Yes | Assumed 5 year payback |  | 55.367 | 55.367 | per unit | 51 R: No FS: All clothes dryer (elec+NG) to all clothes dryer (elect+NG) | Total energy use by all natural gas clothes dryers | 12 | 2014 | Tables 8-32, 8-36, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost assumes 5-year payback based on annual savings of $14.29 | BTO Tool: Assumed same as commercial Appendix B: Table 8-36, page 272, see "inlet air preheat, condensing mode" | 1-41 | 12 | 12 | AEO 2014 NEMS
468 | Add condensing heat exchanger from exhaust air to intake air in commercial tumble dryers | C: CD Condensing tumble | System | 5 | 2 | Commercial | Washing & Drying | Larger-Capacity Clothes Dryer (20-75 lbs) | New | Energy Savings (%) | 14% | 0% | Yes | Assumed 5 year payback |  | 228.6308 | 228.6308 | per unit | 52 C: No FS: All clothes dryer (elec+NG) to all clothes dryer (elect+NG) | Total energy use by commercial tumble dryers | 11 | 2014 | Table 8-37, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost assumes 5-year payback based on annual savings of $41.73 | BTO Tool: Heat exchanger from exhaust air to intake air Appendix B: Table 8-37, page 273, see "inlet air preheat, condensing mode" | 3-3531 | 11 | 11 | AEO 2010 NEMS
469 | Increase usage of low-temperature detergent in single-load commercial clothes washers | C: Single-load CW: Low-T Detergent | System | 5 | 3 | Commercial | Washing & Drying | Single-Load Clothes Washers | All | Energy Savings (%) | 20% | 0% | Yes | $17.97 buys you 78 loads instead of 96 loads; assume 6 loads/washer/day (Navigant) | 409.9406 | 504.5423 | 94.6017 | per unit | 48 C: No FS: All fuels WH to all fuels WH | Total water heating energy use by single load coin operated washers | 1 | 2010 | Chemical and Engineering News, Vol. 85 #5, Jan. 2007; Other Primary Source: Tables 8-24 and 8-25, Navigant Consulting; "Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances" (2009) Other Supporting Sources: Chemical and Engineering News, Vol. 85 #5, Jan. 2007 | BTO Tool: savings to 20% (i.e., rather than +41.7C from the test procedure (for a 55C wash) you go +28 C (for a 40C wash)) - distribution losses keep energy beneift at 20% rather than 1-28/41.7 Appendix B: Table 8-24 & 8-25 | 3-3523 | 1 | 1 | AEO 2010 NEMS
470 | Increase usage of low-temperature detergent in on-site multi-load commercial clothes washers and tunnel washers | C: Multi-load CW: Low-T Detergent | System | 5 | 4 | Commercial | Washing & Drying | Multi-Load Clothes Washers, Tunnel Washers | On Premises Laundry (Hotels, Hospitals, Universities, Prisons), Off-Site, Industrial | Energy Savings (%) | 20% | 0% | Yes | $17.97 buys you 78 loads instead of 96 loads; 300 million loads at 200 pounds/year in 130k washers vs 20 pound load detergent dose | 4319.7115 | 5316.568 | 996.8565 | per unit | 48 C: No FS: All fuels WH to all fuels WH | Total water heating energy use by tunnel and multi-load washers | 1 | 2010 | Chemical and Engineering News, Vol. 85 #5, Jan. 2007; Other Primary Source: Tables 8-24 and 8-25, Navigant Consulting; "Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances" (2009) Other Supporting Sources: Chemical and Engineering News, Vol. 85 #5, Jan. 2007 | BTO Tool: savings to 20% (i.e., rather than +41.7C from the test procedure (for a 55C wash) you go +28 C (for a 40C wash)) - distribution losses keep energy beneift at 20% rather than 1-28/41.7 Appendix B: Table 8-24 & 8-25 | 3-3533 | 1 | 1 | AEO 2010 NEMS
471 | Increase usage of low-temperature detergent in homes; clothes washing | R: Low Temp Detergent in clothes washers | System | 5 | 3 | Residential | Washing & Drying | Single-Load, Top- and Front-Loading Clothes Washer | All | Energy Savings (%) | 20% | 0% | Yes | $17.97 buys you 78 loads instead of 96 loads; assume 250 loads/year/house | 46.7969 | 57.5962 | 10.7993 | per unit | 47 R: No FS: All fuels WH to all fuels WH | Total water heating energy use by residential clothes washers | 1 | 2012 | Chemical and Engineering News, Vol. 85 #5, Jan. 2007; Other Primary Source: Tables 8-24 and 8-25, Navigant Consulting; "Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances" (2009) Other Supporting Sources: Chemical and Engineering News, Vol. 85 #5, Jan. 2007 | BTO Tool: savings to 20% (i.e., rather than +41.7C from the test procedure (for a 55C wash) you go +28 C (for a 40C wash)) - distribution losses keep energy beneift at 20% rather than 1-28/41.7 Appendix B: Table 8-24 & 8-25 | 1-56 | 1 | 1 | AEO 2014 NEMS
472 | Increase adoption of low-flow sprayers in low-temp under counter dishwashers | C: Low-Flow Sprayers in low temp DW | Sprayer | 5 | 4 | Commercial | Dishwashing | Under counter Low-Temp Dishwasher | Small Restaurants, Bars, Nursing Homes, Churches | Energy Savings (%) | 11% | 0% | Yes | $1000; Payback: 7-10 yrs |  |  | 1000 | per unit | 48 C: No FS: All fuels WH to all fuels WH | Total water heating energy use by undercounter low temperature dishwashers | 10 | 2010 | Tables 4-22 and 4-8, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances | BTO Tool: Savings INCLUDES that from reduced water heating needs; ONLY measure is Low-Flow Sprayers | 3-3539 | 10 | 10 | AEO 2010 NEMS
473 | Increase adoption of low-flow sprayers in high-temp under counter dishwashers | C: Low-Flow Sprayers in high temp DW | Sprayer | 5 | 4 | Commercial | Dishwashing | Under counter High-Temp Dishwasher | Small Restaurants, Bars, Nursing Homes, Churches | Energy Savings (%) | 40% | 0% | Yes | $1000;Payback: 1-2 yrs |  |  | 1000 | per unit | 48 C: No FS: All fuels WH to all fuels WH | Total water heating energy use by undercounter high temperature dishwashers | 10 | 2010 | Tables 4-22 and 4-8, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances | BTO Tool: Savings INCLUDES that from reduced water heating needs; ONLY measure is Low-Flow Sprayers | 3-3540 | 10 | 10 | AEO 2010 NEMS
475 | Demonstrate and deploy residential microwave clothes dryers | R: Microwave CD | System | 5 | 2 | Residential | Washing & Drying | Standard-Capacity Clothes Dryer | All | Energy Savings (%) | 21% | 0% | No | 212 |  |  | 212 | per unit | 51 R: No FS: All clothes dryer (elec+NG) to all clothes dryer (elect+NG) | Total energy use by all electric clothes dryers | 12 | 2017 | Table 8-36, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. (p. 270) http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf | BTO Tool: Assumed same as commercial Appendix B: Table 8-36, page 272, see "microwave" | 1-42 | 12 | 12 | AEO 2014 NEMS
477 | Replace conventional dry cleaning with petroleum in new systems | C: Petroleum Dry Cleaning | System | 5 | 3 | Commercial | Washing & Drying | Petroleum Dry Cleaning Equip | Dry Cleaners | Energy Usage, BTU/100lbs | 9440000 | 22300000 | No | 52500 |  |  | 52500 | per unit | 55 C: No FS: Dry Cleaning Energy Use | Total dry cleaning energy use | 15 | 2010 | Figure 8-33, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: EPA, "Case Study: Liquid Carbon Dioxide (CO2) Surfactant System For Garment Care", http://www.epa.gov/dfe/pubs/garment/lcds/micell.htm | BTO Tool: http://www.epa.gov/dfe/pubs/garment/lcds/micell.htm Appendix B: Figure 8-33, page 281. Energy savings is percent difference between PCI and Petroleum | 3-3528 | 15 | 15 | AEO 2010 NEMS
478 | Demonstrate and Deploy Nylon Bead Clothes Washers in Homes | R: Nylon Bead Clothes Washer | System | 5 | 2 | Residential | Washing & Drying | Nylon Bead Clothes Washer | New | Energy Savings (%) | 83% | 0% | No | Assume 70%/30% capital/energy split | 0 | 532.016 | 532.016 | per unit | 54 R: No FS: Total clothes washing, clothes drying and water heating energy | Total residential clothes washing, drying, and water heating energy consumption | 11 | 2017 | LBNL: Priority Setting Estimates spreadsheet: 83% UEC source energy savings, 61% primary energy savings (use 83%... Makes sense b/c commercial front loader is only 7% washer energy, rest is HW and drying) Primary Source: Desroches, L et al. (2011). MaxTech and Beyond, Maximizing Appliance and Equipment Efficiency by Design, http://efficiency.lbl.gov/drupal.files/ees/MTAB%20Final%20LBNL%20Report.pdf | BTO Tool: Assumes 25% premium over current efficient models Appendix B: Page 19, Table 3 | 1-158 | 11 | 11 | AEO 2014 NEMS
479 | Replace conventional dry cleaning with professional wet cleaning in new systems | C: Professional Wet Cleaning instead of dry | System | 5 | 3 | Commercial | Washing & Drying | Wet Cleaning Machine for Dry cleaning | Dry Cleaners | Energy Usage, BTU/100lbs | 16000000 | 22300000 | No | 1565 |  |  | 1565 | per unit | 55 C: No FS: Dry Cleaning Energy Use | Total dry cleaning energy use | 15 | 2010 | Figure 8-33, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances | BTO Tool: 1565 Cost is MONTHLY equipment cost difference b/t wet and dry cleaning over life of equipment; article also gives difference in monthly maintenance costs; Sinsheimer (2007) JAWMA | 3-3528 | 15 | 15 | AEO 2010 NEMS
480 | Standard Sized Front-Loading Clothes Washer (L7 of 8) of the 05/2012 Rulemaking TSD | R: Front Load Standard-Sized CW (L7 of 8) | System | 5 | 4 | Residential | Washing & Drying | Standard Size Front-Loading Clothes Washer | New | Modified Energy Factor (incl. RMC) | 2.26 | 1.26 | No | Assumed no added cost at scale |  |  |  | per unit | 1 C/R: No FS: All electric to all electric | Total electricity usage, excluding hot water usage, by all residential front-loading washers | 11 | 2013 | Standards rulemaking TSD published in 05/2012, Chapter 7, Table 7.2.1. | Standards rulemaking TSD published in 05/2012: 1) Front loading standard CW (1.6 ft^3 capacity) manufactured after 01/2011 must have modified EF of 1.26; and water factor of 9.5. 2) These CW manufactured on or after 03/2015 must have modified EF of 1.84, and water factor of 4.7. Standard is unchanged starting in 2018. | 1-37 | 11 | 11 | AEO 2014 NEMS
481 | Standard-Sized Top-Loading Clothes Washer | R: Top Load Standard-sized CW (L8 of 8) | System | 5 | 4 | Residential | Washing & Drying | Standard Size Top-Loading Clothes Washer | New | Modified Energy Factor (incl. RMC) | 2.04 | 1.29 | No | Assumed no added cost at scale |  |  |  | per unit | 1 C/R: No FS: All electric to all electric | Total electric energy use [excludes hot water] by all residential top-loading washers | 11 | 2013 | Standards rulemaking TSD published in 05/2012 | Standards rulemaking TSD published in 05/2012: 1) Top loading standard CW (1.6 ft^3 capacity) manufactured after 01/2011 must have modified EF of 1.26; and water factor of 9.5 These CW manufactured on or after 03/2015 must have modified EF of 1.29, and water factor of 8.4. 3) Standard starting 01/2018 increases to EF of 1.57 and water factor of 6.5. | 1-38 | 11 | 11 | AEO 2014 NEMS
482 | Deploy and Increase deployment of more efficient compact size front-loading clothes washers. The new efficiency level of 1.7 was proposed in Energy Efficiency and Smart Appliance Agreement of 2010. From the 05/2012 Rulemaking (TSD), all clothes washers manufacturered on or after March 2015 should have modified EF of 1.13 (L1 of 1). No other higher level EF was identified. | R: Efficient Compact Size Front-Loading CW | System | 3 | 5 | Residential | Washing & Drying | Compact Size Front-Loading Clothes Washer | New | Modified Energy Factor (incl. RMC) | 1.7 | 1.13 | No | Assumed no added cost at scale |  |  |  | per unit | 1 C/R: No FS: All electric to all electric | Total electricity usage, excluding hot water usage, by all residential front-loading, compact washers | 11 | 2010 | Energy Efficiency and Smart Appliance Agreement of 2010, AHAM power point | Standards rulemaking TSD published in 05/2012: 1) Front loading compact CW manufactured after 2007 must have modified EF of 0.65. 2) These CW manufactured on or after 03/2015 must have modified EF of 0.86, and water factor of 14.4. 3) Standard starting 01/2018 increases to EF of 1.15 and water factor of 12. | 1-192 | 11 | 11 | AEO 2014 NEMS
483 | Compact Size Top-Loading Clothes Washer standard effective in 2012, must be in compliance in 2018. | R: Compact Size Top-Loading CW Standard (2018) | System | 3 | 5 | Residential | Washing & Drying | Compact Size Top-Loading Clothes Washer | New | Modified Energy Factor (incl. RMC) | 1.15 | 0.65 | No | Assumed no added cost at scale |  |  |  | per unit | 1 C/R: No FS: All electric to all electric | Total electric energy use [excludes hot water] by all residential top-loading, compact washers | 11 | 2018 | Standards rulemaking TSD published in 05/2012 | Standards rulemaking TSD published in 05/2012: 1) Top loading compact CW manufactured after 2007 must have modified EF of 0.65. 2) These CW manufactured on or after 03/2015 must have modified EF of 1.13, and water factor of 8.3. 3) Standard starting 01/2018 increases to EF of 1.15 and water factor of 12. | 1-193 | 11 | 11 | AEO 2014 NEMS
484 | Standard-sized Vented Electric Clothes Dryers standard has a compliance date of 01/2015, effective in 08/2011. | R: Vented Electric CD Standard (2015) | System | 5 | 5 | Residential | Washing & Drying | Standard Vented Electric Clothes Dryer | New | Energy Factor | 3.73 | 3.01 | No | Assumed no added cost at scale |  |  |  | per unit | 1 C/R: No FS: All electric to all electric | Total energy use by all electric clothes dryers | 12 | 2015 | Standards rulemaking, effective in 08/2011 with compliance in 01/2015. http://www1.eere.energy.gov/buildings/appliance_standards/product.aspx/productid/36 | Vented standard-sized electric clothes dryers make up 98.5% of the total electric clothes dryer market. Clothes Dryer Product Class Market Shares: Table 9.3.1 from TSD 2011: Vented Electric Standard: 77.7%; vented electric compact 120V: 0.2%; vented electric compact 240V: 0.8%; Vented gas: 20.9%; ventless electric compact (240V): 0.5%; ventless combination washer/dryer: 0.5%. | 1-42 | 12 | 12 | AEO 2014 NEMS
485 | Compact Vented Electric 120V Clothes Dryer Standard effective in 08/2011 with compliance date of 01/2015. | R: Compact Vented Electric 120V CD Standard (2015) | System | 3 | 5 | Residential | Washing & Drying | Compact Vented Electric, 120V Clothes Dryer | New | Energy Factor | 3.61 | 3.13 | No | Assumed no added cost at scale |  |  |  | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by vented electric compact (120V) clothes dryers | 12 | 2015 | Standards rulemaking, effective in 08/2011 with compliance in 01/2015. http://www1.eere.energy.gov/buildings/appliance_standards/product.aspx/productid/36 | Clothes Dryer Product Class Market Shares: Table 9.3.1 from TSD 2011: Vented Electric Standard: 77.7%; vented electric compact 120V: 0.2%; vented electric compact 240V: 0.8%; Vented gas: 20.9%; ventless electric compact (240V): 0.5%; ventless combination washer/dryer: 0.5%. | 1-188 | 12 | 12 | AEO 2014 NEMS
486 | Compact Vented Electric 240V Clothes Dryer Standard effective in 08/2011 with compliance date of 01/2015. | R: Compact Vented Electric 240V CD Standard (2015) | System | 3 | 5 | Residential | Washing & Drying | Compact Vented Electric, 240V Clothes Dryer | New | Energy Factor | 3.27 | 2.9 | No | Assumed no added cost at scale |  |  |  | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by vented electric compact (240V) clothes dryers | 12 | 2015 | Standards rulemaking, effective in 08/2011 with compliance in 01/2015. http://www1.eere.energy.gov/buildings/appliance_standards/product.aspx/productid/36 | Clothes Dryer Product Class Market Shares: Table 9.3.1 from TSD 2011: Vented Electric Standard: 77.7%; vented electric compact 120V: 0.2%; vented electric compact 240V: 0.8%; Vented gas: 20.9%; ventless electric compact (240V): 0.5%; ventless combination washer/dryer: 0.5%. | 1-189 | 12 | 12 | AEO 2014 NEMS
487 | Standard-sized Vented Gas Clothes Dryer effective in 08/2011 with compliance date of 01/2015. | R: Vented Gas Dryer Standard (2015) | System | 5 | 5 | Residential | Washing & Drying | Vented Gas Clothes Dryer | New | Energy Factor | 3.3 | 2.67 | No | Assumed no added cost at scale |  |  |  | per unit | 2 C/R: No FS: All gas to all gas | Total energy use by all natural gas clothes dryers | 12 | 2015 | Standards rulemaking, effective in 08/2011 with compliance in 01/2015. http://www1.eere.energy.gov/buildings/appliance_standards/product.aspx/productid/36 | Clothes Dryer Product Class Market Shares: Table 9.3.1 from TSD 2011: Vented Electric Standard: 77.7%; vented electric compact 120V: 0.2%; vented electric compact 240V: 0.8%; Vented gas: 20.9%; ventless electric compact (240V): 0.5%; ventless combination washer/dryer: 0.5%. | 1-41 | 12 | 12 | AEO 2014 NEMS
488 | Compact Ventless Electric 240V Clothes Dryer Max Tech (TSD 2011) | R: Max Tech Compact Ventless Electric 240V CD | System | 3 | 5 | Residential | Washing & Drying | Compact Ventless Electric, 240V Clothes Dryer | New | Energy Factor | 4.03 | 2.55 | No | Assumed no added cost at scale |  |  |  | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by ventless electric (240V) clothes dryers | 12 | 2010 | TSD 2011 | Clothes Dryer Product Class Market Shares: Table 9.3.1 from TSD 2011: Vented Electric Standard: 77.7%; vented electric compact 120V: 0.2%; vented electric compact 240V: 0.8%; Vented gas: 20.9%; ventless electric compact (240V): 0.5%; ventless combination washer/dryer: 0.5%. | 1-190 | 12 | 12 | AEO 2014 NEMS
489 | Ventless Electric Combination Washer-Dryer Max Tech (TSD 2011) | R: Max Tech Ventless Electric Combination W/D | System | 3 | 5 | Residential | Washing & Drying | Compact Ventless Electric, Combined W/D Clothes Dryer | New | Energy Factor | 3.69 | 2.08 | No | Assumed no added cost at scale |  |  |  | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by ventless combination washer/dryer | 12 | 2010 | TSD 2011 | Clothes Dryer Product Class Market Shares: Table 9.3.1 from TSD 2011: Vented Electric Standard: 77.7%; vented electric compact 120V: 0.2%; vented electric compact 240V: 0.8%; Vented gas: 20.9%; ventless electric compact (240V): 0.5%; ventless combination washer/dryer: 0.5%. | 1-191 | 12 | 12 | AEO 2014 NEMS
493 | Increase deployment of soil sensors in new residential dishwashers | R: DW Soil Sensors | Use Intensity | 5 | 3 | Residential | Dishwashing | Dishwashing | All | Energy Savings (%) | 25% | 0% | Yes | 30 |  |  | 30 | per unit | 1 C/R: No FS: All electric to all electric | Total dishwashing energy use, not including water heating consumption | 19 | 2012 | ACEEE, "Dishwashing", http://www.aceee.org/consumer/dishwashing | BTO Tool: Soil sensor replacement cost for Sears model | 1-173 | 19 | 19 | AEO 2014 NEMS
495 | Deploy commercial top-loading clothes washers with spray rinse technology (instead of filling tank for rinse cycle) | C: Top-loading CW Spray Rinse | Sprayer | 5 | 2 | Commercial | Washing & Drying | Single-Load, Top-Loading Clothes Washer | Coin Laundries, Mulit-Family Common Areas | Energy Savings (%) | 50% | 0% | No | Assumed 5 year payback |  | 201.716 | 201.716 | per unit | 48 C: No FS: All fuels WH to all fuels WH | Total water heating energy use by single load coin operated washers | 7.1 | 2014 | Table 8-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Cost assumes 5-year payback based on annual savings of $34.81 | BTO Tool: Earlier versions pulled from market Appendix B: Table 8-23, page 257, see "spray rinse technology" | 3-3523 | 7.1 | 7.1 | AEO 2010 NEMS
496 | Demonstrate and Deploy Nylon Bead Clothes Washers in Off-Site Commercial Laundries | C: Nylon Bead CW | System | 5 | 3 | Commercial | Washing & Drying | Nylon Bead Clothes Washer | Commercial Laundries | Energy Savings (%) | 94.13% | 0% | No | $2.55 value created per load; $15k dryer savings; std cost is wgt avg of $824 (top load,80%) and $1355 (front, 20%) but estimated first cost of nylon by 125% of 1355 (front) | 40000 | 34000 | -6000 | per unit | 48 C: No FS: All fuels WH to all fuels WH | Total energy use by all commercial washers and dryers, except tunnel and multi-family washers and dryers | 15 | 2013 | LBNL: Priority Setting Estimates spreadsheet; Misra et.al. presentation showing cost analysis; Xeros website Primary Source: Misra, A., Pimphalkhute, H., Murthi, S. & Kamdar, T. Pricing strategy: Waterless Washing Machine (2010) Xeros website, Desroches, L.-B. et al. Max Tech and Beyond (2011) | BTO Tool: Have only included first costs--$2.55 additional value created per load; 30% machine energy and 90% hot water reduction; 100% drying reduction Appendix B: "Savings are estimated to be approximately 15%, associated with machine energy (shorter cycle times). The small amount of cold water used per cycle results in 100% savings in water heating energy, and 100% savings in clothes dryer energy" Used Weighted average of savings for full cycle | 3-3547 | 15 | 15 | AEO 2010 NEMS
497 | Offer incentives or awareness campaign to move multi-load washing to offsite tunnel washers | C: Multi-Load to Tunnel Washers | System | 5 | 4 | Commercial | Washing & Drying | Multi-Load Clothes Washers | On Premises Laundry (Hotels, Hospitals, Universities, Prisons) | Energy Savings (%) | 82% | 0% | No | Reported annual savings of $1M; unclear what is included | 190000 | 68750 | -121250 | per unit | 48 C: No FS: All fuels WH to all fuels WH | Total water heating energy use by multi-load washers | 15 | 2010 | Tables 8-24 and 8-25, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances; NY times article on Hilton case study/business model Primary Source: Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. Navigant Consulting (2011) Garbarine, R. Commercial Property / New Jersey ; In Piscataway , a Central Laundry for Region Hiltons. New York Times 5 (1999) | BTO Tool: Represents dramatic business model change; very hard to quantify cost and full cycle energy savings Appendix B: Savings from Goetzler: Tables 8-24, 8-25 Cost from New York Times payback calculation 82% savings, $120,000 savings per establishment | 3-3526 | 15 | 15 | AEO 2010 NEMS
499 | Retrofit multi-load and tunnel washers to reuse wash water and reduce need for hot water | C: Multi-/Tunnel CW: Waste-H2O Recycling | System | 5 | 4 | Commercial | Washing & Drying | Multi-Load and Tunnel Clothes Washers | On Premises Laundry (Hotels, Hospitals, Universities, Prisons); off-site and industrial | Energy Savings (%) | 53% | 0% | Yes | Case study of 1 site with 4 units: $91k installed, $145k water & sewer savings |  | 22758.75 | 22758.75 | per unit; 20 GPM over 4 machines | 48 C: No FS: All fuels WH to all fuels WH | Total water heating energy use by tunnel and multi-load washers | 15 | 2010 | Tables 8-24 and 8-25, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances; Lake Arrowhead resort Case Study Primary Source: Savings: Navigant Consulting; "Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances" (2009) Cost: RMC Water nd Environment; Integrated Water Resources Program Report, Appendix H (12/2007) | BTO Tool: Note: used "Eco" system as marginal cost for premium is not cost effective at $12/MMBTU; See additional data tab Appendix B: Table 8-24 & 8-25 | 3-3533 | 15 | 15 | AEO 2010 NEMS
502 | Decrease cost and deploy thermosiphon (indirect, passive) solar water heaters (electric to electric back-up) | R: Solar WH, Elec. - Ind. Passive | System | 5 | 2 | Residential | Water Heating | Solar WH: indirect, passive | All | Energy Savings (%) | 44.94% | 0 | Yes | $ 2,030 (assumed incremental to backup; all roadmap measures except "marketing") |  |  | 2030 | per home; 48.3 sq. ft absorber | 1 C/R: No FS: All electric to all electric | Total electric water heating energy consumption | 13 | 2017 | SWH roadmap; Cold Climate Solar Domestic Water Heating Systems: Cost/Benefit Analysis and Opportunities for Improvements (Burch et. Al.) Primary Source: Itron, Inc.; "California Center for Sustainable Energy Solar Water Heating Pilot Program" (3/2011) Federal Energy Management Program, "Solar Water Heating with Low-Cost Plastic Systems" (1/2012) Other Supporting Sources: Hudon, Burch "Solar Water Heating Roadmap" (in preperation) | BTO Tool: Includes 3% penalty for thermosiphon over active; 3.5% for freeze-proofing Appendix B: Thorough analysis of multiple sources; represents aggregate savings net of parasitic loads Costs represent program targets informed by roadmap (in preperation) | 1-53 | 13 | 13 | AEO 2014 NEMS
505 | Increase deployment of low flow fixtures in existing and new homes | R: Low-flow Faucets | Use Intensity | 5 | 4 | Residential | Water Heating | Fixtures | Retrofits | Energy Savings (%) | 52% | 0% | Yes | $ 8 - 50, $4/1000 gal water savings | 0 |  | -409.1496 | per unit | 47 R: No FS: All fuels WH to all fuels WH | Total residential energy use in high flow water heating for showers and faucets | 15 | 2010 | http://eartheasy.com/live_lowflow_aerators.htm, cost from 2005 FEMP study of water conservation (http://www.pnl.gov/main/publications/external/technical_reports/PNNL-15320.pdf), total water use from Aquacraft study; East Bay Muni. Water District report Primary Source: Water Resources Engineering, I. Water Conservation Market Penetration Study. East Bay Municipal Utility District (2002) Other Supporting Sources: McMordie-Stoughton, K.L., Elliott, D., Parker, G., Solana, A. & Sullivan, G. Update of Market Assessment for Capturing Water Conservation Opportunities in the Federal Sector. Pacific North West National Laboratory (2005). | This tech was not included in teh UBER/active cascade b/c it was deemed as an ainappropriate role for the government to pursue. BTO Tool: Cost info: http://eartheasy.com/live_lowflow_aerators.htm: faucet aerators 8-10; showerheads 8-50; 2 showers, 3 faucets per home. Costs also include water/sewer cost savings (6% discount factor, 15 year life, $4.47/1000 gal) Appendix B: Tables 4-7 and 4-9 represents installed faucet aerator base (used to scale nationally); fixture cost ($90 for 5 per home)provided by web search (3/2012) net of water savings valued at $8/1000 gallons Results in $409 cost savings per home, 71% reduction moving to 2 gpm faucets. | 1-57 | 15 | 15 | AEO 2014 NEMS
506 | Demonstrate and Deploy Zeolithic Dishwashers to Reduce Energy for Drying | R: Zeolithic DW | System | 5 | 2 | Residential | Dishwashing | Dishwasher | New | kWh/cycle | 0.83 | 1.37 | No | 13 yr payback @ 200 cylces/year and $0.15/kWh |  |  | 486 | per unit | 1 C/R: No FS: All electric to all electric | Total dishwashing energy use, not including water heating consumption | 19 | 2018 | LBNL Priority Setting Estimates spreadsheet; http://www.siemens.com/innovation/en/publications/publications_pof/pof_spring_2010/zeolith.htm Primary Source: Siemens product description (available in the UK) | Appendix B: Siemens: 0.83 kWh/cycle AHAM blog: in 1991 the average dishwasher consumed 2.67 kilowatts (kWh) per cycle and by 2010 it was only 1.37 kWh/ cycle | 1-173 | 19 | 19 | AEO 2014 NEMS
507 | Demonstrate and deploy heat pump water heating in commercial kitchens for water heating and space cooling | C: Kitchen: HPWH | System | 5 | 3 | Commercial | Water Heating | Commercial Kitchen | Food Service Establishments | COP | 44.57% | 0% | No | $2000-$2500 per ton cooling ($5000; payback ~3.8 yrs) | 1500 | 5000 | 3500 | per unit | 61 Manual | Total electric cooling and electric, NG, and distillate water heating in all food service buildings | 13 | 2013 | WSU fact sheet (2003), http://www.energy.wsu.edu/documents/engineering/comm_water_htrs.pdf Primary Source: Washington State University (2005), "Energy Efficiency Fact Sheet: Commercial Water Heaters" Other Supporting Sources: Estimated new unit cost is $5,000, $3,500 more than a traditional water heater | BTO Tool: Approx. 50% savings in WH; assume 30% reduction in cooling needed; Cost from WSU example calc | 4-3501 | 13 | 13 | AEO 2010 NEMS
508 | Improve insulation in new oil water heaters | R: Improved oil WH insulation | Heat loss (non-envelope) | 5 | 4 | Residential | Water Heating | Tank Oil WH | New | Energy Factor | 0.62 | 0.53 | Yes | 1347 | 795 | 848 | 53 | per unit | 49 R: No FS: LPG and distillate WH | Total residential water heating by LPG and distillate fuel oil | 13 | 2010 | DOE TSD (2010) Ch5, Table 5.13.2, http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr.html Primary Source: U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy (EERE). (2011, March 30). Residential Heating Products Final Rule Analytical Tools. Retrieved from Appliance & Equipment Standards: http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html | BTO Tool: 2.5 inches foam insulation Appendix B: Cost and energy savings from DOE 2011, Level 0 to Level 5. EF improved from 0.53 to 0.62 (15% savings). | 1-63 | 13 | 13 | AEO 2014 NEMS
509 | Replace standard gas storage water heaters with condensing gas storage water heaters | R: Condensing Gas WH | Thermal transfer | 5 | 4 | Residential | Water Heating | Waterh heater, gas | New | Energy Factor | 0.77 | 0.59 | No | See existing & efficient costs | 1079 | 1893 | 814 | per unit | 2 C/R: No FS: All gas to all gas | Total residential storage natural gas water heaters | 13 | 2010 | EPA ENERGY STAR, http://www.energystar.gov/index.cfm?c=water_heat.pr_crit_water_heaters Primary Source: Water Resources Engineering, I. Water Conservation Market Penetration Study. East Bay Municipal Utility District (2002) | BTO Tool: Cost for 50 gal from ENERGY STAR table 2; standard Tank Gas installed cost of $865 Appendix B: Tables 4-7 and 4-9 represents installed faucet aerator base; used to scale nationally; fixture cost ($90 for 5 per home)provided by web search and is net of water savings valued at $8/1000 gallons | 1-58 | 13 | 13 | AEO 2014 NEMS
510 | Replace commercial gas storage water heaters with condensing gas storage water heaters | C: Condensing Gas WH | Thermal transfer | 5 | 4 | Commercial | Water Heating | Waterh heater, gas | New | Energy Savings (%) | 21.5% | 0% | No | $5,430 for a typical gas unit with 200 kBtu/h capacity and thermal efficiency of 80%, assuming can be replaced with 3 tankless instantaneous gas WHs at 180-250 kBTU/hr capacity and a cost of $1875/each. | 5430 | 6630 | 1200 | per unit | 2 C/R: No FS: All gas to all gas | Total energy consumption by all commercial gas storage water heaters | 13 | 2010 | 1) Tables 6-11, 6-21, and 6-23, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf 2) Costs from distributors, CEC, and Navigant. September 2013. 2) Typical unit costs obtained from NCI data. Assumes 3 tankless WH with typical capacity of 180-250 kBtu/hr would be necessary to replace one typical storage unit with 200 kBtu/hr capacity. |  | 3-3561 | 13 | 13 | AEO 2010 NEMS
511 | Deploy and standardize max tech tankless instantaneous gas water heaters to replace commercial storage water heaters in buildings with small hot water demands | C: Max Tech Tankless Gas WH for small loads | System | 2+ | 3 | Commercial | Water Heating | Tankless Gas WH | Commercial Buildings with small WH requirements | Energy Savings (%) | 15% | 0% | No | $5,430 for a typical gas unit with 200 kBtu/h capacity and thermal efficiency of 80%, assuming can be replaced with 3 tankless instantaneous gas WHs at 180-250 kBTU/hr capacity and a cost of $1875/each. | 5430 | 5625 | 195 | per unit | 2 C/R: No FS: All gas to all gas | All commercial gas small water heaters | 13 | 2013 | Tables 6-8, 6-11, 6-21, and 6-23, Navigant Consulting. (2009). Energy Savings 1) Tables 6-8, 6-11, and 6-21, Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf 2) Typical unit costs obtained from NCI data. Assumes 3 tankless WH with typical capacity of 180-250 kBtu/hr would be necessary to replace one typical storage unit with 200 kBtu/hr capacity. | Unknown gas access and cost for gas plumbing imply this is an aggressive estimate. | 4-3503 | 13 | 13 | AEO 2010 NEMS
512 | Deploy and standardize max tech gas tankless water heaters (Level 8) to replace residential storage water heaters | R: Tankless Gas WH, level 8 (No FS) | System | 2+ | 4 | Residential | Water Heating | Tankless Gas WH | All | Energy Factor | 0.95 | 0.59 | No | 3083 | 1079 | 3083 | 2004 | per unit; 199,000 BTU/hr tankless | 2 C/R: No FS: All gas to all gas | Total residential storage natural gas water heaters | 13 | 2012 | Rheem website, http://www.rheem.com/product.aspx?id=5AE02BB6-A8A9-49DE-8F3A-08DA596EB980, prices based on large WH in residential TSD | BTO Tool: Unknown gas access and cost for gas plumbing imply this is an aggressive estimate; input: 199,000 BTU/hr tankless; "large" storage (>55 gal) per TSD | 1-58 | 13 | 19 | AEO 2014 NEMS
513 | Encourage adoption of system that captures waste heat from space cooling (desuperheater) for water heating | C: AC waste heat recovery (for WH) - desuperheater | System | 5 | 3 | Commercial | Water Heating | Water heater, all | Hottest 2 climates | Energy Savings (%) | 10% | 0% | Yes | $3320, WTP (5-yr payback) | 0 | 600 | 600 | per unit | 48 C: No FS: All fuels WH to all fuels WH | Total commercial water heating in the hottest two climates | 13 | 2013 | Savings from NCI Commercial Appliances 2009 report. P. 207, Table 6-19. Cost: See 1. http://www.cdhenergy.com/presentations/ASHRAE%20Chicago%201999%20Desuperheater%20Impact.pdf; 2. http://stampededrive.net/PDF/BuilderGuide3E.pdf; 3. http://www.bpa.gov/energy/n/reports/evaluation/commercial/pdf/BPA-Evaluation_Reverse-Cycle-Chillers_09-30-09.pdf | Appendix B: Energy savings and cost estimates from Navigant Tables 6-11 and 6-19, respectively. | 3-3570 | 13 | 13 | AEO 2010 NEMS
516 | Decrease cost and deploy thermosiphon (indirect, passive) solar water heaters (gas to gas back-up) | R: Solar WH, Gas - Ind. Passive | System | 5 | 2 | Residential | Water Heating | Solar WH: indirect, passive | All | Energy Savings (%) | 44.26% | 0 | Yes | $ 2,030 (assumed incremental to backup; all roadmap measures except "marketing") |  |  | 2030 | per home; 48.3 sq. ft absorber | 2 C/R: No FS: All gas to all gas | Total gas water heating energy consumption | 13 | 2017 | SWH roadmap; California Center for Sustainable Energy Solar Water Heating Pilot Program 3/2011; Cold Climate Solar Domestic Water Heating Systems: Cost/Benefit Analysis and Opportunities for Improvements (Burch et. Al.) Primary Source: Itron, Inc.; "California Center for Sustainable Energy Solar Water Heating Pilot Program" (3/2011) Federal Energy Management Program, "Solar Water Heating with Low-Cost Plastic Systems" (1/2012) Other Supporting Sources: Hudon, Burch "Solar Water Heating Roadmap" (in preperation) | BTO Tool: Includes 3% penalty for thermosiphon over active; 3.5% for freeze-proofing Appendix B: Thorough analysis of multiple sources; represents aggregate savings net of parasitic loads Costs represent program targets informed by roadmap (in preperation) | 1-61 | 13 | 13 | AEO 2014 NEMS
520 | Accelerate retirement of home water heaters from 16 to 12 years | R: Early Retirement of Inefficient WH Units | Use Intensity | 2+ | 4 | Residential | Water Heating | Water heater, all | Existing | Energy Factor | 0.17 | 0 | Yes | 890 | 678.9767 | 890 | 211.0233 | per unit | 47 R: No FS: All fuels WH to all fuels WH | All types of residential water heaters older than 10 years | 13 | 2010 | Average of 517-519 | BTO Tool: Accelerating retirement 4 years; cost is difference in NPV of purchase price, savings is averaged over shortened lifetime | 1-59 | 13 | 13 | AEO 2014 NEMS
521 | Increase usage of low-temperature detergent in residential dishwashers | R: DW Low Temperature Detergent | System | 5 | 3 | Residential | Dishwashing | Dishwasher | Existing | Energy Savings (%) | 20% | 0% | Yes | $17.97 buys you 78 loads instead of 96 loads; assume 250 loads/year/house | 46.7969 | 57.5962 | 10.7993 | per unit | 47 R: No FS: All fuels WH to all fuels WH | Total residential water heating for dishwashing energy consumption | 19 | 2010 | Chemical and Engineering News, Vol. 85 #5, Jan. 2007; Other Primary Source: Tables 8-24 and 8-25 Navigant Consulting; "Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances" (2009) Other Supporting Sources: Chemical and Engineering News, Vol. 85 #5, Jan. 2007 | Appendix B: Table 8-24 & 8-25 | 1-60 | 19 | 19 | AEO 2014 NEMS
524 | Deploy heat pump water heaters to replace all electric water heaters in commercial buildings (no fuel switching) | C: HPWH (COP 4) | System | 5 | 3 | Commercial | Water Heating | Heat Pump | New | Energy Savings (%) | 68% | 0% | No | 10411 |  |  | 10411 | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by all commercial electric storage water heaters | 13 | 2013 | 1) Energy savings from first principles and pg. 194 Tables 6-11, 6-21, and 6-24 in Goetzler, W., Zogg, R., Ahlfeldt, J., Hiraiwa, H., Sathe & Sutherland. Energy Savings Potential and RD & D Opportunities for Commercial Building Appliances. December 21, 2009. 2) Installed cost estimates obtained for a typical unit with input capacity of 54kW and storage of 120 gal for a standard electric resistance WH, and equivalent HPWH of input capacity of 10-16kW. Source: AO Smith quote. *Heat pump water heaters are not sold with a tank; however, HPWH can be added to an existing WH system and can use an existing tank. The cost of the tank is not included in the incremental cost calculation. |  | 3-3562 | 13 | 13 | AEO 2010 NEMS
525 | Demonstrate and deploy advanced CO2 heat pump water heaters with COP of 5.1 (no fuel switching). EcoCute. | R: Adv. HPWH (COP 5.1, EF 3.6) | System | 5 | 3 | Residential | Water Heating | Water heater, electric | New | Energy Factor (converted from 5.1 COP) | 3.5581 | 0.92 | Yes | Assume a 50% cost compression for large scale manufacturing. Unit cost is 814,643 yen in 2011. | 615 | 5400 | 4785 | per unit | 1 C/R: No FS: All electric to all electric | Total electric water heating energy consumption | 13 | 2013 | 1) Baseline unit cost: Total installed cost is $566 ($2008) (2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses) Cost adjusted from $2008 to $2014 (http://data.bls.gov/cgi-bin/cpicalc.pl) 2) Efficient unit cost: '-This is a target cost for US manufacturers, assuming a 50% cost compression for large scale manufacturing. Unit cost is 814,643 yen in October 2011 (Source: http://www.r744.com/articles/150420111031.php). Yen to US dollar conversion rate from October 2011 is 1 USD = 78.3331 JPY (Source: http://www.exchangerates.org.uk/USD-JPY-31_10_2011-exchange-rate-history.html). Cost adjusted from $2011 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl) 3) Efficiency target: This is a target for EF for US HPWH manufacturers. Panasonic released CO2 HPWH with COP of 5.1 (Source: r744.com, "Eco Cute Update: new line-up with 5.1 COP by Panasonic, upgrades by Hitachi and domestic statistics in Japan" (2011)) 5.1 COP converted to 3.56 EF, using a 0.697 conversion factor which accounts for differences between lab rating and typical field performance (Source: Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007)) 4) Base performance: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment -EIA AEO 2014 Early Release, http://www.eia.gov/forecasts/aeo/er/index.cfm -r744.com, "Eco Cute Update: new line-up with 5.1 COP by Panasonic, upgrades by Hitachi and domestic statistics in Japan" (2011) -Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007) -2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses -http://data.bls.gov/cgi-bin/cpicalc.pl - http://www.exchangerates.org.uk/USD-JPY-31_10_2011-exchange-rate-history.html | http://www.climaticoanalysis.org/post/eco-cute-vs-ene-farm-electricity-or-gas-battle-over-next-generation-environmentally-friendly-water-heaters/; popular Japanese product; referenced to baseline for electric water heater market, 2010 (backed off 5.1 COP as per Bouza to convert to US EF 3.56 measure) The current retail price of this Eco Cute is 814,653 Yen (~€7,940.12). | 1-53 | 13 | 13 | AEO 2014 NEMS
526 | Deploy highest efficiency heat pump water heaters in homes (no fuel switching) | R: HPWH (EF 2.4) | System | 5 | 4 | Residential | Water Heating | Water heater, electric | New | Energy Factor | 2.4 | 0.92 | Yes |  | 615 | 1299 | 684 | per unit | 1 C/R: No FS: All electric to all electric | Total electric water heating energy consumption | 13 | 2010 | 1) Baseline unit cost: Total installed cost is $566 ($2008) (2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses) Cost adjusted from $2008 to $2014 (http://data.bls.gov/cgi-bin/cpicalc.pl) 2) Efficent unit cost: GE listed MRSP, http://products.geappliances.com/ApplProducts/Dispatcher?REQUEST=SpecPage&Sku=GEH50DEEDSR -2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment -EIA AEO 2014 Early Release, http://www.eia.gov/forecasts/aeo/er/index.cfm -2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 5 - Engineering Analysis -http://products.geappliances.com/ApplProducts/Dispatcher?REQUEST=SpecPage&Sku=GEH50DEEDSR DOE TSD (2010), Table 5.7.4, 5.13.4 (MSP); Tables 6-11 and 6-24, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances; EPA ENERGY STAR doc Primary Source: Fitzpatrick, S, Murray, M; "GE Heat Pump Water Heater Report", Advanced Energy (2011) Other Supporting Sources: Navigant Consulting Research and Development Roadmap for Water Heating. Department of Energy (2011). |  | 1-53 | 13 | 13 | AEO 2014 NEMS
527 | Replace gas water heaters with tankless gas water heaters with improved heat exchangers and condensate mgmt (Level 5) | R: Tankless With Improved Heat Exchanger Area | Heat Exchanger | 3 | 3 | Residential | Water Heating | Tankless Gas WH | New | Energy Factor | 0.84 | 0.59 | Yes | 2935 | 1021.72 | 2935 | 1913.28 | per unit | 2 C/R: No FS: All gas to all gas | Total gas water heating energy consumption | 13 | 2010 | DOE TSD (2010), http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr.html | BTO Tool: Unknown gas access and cost for gas plumbing imply this is an aggressive estimate; Baseline efficiency and cost is weighted average of standard gas storage (98%) and tankless water heaters (2%) | 1-61 | 13 | 13 | AEO 2014 NEMS
528 | Increase insulation standard in residential tank H2O heaters: gas | R: Gas storage WH - more insulation | Heat loss (non-envelope) | 5 | 5 | Residential | Water Heating | Tank Gas WH | New | Energy Factor | 0.63 | 0.59 | Yes | See existing & efficient costs | 1079 | 1244 | 165 | per unit | 2 C/R: No FS: All gas to all gas | Total residential storage natural gas water heaters | 13 | 2010 | DOE TSD (2010), http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr.html | BTO Tool: COGS = MPC, Market = Retail Price (no installation) from LCC spreadsheet | 1-58 | 13 | 13 | AEO 2014 NEMS
529 | Increase insulation standard in residential tank H2O heaters: electric | R: Elec. storage WH - more insulation | Heat loss (non-envelope) | 5 | 5 | Residential | Water Heating | Tank Electric | New | Energy Factor | 0.95 | 0.9 | Yes | 408 |  |  | 408 | per unit | 1 C/R: No FS: All electric to all electric | Total electric water heating energy consumption | 13 | 2010 | DOE TSD (2010), http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr.html | BTO Tool: Increase foam insulation from 1.5 inches to 4 inches | 1-53 | 13 | 13 | AEO 2014 NEMS
530 | Increase insulation standard in residential tank H2O heaters: oil | R: Oil storage WH - more insulation | Heat loss (non-envelope) | 5 | 5 | Residential | Water Heating | Tank Oil WH | New | Energy Factor | 0.58 | 0.53 | Yes | 1333 |  |  | 1333 | per unit | 49 R: No FS: LPG and distillate WH | Total residential water heating by LPG and distillate fuel oil | 13 | 2010 | DOE TSD (2010), http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr.html | BTO Tool: Increase fiberglass insulation from 1 inch to 2.5 inches | 1-63 | 13 | 13 | AEO 2014 NEMS
531 | Increase deployment of insulating blankets on residential water heaters | R: WH Insulation Blankets | Maintenance | 5 | 4 | Residential | Water Heating | Water heater, all | Existing | Energy Savings (%) | 50% | 0% | Yes | 20 |  |  | 20 | per unit | 47 R: No FS: All fuels WH to all fuels WH | Total residential storage water heater (with no blanket installed) energy consumption | 13 | 2010 | EERE Water Heater Final Rule Analytical Spreadsheet (consistent with the TSD) (http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html) Primary Source: U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy (EERE). (2011, March 30). Residential Heating Products Final Rule Analytical Tools. Retrieved from Appliance & Equipment Standards: http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html | BTO Tool: Using the TSD baseline UA of 2.6 Btu/hr/F for electric water heaters and the RECS household energy use, the % standby losses are 17%. This includes thermosyphoning, which might be 30% of the total standby loss (5% of total). For gas tanks, similar calculations suggest 22% standby losses, including flue losses. Assuming 50% reduction in tank losses (12% of total energy use), I recommend using 6% savings. Appendix B: Cost from DOE 2011. Insulating blankets designed to reduce tank losses by roughly 50%. | 1-64 | 13 | 13 | AEO 2014 NEMS
532 | Increase deployment of insulating blankets on commercial WH | C: WH insulation blankets | Maintenance | 5 | 4 | Commercial | Water Heating | Water heater, all | Retrofits | Energy Savings (%) | 40% | 0% | Yes | $20; $220 WTP (5-yr payback) |  |  | 20 | per unit | 48 C: No FS: All fuels WH to all fuels WH | Total commercial water heater standby energy losses | 13 | 2010 | Tables 6-11 and 6-18, Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Standby losses estimated based on Federal Standard (329 Btu/hr), combined with CBECS water heater energy assuming one water heater per building on average (3%). Primary Source: Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy. http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy (EERE). (2011, March 30). Residential Heating Products Final Rule Analytical Tools. Retrieved from Appliance & Equipment Standards: http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html | Appendix B: Energy savings of 40% from Tables 6-11 in the Navigant reference. Costfrom DOE 2011. | 3-3569 | 13 | 13 | AEO 2010 NEMS
534 | Deploy timers for existing water heaters | R: Install night time timers on water heaters | Use Intensity | 5 | 4 | Residential | Water Heating | Inefficient models | Existing | Energy Savings (%) | 7.5% | 0% | Yes | 100 |  |  | 40 | per unit | 47 R: No FS: All fuels WH to all fuels WH | Total residential storage electric and natural gas water heaters | 13 | 2010 | Original source: http://michaelbluejay.com/electricity/waterheaters.html. New sources used for cost & savings data: Energy Efficiency & Environmental News: 1) Water Heater Timers s insulated Jackets. Florida Energy Extension Service and Gary Cook. January 1993. http://www.greatlakeshomeperformance.com/elibrary/Water%20Heater%20Timers%20&%20Jackets.pdf; 2) Exclusion of timers for gas water heaters due to: Energy Efficient Water Heating. LBNL. January 1995. http://www.ces.ncsu.edu/depts/fcs/pdfs/energy_efficient.pdf) | BTO Tool: Original 3% value was based on calculation for pre-1998 electric WH for family of 4 using ~80 gal/day; heater off for 4-6 hrs/day. Edited value of 7.6% is based on BED 2011 average family characteristics & Florida Energy Extension study. The cost values were consistent among several sources, and include the cost of the timers for electric WH as well its installation cost. Appendix B: "A timer for an old (pre-1998) electric heater costs around $40 and saves about 25kWh/mo. for a family of two using 40 gallons a day with the heater off four to six hours a day, but only 14kWh/mo. for a family of four using 80 gallons a day." | 1-71 | 13 | 13 | AEO 2014 NEMS
536 | Develop max tech option for residential oil water heaters | R: Multiple Flue Design, Insulation for oil WH | System | 5 | 3 | Residential | Water Heating | Water heater, Oil | New | Energy Factor | 0.68 | 0.53 | No | 1485 | 795 | 955 | 160 | per unit | 49 R: No FS: LPG and distillate WH | Total residential water heating by LPG and distillate fuel oil | 13 | 2010 | http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr.html Primary Source: Table 5.13.3, U.S. Department of Energy, Technical Support Document (2010) | BTO Tool: Multiple flue design to increase heat transfer, combined with foam insulation (multiple flue design + 1" foam insulation) Appendix B: Table 5.13.3: Multiple flue design to increase heat transfer, combined with foam insulation (multiple flue design + 1" foam insulation) | 1-63 | 13 | 13 | AEO 2014 NEMS
541 | Replace residential gas storage with whole-home gas tankless water heaters (Tankless Level 3) | R: Replace Tank w/ Tankless Gas (Level 3) | System | 2+ | 4 | Residential | Water Heating | Tankless Gas WH | Usage: <86 gal/day | Energy Factor | 0.8 | 0.59 | No | $2303 for tankless | 1079 | 2303 | 1224 | per unit | 2 C/R: No FS: All gas to all gas | Total residential storage natural gas water heaters | 13 | 2010 | EERE Water Heater Final Rule Analytical Spreadsheet (consistent with the TSD) (http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html) | BTO Tool: Unknown gas access and cost for gas plumbing imply this is an aggressive estimate | 1-58 | 13 | 13 | AEO 2014 NEMS
543 | Replace standing pilot in new gas WH with electronic ignitions | R: Gas water heater electronic ignition | Parasitic | 5 | 5 | Residential | Water Heating | Water heater, all | New | Energy Factor | 0.64 | 0.59 | No | Cost of electronic ignition plus power venting from TSD | 1079 | 1523 | 444 | per unit | 2 C/R: No FS: All gas to all gas | All residential gas water heaters with pilot lights | 13 | 2010 | EERE Water Heater Final Rule Analytical Spreadsheet (consistent with the TSD) (http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html) Primary Source: U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy (EERE). (2011, March 30). Residential Heating Products Final Rule Analytical Tools. Retrieved from Appliance & Equipment Standards: http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html | BTO Tool: Used TSD for efficiency improvement and cost. Electronic ignition was not separated from power venting. Appendix B: DOE 2011 for efficiency improvement and cost. Savings based on moving EF from 0.59 to 0.64. | 1-65 | 13 | 13 | AEO 2014 NEMS
544 | Replace residential gas storage with whole-home gas tankless water heaters (Tankless Level 4) | R: Replace Tank w/ Tankless Gas (Level 4) | System | 2+ | 3 | Residential | Water Heating | Tankless Gas WH | All | Energy Factor | 0.82 | 0.59 | No | See existing & efficient costs | 1079 | 2377 | 1298 | per unit; 199,000 BTU/hr tankless | 2 C/R: No FS: All gas to all gas | Total residential storage natural gas water heaters | 13 | 2010 | EERE Water Heater Final Rule Analytical Spreadsheet (consistent with the TSD) (http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html) | BTO Tool: Unknown gas access and cost for gas plumbing imply this is an aggressive estimate | 1-58 | 13 | 13 | AEO 2014 NEMS
548 | Decrease cost and deploy Forced circulation (indirect active) SWH (El. to El. back up) TARGET | R: Solar WH elec. BU - indirect active (no FS)* | System | 5 | 0 | Residential | Water Heating | Solar WH: indirect, active | All | Energy Savings (%) | 37.5% | 0 | Yes | $2900 (assumed incremental to backup); Approximate target installed price: $1200 (including installation and permit) |  | 1200 | 1200 | per home; 48.3 sq. ft absorber | 1 C/R: No FS: All electric to all electric | Total electric water heating energy consumption | 13 | 2015 | SWH roadmap; Primary Source: Itron, Inc.; "California Center for Sustainable Energy Solar Water Heating Pilot Program" (3/2011) Federal Energy Management Program, "Solar Water Heating with Low-Cost Plastic Systems" (1/2012) Other Supporting Sources: Hudon, Burch "Solar Water Heating Roadmap" (in preperation) | BTO Tool: 3% end use penalty for 40W pump (scaled to 2 % for 20W design) Appendix B: Thorough analysis of multiple sources; represents aggregate savings net of parasitic loads Costs represent program targets informed by roadmap (in preperation) the price is actually the maximum price (range was 8000 to 13300 installed cost that correspond to 3-5 years payback. According to www.lhprotrade.com/getcatfile.php?w=18, the gas absorption airsource heat pump water heaters is 11480 euros for a nominal heating capacity of 41.7kW. Assuming the typical commerical gas storage water heater has a capacity of 5 Tons ~ 17 kW the cost would be ~ 4841 euros or $6324 (4/18/2013) | 1-53 | 13 | 13 | AEO 2014 NEMS
549 | Decrease cost and deploy Forced circulation (indirect active) SWH (gas to gas back up) TARGET | R: Solar WH gas BU - indirect active (no FS)* | System | 5 | 0 | Residential | Water Heating | Solar WH: indirect, active | All | Energy Savings (%) | 37.5% | 0 | Yes | $2900 (assumed incremental to backup); Approximate target installed price: $1200 (including installation and permit) |  | 1200 | 1200 | per home; 48.3 sq. ft absorber | 2 C/R: No FS: All gas to all gas | Total gas water heating energy consumption | 13 | 2015 | SWH roadmap; Primary Source: Itron, Inc.; "California Center for Sustainable Energy Solar Water Heating Pilot Program" (3/2011) Federal Energy Management Program, "Solar Water Heating with Low-Cost Plastic Systems" (1/2012) Other Supporting Sources: Hudon, Burch "Solar Water Heating Roadmap" (in preperation) | BTO Tool: 3% end use penalty for 40W pump (scaled to 2 % for 20W design) Appendix B: Thorough analysis of multiple sources; represents aggregate savings net of parasitic loads Costs represent program targets informed by roadmap (in preperation) the price is actually the maximum price (range was 8000 to 13300 installed cost that correspond to 3-5 years payback. According to www.lhprotrade.com/getcatfile.php?w=18, the gas absorption airsource heat pump water heaters is 11480 euros for a nominal heating capacity of 41.7kW. Assuming the typical commerical gas storage water heater has a capacity of 5 Tons ~ 17 kW the cost would be ~ 4841 euros or $6324 (4/18/2013) | 1-61 | 13 | 13 | AEO 2014 NEMS
553 | Deploy ground source heat pumps to all single family homes, no fuel switching | R: Single Family GSHP | System | 5 | 4 | Residential | Heating/Cooling/Water | Heat pump | Existing | Energy Savings (%) | 64.8% | 0% | Yes | $4,800/ton (average of $5,000 and $4,600 from two sources) | 5919 | 20319 | 14400 | per home; 3 ton | 1 C/R: No FS: All electric to all electric | Total electric heating, electric hot water, and proportion of electric cooling in homes with electric heating | 15 | 2013 | ORNL Residential Retrofti Tech potential Primary Source: Liu, X. Assessment of National Benefits from Retrofitting Existing Single-Family Homes with Ground Source Heat Pump Systems. Oak Ridge National Laboratory (2010) Hughes, P.J. Geothermal ( Ground-Source ) Heat Pumps: Market Status , Barriers to Adoption , and Actions to Overcome Barriers. Oak Ridge National Laboratory (2008) Other Supporting Sources: Office of the Deputy Under Secretary of Defense Report to Congress: Ground-Source Heat Pumps at Department of Defense Facilities. (2007) Hughes, P.J. & Shonder, J.A. The Evaluation of a 4000-Home Geothermal Heat Pump Retrofit at Fort Polk , Louisiana: Final Report. Oak Ridge National Laboratory (1998) | BTO Tool: Derated 10% to account for earth heating, etc. Appendix B: savings of [4.2 quads primary energy], a 45% reduction associated with SH–SC–WH in existing U.S. single-family homes Worked with author to disaggregagte into fuel-switching and non-fuel-switching opportunities DoD, perhaps the largest single customer for GHP retrofit projects, reports that in 2006 dollars housing and commercial retrofits cost $4600 and $7000 per ton respectively | 1-152 | 15 | 15 | AEO 2014 NEMS
557 | Commercialize, demonstrate, and deploy comprehensive home automation system | R: Home Automation | Use Intensity | 5 | 3 | Residential | HVAC/Lighting | Home automation | All | Energy Savings (%) | 6% | 0% | Yes | Off the shelf components: $1000; integrated system will likely reduce the cost to less than $1000 per home; at large scale adoption: ~$200. |  | 600 | 600 | per home | 59 R: No FS: All fuels/end-uses | Total residential energy consumption in all single-family homes | 20 | 2013 | 1) Cost as found $1000 (without PC, assume most homes have a PC); cost compressed to $600: Williams, Matthews, Breton, and Brady; "Use of a Computer-Based System to Measure and Manage Energy Consumption in the Home" IEEE 2006 Other Supporting Sources: Wireless home automation networks: A survey of architectures and technologies 2) Energy savings: Effectiveness of Displaying Energy Consumption Data in residential buildings: To Know is to Change. Tsuyoshi Ueno, Centeral Research Institute of Electric Power Industry (CRIEPI). Kiichiro Tsuji, Osaka University. Yukio Nakano, CRIEPI. |  | 1-179 | 20 | 20 | AEO 2014 NEMS
558 | Research, demonstrate, and deploy spray-cooled condenser for rooftop AC units in commercial buildings | C: Spray-cooled Condenser | Evaporator | 5 | 4 | Commercial | Cooling | A/C | Resi & rooftop style | COP | 3.53 | 3.04 | Yes | See incremental cost |  | 0.525 | 0.525 | per square foot; 1 ton per 280 sq.ft. | 1 C/R: No FS: All electric to all electric | Total commercial electric load of rooftop AC units (residential style) | 15 | 2010 | Friterm document pg. 4/13 Primary Source: Acul, H. Air Cooled Condensers And Their Effect On Energy. 1-13 (2008) | BTO Tool: 8525 vs 4515 Euro for 168 kW Appendix B: Impacts estimated from table on page 11 Decrease fan use from 4.68 to 1.12 kW/h | 3-3671 | 15 | 15 | AEO 2010 NEMS
561 | Research, demonstrate, and deploy climate optimized hot-dry A/C in homes. (To assure adequate dehumidification in most climates, the evaporator provides extra cooling which is unnecessary in hot-dry climates.) | R: Hot-dry AC | System | 2+ | 2 | Residential | Cooling | A/C | All | Energy Savings (%) | 20% | 0% | Yes | Assumed as Resi scales from 3 ton to 20 ton |  |  | 246 | per home | 1 C/R: No FS: All electric to all electric | Total cooling in mixed-dry and hot-dry climates | 16 | 2014 | Primary Source: Desroches, L.-B. et al. Max Tech and Beyond (2011) & Sachs, Lin, Lowenberger. Emergin Energy-Saving HVAC Technologies and Practices for the Buildings Sector, AEEE (2009) | Appendix B: Pg 22: Such regionally appropriate designs could save 20%. | 1-18 | 16 | 16 | AEO 2014 NEMS
562 | Research, demonstrate, and deploy climate optimized hot-dry A/C in commercial buildings. (To assure adequate dehumidification in most climates, the evaporator provides extra cooling which is unnecessary in hot-dry climates.) | C: Hot-dry AC | System | 2+ | 2 | Commercial | Cooling | A/C | All | Energy Savings (%) | 20% | 0% | Yes | $140-$265 above SEER13 |  |  | 0.10933 | per square foot; 1 ton per 280 sq.ft. | 1 C/R: No FS: All electric to all electric | Total cooling in hot, dry climates in all commercial buildings | 15 | 2014 | Primary Source: Desroches, L.-B. et al. Max Tech and Beyond (2011) & Sachs, Lin, Lowenberger. Emergin Energy-Saving HVAC Technologies and Practices for the Buildings Sector, AEEE (2009) | Appendix B: Pg 22: Such regionally appropriate designs could save 20%. | 3-3667 | 15 | 15 | AEO 2010 NEMS
563 | Demonstrate and deploy pre-dehumidification multiple-small plate dehumidifiers in commercial buildings in hot, humid climates | C: MSP Dehumidifier | Use Intensity | 5 | 1 | Commercial | Cooling | Dehumidifier | All | Energy Savings (%) | 32% | 0% | Yes | See incremental cost |  | 0.5 | 0.5 | per square foot | 10 C: No FS: All fuels cooling (elec+NG) | Total cooling in hot, humid climates in all commercial buildings | 15 | 2018 | MTAB, nauticadehumid.com Primary Source: MSP Technology, "Dehumidification Equipment for Recirculated Air and Dedicated Outside Air Systems (DOAS)" Desroches, L.-B. et al. Max Tech and Beyond (2011) | Appendix B: Savings taken from page 7 of MSP manual; supported by nautica claims (used manufacturer estimate) | 3-3655 | 15 | 15 | AEO 2010 NEMS
564 | Demonstrate and deploy magnetic bearing variable speed centrifugal chillers | C: Magnetic Bearing Variable Speed Centrifugal Chiller | System | 5 | 3 | Commercial | Cooling | A/C | All | kW/ton cooling | 0.5 | 0.9 | Yes | RS Means data for 135 ton water cooled screw compressor, tower not included, $595/ton/280SF=$2.12/SF. Efficent centrifugal chiller data obtained from FEMP deployment Navy study at 3 locations, averaged out costs per ton/280sf = $3.4/SF. Simple payback ranged for the 3 locations of 3.8-7.1 years. | 2.1 | 3.4 | 1.3 | per square foot; 1 ton per 280 sq.ft. | 1 C/R: No FS: All electric to all electric | All commercial centrifugal chillers | 25 | 2011 | MTAB, turbocor_chiller.pdf Primary Source: U.S. Navy Technology Validation, FEMP: "Evaluation of a Variable-speed Centrifugal Compressor with Magnetic Bearings". Pg 3. Fig 4 & 5. http://www1.eere.energy.gov/femp/pdfs/etcs_vscompressor.pdf Desroches, L.-B. et al. Max Tech and Beyond (2011) | Appendix B: Average of high capacity Navy (41-67%) and Desroches (26%) numbers Page 3 of FEMP & Navy Technology Validation study shows at ~ average ton of cooling of (60+20)/2=40 tons, baseline is 0.9 kW/ton, and var speed chiller of ~0.5 kW/ton. Fig 4&5. | 3-3643 | 25 | 25 | AEO 2010 NEMS
566 | CBI high efficiency RTU specification challenge | C: Adv. RTU (IEER 18) | System | 5 | 4 | Commercial | Cooling | RTU | Central | IEER | 18 | 11.4 | Yes |  | 0.8525 | 1.984 | 1.1315 | per square foot; 10 RTU's per 100k sq.ft | 1 C/R: No FS: All electric to all electric | Total commercial cooling by rooftop AC units (RTUs) | 15 | 2011 | 1) Base and efficient unit costs: Base cost from EIA Tech Forecast 2013; efficient cost intrapolated based on EIA Tech Forecast data for IEER 20.8 unit. 2) Performance estimated from Challenge specifications. DOE and PrivateSector Partners Introduce a New Money-Saving Specification for Commercial Air Conditioners", 2011. Daikon McQuay Rebel RTU Specifications |  | 3-3681 | 15 | 15 | AEO 2010 NEMS
567 | Improve scroll compressor performance - TARGET (COP) | C: Improved scroll compressor* | Compressor | 5 | 0 | Commercial | Cooling | Scroll compressor | Scroll compressors | Compressor COP | 4.7 | 3.4 | Yes | 272000 per building | 1.8133 | 1.05 | 0.76333 | per square foot; 150k sq.ft. building | 1 C/R: No FS: All electric to all electric | Commercial cooling: Scroll | 20 | 2015 | 28% savings from Bouza. Baseline efficiency estimated from multiple references: http://www.hitachi-ap.com/products/business/compressor/scroll/aircon_spec.html, http://www.emersoncanada.ca/pages/energy/presentations/Scroll_Compressor_Technology_Optimizing_Efficiency_Feb08.pdf) Primary Source: Personal communication: Bouza, DOE Other Supporting Sources: Manufacturer presentation (http://www.emersoncanada.ca/pages/energy/presentations/Scroll_Compressor_Technology_Optimizing_Efficiency_Feb08.pdf) and specifications: Hitachi EU Series DC Inverter controlled series, Mitsubishi R407C & 410A | Appendix B: 28% savings from DOE Funded research target. Baseline efficiency estimated from multiple references | 3-3678 | 20 | 20 | AEO 2010 NEMS
574 | Natural ventilation cooling system in all new homes (single/multi/mobile) | R: Nat. Ventilation Cooling (N, exc. Hot-humid CZ) | Windows | 2+ | 2 | Residential | Building | Windows | All A/C | Energy Savings (%) | 30% | 0% | Yes | Estimated at 1,500 British ponds, 1.6 pounds/$ |  |  | 2400 | per unit | 1 C/R: No FS: All electric to all electric | Total cooling in new homes in all but hot-humid climates | 30 | 2014 | Cardinale, et. Al. (http://www.sciencedirect.com/science/article/pii/S0378778802000245), WBDG (http://www.wbdg.org/resources/naturalventilation.php) | BTO Tool: Price data from monodraught sola-boost type system | 1-19 | 30 | 30 | AEO 2014 NEMS
575 | Demonstrate and deploy insulating and reflective attachments to homes | R: Window Attachments | Windows | 5 | 3 | Residential | HVAC | Windows | All | Energy Savings (%) | 48.15% | 0% | Yes | $157.80 vs. $48 for 30"x60" window | 720 | 2367 | 1647 | per home; 15 windows/home (BED 2011) | 30 R: No FS: Window (cond+rad) specific | Total cooling lost due to solar gain through residential windows that can benefit from attachments (assuming 50% of homes have windows that can benefit from advanced attachments (beyond typical blinds or curtains which may not be properly utilized for greater savings) | 30 | 2013 | DOE-EPA Attachments industry presentation; http://www.solar-components.com/comfortex.htm Primary Source: Savings: first principles calculation from R- and SHGC- impacts of product Price: Comfortex. Manufacturer & expert interviews Other Supporting Sources: Kotey, N.A., Wright, J.L., Barnaby, C.S., Collins, M.R., "Solar Gain Through Windows with Shading Devices: Simulation versus Measurement," ASHRAE Transactions, Vol. 115, Pt. 2, (2009) | Appendix B: Savings: adding R-value of 1.75 and reducing SHGC to 0.35 Price: Comfortex current prices compressed 1/3rd to represent learning curve | 1-117 | 30 | 30 | AEO 2014 NEMS
576 | Demonstrate and deploy insulating and reflective attachments to pre-2010 commercial buildings | C: Window Attachments [E] | Use Intensity | 5 | 3 | Commercial | HVAC | Windows | Existing | Energy Savings (%) | 51.26% | 0% | Yes | $157.80 vs. $48 for 30"x60" window; or approximately $13/sq.ft. for attachements and $4/sq.ft. for baseline | 1.44 | 4.68 | 3.24 | per square foot; wall: floor space of .9, window fill ratio of 0.4 | 33 C: No FS: Window (cond+rad) specific | All commercial windows that can benefit from attachments in pre-2010 buildings | 40 | 2013 | DOE-EPA Attachmentsindustry presentation; http://www.solar-components.com/comfortex.htm Primary Source: Savings: first principles calculation from R- and SHGC- impacts of product Price: Comfortex Manufacturer & expert interviews Other Supporting Sources: Kotey, N.A., Wright, J.L., Barnaby, C.S., Collins, M.R., "Solar Gain Through Windows with Shading Devices: Simulation versus Measurement," ASHRAE Transactions, Vol. 115, Pt. 2, (2009) | Appendix B: Savings: adding R_value of 1.75 and reducing SHGC to 0.35 Price: Comfortex current prices compressed 1/3rd to represent learning curve Market: assumes 50% of windows benefit from attachments | 3-3768 | 40 | 40 | AEO 2010 NEMS
585 | Increase adoption of standard storm windows on existing 1-pane metal framed windows in single and multi family homes | R: Standard storms on single pane windows [E] | Windows | 5 | 4 | Residential | HVAC | Windows | Existing | Energy Savings (%) | 45.79% | 0% | Yes | $150/window, uninstalled |  | 2250 | 2250 | per home; 15 storms/home, assumes 15 windows/home, 2.5x5 ft^2 (BED 2011) | 28 R: No FS: Window conduction specific | Total energy losses due to conduction for single pane glass windows for all homes built before 2010 | 30 | 2010 | 1) Costs were adjusted based on PNNL RFI response: $150 per 30"x60" window, uninstalled from http://www.efficientwindowcoverings.org/understanding-window-coverings/storm-window/ 2) Kohler, C Letter report for low-e storm window retrofits, 2006 | 1) Costs were adjusted based on PNNL RFI response: $150 per 30"x60" window, uninstalled from http://www.efficientwindowcoverings.org/understanding-window-coverings/storm-window/ 2) Report indicates 18% savings of whole home heating for low-e storms, scaled to address conductive and radiative loss, 18% of home heating and cooling is 58% of window load heating/cooling. "A simulation study in 2004 has shown that by using pyrolitic “hard” low-e coatings.. will increase from approximately 15% of the home’s heating energy to 18%. The additional cost is...on the order of $100." 3) Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 1-118 | 30 | 30 | AEO 2014 NEMS
586 | Increase adoption of low-e standard storm windows on existing 1-pane metal framed windows in homes | R: Low-e Storms [E] | Windows | 5 | 4 | Residential | Building | Windows | Existing | Energy Savings (%) | 54.63% | 0% | Yes | $150/window, uninstalled, assumes 12ft^2 window (2.5'x5') | 0 | 2250 | 2250 | per home; 15 storms/home, assumes 15 windows/home, 2.5x5 ft^2 (BED 2011) | 30 R: No FS: Window (cond+rad) specific | Total energy losses due to conduction and radiation for single pane glass windows for all homes built before 2010 | 30 | 2010 | 1) Costs were adjusted based on PNNL RFI response: $150 per 30"x60" window, uninstalled from http://www.efficientwindowcoverings.org/understanding-window-coverings/storm-window/ 2) Kohler, C Letter report for low-e storm window retrofits, 2006 | 1) Costs were adjusted based on PNNL RFI response: $150 per 30"x60" window, uninstalled from http://www.efficientwindowcoverings.org/understanding-window-coverings/storm-window/ 2) Report indicates 18% savings of whole home heating for low-e storms, scaled to address conductive and radiative loss, 18% of home heating and cooling is 55% of window load heating/cooling. "A simulation study in 2004 has shown that by using pyrolitic “hard” low-e coatings.. will increase from approximately 15% of the home’s heating energy to 18%. The additional cost is...on the order of $100." 3) Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 1-119 | 30 | 30 | AEO 2014 NEMS
587 | Increase adoption of low-e standard storm windows on existing 1-pane metal framed windows in commercial buildings | C: Low-e Storms [E] | Windows | 5 | 4 | Commercial | Building | Windows | Existing | Energy Savings (%) | 54.63% | 0% | Yes | $150/window, uninstalled, price for residential windows, assumes 12ft^2 window (2.5'x5'), also assumes similar cost for commercial windows | 0 | 4.32 | 4.32 | per square foot; wall: floor space of .9, window fill ratio of 0.4 | 33 C: No FS: Window (cond+rad) specific | Total commercial radiative and conductive window load for pre-2010 buildings with single pane windows (includes solar heat gain loss during cooling season as well as solar heat gain benefit during heating season) | 40 | 2010 | 1) Costs were adjusted based on PNNL RFI response: $150 per 30"x60" window, uninstalled from http://www.efficientwindowcoverings.org/understanding-window-coverings/storm-window/ 2) Kohler, C Letter report for low-e storm window retrofits, 2006 | 1) Costs were adjusted based on PNNL RFI response: $150 per 30"x60" window, uninstalled from http://www.efficientwindowcoverings.org/understanding-window-coverings/storm-window/ 2) Report indicates 18% savings of whole home heating for low-e storms, scaled to address conductive and radiative loss, 18% of home heating and cooling is 55% of window load heating/cooling. "A simulation study in 2004 has shown that by using pyrolitic “hard” low-e coatings.. will increase from approximately 15% of the home’s heating energy to 18%. The additional cost is...on the order of $100." 3) Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 3-3674 | 40 | 40 | AEO 2010 NEMS
590 | Deploy advanced walls in new residential buildings (offset frame with spray foam) | R: R-30 Walls (N) | Walls | 5 | 2 | Residential | Building | Walls | New | R-value | 37.1 | 11.1 | Yes | $5/sq.ft |  | 962 | 962 | per home; 2600 square feet wall space | 34 R: No FS: Wall specific | Total heating and cooling lost through walls in new single/multi/mobile homes | 30 | 2015 | Building Science, research report 0903, LaFrance Primary Source: Straube, J. and Smegal, J.; Building America Special Research Project: High-R Walls Case Study Analysis; Building Science Corporation 2009 (updated 2011) | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Appendix B: Costs calculated from manufacturer quotes; savings calculated from first principles | 1-120 | 30 | 30 | AEO 2014 NEMS
591 | Deploy advanced walls in existing residential buildings, i.e., exterior insulation finishing systems (EIFS) | R: R-30 Walls (E) | Walls | 5 | 2 | Residential | Building | Walls | Existing | R-value | 36.2 | 6 | Yes | $8/sqft (Dryvit quote thrpugh ORNL) |  | 20800 | 20800 | per home; 2600 square feet wall space | 34 R: No FS: Wall specific | Total heating and cooling lost through walls in single-family homes built before 2010 | 30 | 2015 | Building Science, research report 0903, LaFrance Primary Source: Straube, J. and Smegal, J.; Building America Special Research Project: High-R Walls Case Study Analysis; Building Science Corporation 2009 (updated 2011) | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Appendix B: Costs calculated from manufacturer quotes; savings calculated from first principles | 1-121 | 30 | 30 | AEO 2014 NEMS
593 | Deploy advanced walls in new commercial buildings (offset frame with spray foam) | C: EIFS R-30 Walls (N) | Walls | 3 | 1 | Commercial | Building | Walls | New | R-value | 37.1 | 17 | Yes | $5/sq.ft |  |  | 2.7 | per square foot; wall to floor space ratio of 0.9 | 35 C: No FS: Wall specific | Total heating and cooling energy lost through wall in all new commercial buildings | 40 | 2013 | Building Science, research report 0903, LaFrance and LBNL "Overview of US Building Stock", http://eetd.lbl.gov/ie/pdf/LBNL-43640.pdf | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 3-3688 | 40 | 40 | AEO 2010 NEMS
594 | Deploy advanced walls in existing commercial buildings, i.e., exterior insulation finishing systems (EIFS) | C: EIFS R-30 Walls (E) | Walls | 3 | 1 | Commercial | Building | Walls | Existing | R-value | 36.2 | 11.1 | Yes | $8/sqft (Dryvit quote through ORNL) |  |  | 4.32 | per square foot; wall to floor space ratio of 0.9 | 35 C: No FS: Wall specific | Total heating and cooling load due to energy loss through walls in all commercial buildings built before 2010 | 40 | 2013 | Building Science, research report 0903, LaFrance and LBNL "Overview of US Building Stock", http://eetd.lbl.gov/ie/pdf/LBNL-43640.pdf | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 3-3689 | 40 | 40 | AEO 2010 NEMS
600 | Develop integrated roofing package for existing homes in non-hot climates using phase change materials (PCM) for R-75 equivalent | R: R-75 PCM Roofs, non-hot CZ (E) | Roof | 5 | 2 | Residential | Building | Roof/ attic insulation | All homes | R-value | 75 | 23.1875 | Yes | $2.30/sq-ft; asumed $1.00 premium for retrofit |  | 3186.9735 | 3186.9735 | per home; 30x40 home, 2 stories, 10' per story | 36 R: No FS: Roof specific | Total heating and cooling energy lost through attics in all existing homes in all non-hot climates | 30 | 2025 | Miller, W. & Kosny, J. Next-Generation Roofs and Attics for Homes. ACEEE Summer Study on Energy Efficiency in Buildings 180-195 (2008) | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Appendix B: Analyzed savings for ducts and attic laods scaled to national average using existing stock as base | 1-122 | 30 | 30 | AEO 2014 NEMS
605 | Demonstration and deployment assistance to advanced (CO2) HPWH w COP of 5.1 (no fuel switching) | C: Adv. HPWH (COP 5.1, EF 3.6) (no FS) | System | 5 | 2 | Commercial | Water Heating | Water heater, electric | Commercial Buildings with small WH requirements | EF (converted from 5.1 COP) | 3.5581 | 1 | No | 3-4 year payback off eco cute spa investment vs. median commercial boiler price on google search; bsed off Japan spa case study w/ 11 units | 2799 | 30830 | 28031 | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by all commercial electric storage water heaters | 13 | 2017 | Navigant/DOE (2009): Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances Primary Source: r744.com, "Eco Cute Update: new line-up with 5.1 COP by Panasonic, upgrades by Hitachi and domestic statistics in Japan" (2011) Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007) Other Supporting Sources: Navigant Consulting Research and Development Roadmap for Water Heating. Department of Energy (2011). | BTO Tool: http://www.climaticoanalysis.org/post/eco-cute-vs-ene-farm-electricity-or-gas-battle-over-next-generation-environmentally-friendly-water-heaters/; popular Japanese product; referenced to baseline for electric water heater market, 2010 Appendix B: "achieve a COP of 5.1"; The current retail price of this Eco Cute is 814,653 Yen (~€7,940.12) | 3-3562 | 13 | 13 | AEO 2010 NEMS
608 | Deploy highest efficiency heat pump water heaters commercial buildings w small WH needs (no FS) | C: HPWH (no FS) | System | 5 | 4 | Commercial | Water Heating | Water heater, electric | New | Energy Factor | 2.27 | 0.81 | No | See existing & efficient costs | 1022 | 2097 | 1075 | per unit; 120 gallons | 1 C/R: No FS: All electric to all electric | All commercial electric small water heaters | 13 | 2012 | $150 premium for 120 gallon tank vs 50 gallon tank, (consistent with the TSD). U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy (EERE). (2011, March 30). Residential Heating Products Final Rule Analytical Tools. Retrieved from Appliance & Equipment Standards: http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html | BTO Tool: Use of HPWH with improved compressor efficiency and better coils and airflow; Appendix B: DOE 2011: Used 120 gal HPWH at 2.27 EF. $1022 used for price of baseline electric, and $2097 used for price of best 120 gallon HPWH, based on scaling 50-gallon. Assumed 1.5 water heaters per building. | 4-3502 | 13 | 13 | AEO 2010 NEMS
613 | Replace all commercial and industrial lighting with LEDs - TARGET | C/I: LEDs, SSL Program Goal (2020)* | Luminaire | 5 | 0 | Commercial/Industrial | Lighting | Lamp | All | lumens/watt | 210 | 67 | Yes | The DOE SSL Program goal is for LED troffers to reach a first cost of $85 by 2020. It is expected that there will be little to no change to commercial conventional lighting. This is estimated at a weighted average of $20/klm. Assume a 5000 lumen output is typical for commercial products. | 97.5 | 85 | -97.5 | per luminaire | 1 C/R: No FS: All electric to all electric | All lighting in all types of commercial and industrial buildings | 5 | 2020 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 3-3446 | 5 | 26 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
614 | Replace all residential lighting with LEDs - TARGET | R: LEDs, SSL Program Goal (2020)* | Lamp | 5 | 0 | Residential | Lighting | Lamp | All | lumens/watt | 210 | 26 | Yes | The DOE SSL Program goal is for LED lamps to reach a first cost of $5/klm by 2020. It is expected that there will be little to no change to residential conventional lighting. This is estimated at a weighted average of $3.6/klm. Assume a 800 lumen output is typical for residential products. | 1.2 | 4 | -17.2 | per lamp | 1 C/R: No FS: All electric to all electric | Total lighting energy consumption in all homes | 5 | 2020 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 1-73 | 5 | 86 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
615 | Deploy max tech compressor racks | C: Remote condensing units for refrigeration | System | 5 | 2 | Commercial | Refrigeration | Compressor Racks | New | Energy Savings (%) | 9% | 0% | No | See existing & efficient costs | 0 | 38016 | 38016 | per unit | 1 C/R: No FS: All electric to all electric | All supermarket compressor racks | 15 | 2014 | Table 5-9, Navigant CRE | BTO Tool: Need to update with TSD release 2/12 | 3-3501 | 15 | 15 | AEO 2010 NEMS
616 | Deploy max tech walk-in coolers and freezers | C: Max Tech Walk-In Refrigerator | System | 5 | 2 | Commercial | Refrigeration | Walk-In Coolers, Freezers | New | Energy Savings (%) | 54% | 0% | No | See existing & efficient costs | 0 | 1554 | 1554 | per unit | 1 C/R: No FS: All electric to all electric | All walk-in coolers and freezers | 11 | 2015 | Table 5-13, 5-14, Navigant CRE | No notes | 3-3508 | 11 | 11 | AEO 2010 NEMS
617 | Deploy and standardize max tech refrigerated food service equipment | C: Max Tech food service equipment | System | 5 | 2 | Commercial | Refrigeration | Refrigerated Food Service Equip | New | Energy Savings (%) | 56% | 0% | No | See existing & efficient costs | 0 | 379 | 379 | per unit | 1 C/R: No FS: All electric to all electric | Food Prep Equipment | 12 | 2015 | Table 5-17, Navigant CRE | Expected lifetime is assumed - we do not have a good source to support this assumption. | 3-3499 | 12 | 12 | AEO 2010 NEMS
619 | Deploy max tech beverage merchandisers | C: Max Tech Refrig. Beverage Merchandisers | System | 5 | 2 | Commercial | Refrigeration | Beverage Merchandiser | New | Energy Savings (%) | 55% | 0% | No | See existing & efficient costs | 0 | 620 | 620 | per unit | 1 C/R: No FS: All electric to all electric | All commercial beverage merchandisers | 15 | 2015 | Table 5-22, Navigant CRE | No notes | 3-3521 | 15 | 15 | AEO 2010 NEMS
621 | Deploy and standardize max tech supermarket display cases | C: Max Tech Supermarket Display Case | System | 5 | 2 | Commercial | Refrigeration | Display Cases | New | Energy Savings (%) | 36% | 0% | No | See existing & efficient costs | 0 | 1592 | 1592 | per unit | 1 C/R: No FS: All electric to all electric | Display Cases, Supermarkets | 10 | 2015 | Table 5-6,5-7,5-8 Navigant CRE | No notes | 3-3504 | 10 | 10 | AEO 2010 NEMS
622 | Incentives or campaign to build max tech supermarkets | C: Max Tech Supermarket | System | 5 | 2 | Commercial | Refrigeration | Supermarket Systems | New | Energy Savings (%) | 28.4% | 0% | No | See existing & efficient costs | 0 | 228536 | 228536 | per unit | 1 C/R: No FS: All electric to all electric | All supermarket refrigeration systems (cond, comp, walk-ins, & display) | 12 | 2016 | Table 5-12, 4-3, DOE/Navigant (2009), Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Equipment (http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_refrig_report_10-09.pdf) | BTO Tool: Cost is sum of compressor racks, condensers, sprmkt walk-ins, and 60x display cases, all max tech options; savings are reduced to account for load reduction (derived from Table 5-12) Appendix B: Cost is sum of compressor racks, condensers, sprmkt walk-ins, and 60x display cases, all max tech options; savings are reduced to account for load reduction (derived from Table 5-12) | 3-3507 | 12 | 12 | AEO 2010 NEMS
624 | Resi code: 30% lower than today, starting in 2017 | R: Code target: 30%* | Whole building | 5 | 0 | Residential | Building | Whole building | New | Energy Savings (%) | 30% | 0% | No | See incremental cost |  |  | 0 | per home | 5 R: No FS: All fuels HVAC (heating+cooling, no separate ventilation component) | Total heating and cooling in all new single-family homes | 30 | 2014 | Program goal | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 1-123 | 30 | 30 | AEO 2014 NEMS
625 | Resi code: 50% lower than today, starting in 2023 | R: Code target: 50%* | Whole building | 5 | 0 | Residential | Building | Whole building | New | Energy Savings (%) | 50% | 0% | No | See incremental cost |  |  | 0 | per home | 5 R: No FS: All fuels HVAC (heating+cooling, no separate ventilation component) | Total heating and cooling in all new single-family homes | 30 | 2014 | Program goal | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 1-123 | 30 | 30 | AEO 2014 NEMS
628 | Develop, demonstrate, and deploy integrated heat pumps (No fuel switching) | R: IHP | System | 5 | 2 | Residential | Heating/Cooling/Water | Heat pump | All | Energy Savings (%) | 50% | 0% | Yes |  | 5207 | 8184 | 2977 | per home; 3 ton | 1 C/R: No FS: All electric to all electric | Total electric heating, electric hot water, and proportion of electric cooling in homes with electric heating | 15 | 2017 | 1) Baxter, V.; Murphy, R; Rice, K; Craddick, B; "Development of a Small Integrated Heat Pump (IHP) for Net Zero Energy Homes" 9th International IEA Heat Pump Conference (2008): a. Standard unit cost: Estimated based on average between installed cost estimates of $5,408 and $6,013, minus $503 for the cost of the WH b. Efficient unit cost: Estimated based on average between installed cost estimates of $7,582 and $8,786 c. Used 50% as conservative estimate for total energy savings based on 46-67% range: "For the air source IHP version, the simulation results showed ~46-67% energy savings depending upon location. For the ground-source IHP version, the simulation showed over 50% savings in all locations" 2) 2008 ORNL paper "DEVELOPMENT OF A SMALL INTEGRATED HEAT PUMP (IHP) FOR NET ZERO ENERGY HOMES" | Appendix B: "For the airsource IHP version, the simulation results showed ~46-67% energy savings depending upon location. For the ground-source IHP version, the simulation showed over 50% savings in all locations" Used 50% as conservative estimate within 46-67% range | 1-152 | 15 | 15 | AEO 2014 NEMS
629 | Max Tech Level ASHP | R: Max Tech ASHP | System | 5 | 0 | Residential | Heating & Cooling | Heat pump | All | Energy Savings (%) | 40.77% | 0% | Yes | Bouza | 4680 | 4508 | -172 | per unit | 1 C/R: No FS: All electric to all electric | All electric heating, proportion of cooling in homes with electric heating | 15 | 2017 | Personal communication: Bouza, DOE. Hewitt, N.J., Huang, M.J., Anderson, M. & Quinn, M. Advanced air source heat pumps for UK and European domestic buildings. Applied Thermal Engineering 31, 3713-3719 (2011); Res CAC, HP, and Furnace TSD, June 2011. | Appendix B: Savings and cost targets reflect Building Technology Program funded targets; Hewitt et.al. demonstrate technical feasibility Single Package HP, 16.5 SEER National Average: $4866 Split System HP, 22 SEER National Average: $4149 Use Average: $4508 (instead of current cost of $5800) ASHP FS measure, Std Unit market cost changed from $3330 to $1079 (pulled from measure 695); ASHP no FS measure, Std Unit market cost changed from $4680 to $552 (pulled from measure 694) | 1-124 | 15 | 15 | AEO 2014 NEMS
630 | Residential absorption gas heat pump water heaters (no fuel switching) - TARGET | R: Absorption Gas HPWH* | System | 5 | 0 | Residential | Water Heating | Heat pump | All | Energy Factor | 1.3 | 0.59 | Yes |  | 1116 | 1800 | 684 | per unit | 2 C/R: No FS: All gas to all gas | Total gas water heating energy consumption | 13 | 2019 | 1) Efficiency: target EF for manufacturers: M. Garrabrant, Stone Mountain Technologies Inc, Development & Validation of a Gas-Fired Residential Heat Pump Water Heater, January 2013, Report DE-EE0003985, http://www.osti.gov/scitech/servlets/purl/1060285 2) Total installed cost is $1027 ($2008) (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses) Cost adjusted from $2008 to $2014 (Source: Baseline cost from EERE Water Heater Final Rule Analytical Spreadsheet (http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html). 3) This is a target installed cost for 2030 (Source: M. Garrabrant, Stone Mountain Technologies Inc, Development & Validation of a Gas-Fired Residential Heat Pump Water Heater, January 2013, Report DE-EE0003985, http://www.osti.gov/scitech/servlets/purl/1060285) |  | 1-61 | 13 | 13 | AEO 2014 NEMS
634 | Develop, demonstrate, and deploy integrated heat pumps: fuel switching only | R: IHP (FS) | System | 5 | 2 | Residential | Heating/Cooling/Water | Heat pump | Oil-gas heating and water; AC | Energy Savings (%) | 42.5% | 0% | Yes | 9,000-11,000 | 3919 | 8184 | 4265 | per home; 3 ton | 16 R: FS: All non-electric heating, non-electric WH and CAC in homes with electric heating switch to electric | All non-electric heating and water heating plus cac | 15 | 2022 | 2008 ORNL paper "DEVELOPMENT OF A SMALL INTEGRATED HEAT PUMP (IHP) FOR NET ZERO ENERGY HOMES" Primary Source: Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy., http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf | Appendix B: Table 6-11: Summary of Primary Energy Savings Potential of all Water Heating Technology Options Percent savings and cost changed to reflect site energy baseline of non-electric heating -> 43% savings | 1-153 | 15 | 15 | AEO 2014 NEMS
635 | Develop, demonstrate, and deploy integrated heat pumps: fuel switching only (commercial) | C: IHP (FS) | System | 5 | 2 | Commercial | Heating/Cooling/Water | Heat pump | All | Energy Savings (%) | 42.5% | 0% | Yes | 31530 | 21830 | 31530 | 0.64667 | per square foot | 18 C: FS: All non-electric heating, proportion of cooling and hot water in buildings with non-electric heating switch to electric | Non-electric space heating, proportion of cooling and hot water | 15 | 2022 | Tables 6-11, 6-21, and 6-23, Navigant Consulting. (2009). Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances. Washington, D.C.: Building Technology Program, Department of Energy., http://apps1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf Other Supporting Sources: Murphy,R; Rice, C; Baxter, V; Craddick, W. "Air-Source Integrated Heat Pump for NetZero-Energy Houses: Technology Status Report". Oak Ridge National Laboratory ORNL/TM-2007/112 Baxter, V.; Murphy, R; Rice, K; Craddick, B; "Development of a Small Integrated Heat Pump (IHP) for Net Zero Energy Homes" 9th International IEA Heat Pump Conference (2008) | Appendix B: Table 6-11: Summary of Primary Energy Savings Potential of all Water Heating Technology Options Percent savings and cost changed to reflect site energy baseline of non-electric heating -> 43% savings | 3-3725 | 15 | 15 | AEO 2010 NEMS
638 | Develop, demonstrate, and deploy integrated heat pumps: no fuel switching (commercial) | C: IHP | System | 5 | 2 | Commercial | Heating/Cooling/Water | Heat pump | All | Energy Savings (%) | 50% | 0% | Yes |  | 3.1833 | 6.6667 | 3.4833 | per square foot | 26 C: FS: Electric heating, electric cooling, and hot water in buildings with electric heating to all electric | Electric space heating (ASHP, GSHP, screw &other) and proportion of cooling and hot water in building with electric space heating (assumption) | 15 | 2018 | 1) Assuming 50% total energy savings as used in the residential IHP measure (# 628) (Baxter, V.; Murphy, R; Rice, K; Craddick, B; "Development of a Small Integrated Heat Pump (IHP) for Net Zero Energy Homes" 9th International IEA Heat Pump Conference (2008), "For the air source IHP version, the simulation results showed ~46-67% energy savings depending upon location. For the ground-source IHP version, the simulation showed over 50% savings in all locations") 2) Standard unit cost estimated based on the cost typical of a commercial rooftop heat pump ($5,850) and commercial electric storage WH ($3,700) (EIA - Technology Forecast Updates – Residential and Commercial Building Technologies, September 2013) 3) Efficient unit cost estimated based on the list price of 15,015 euros for a 90kBtu/Hr IHP (with integrated electric WH), which is equal to roughly $20,000 (ORIGEN COMPLETE PRICELIST 2013) 4) Incremental cost calculated based on the cost difference for two 90kBTU/Hr (7.5 Tons) systems for a 3,000 square foot building, assuming a typical ratio of 40 tons per 15,000 sq ft building. | BTO Tool: Assumed same savings as residential (%); Assumed $5000 incremental cost per 15,000 SF, i.e., the incremental cost is only 0.33/SF. The IHP technology is basically similar to the rooftop unit with the addition of a variable speed compressor and water to refrigerant heat exchanger. Appendix B: Table 6-11: Summary of Primary Energy Savings Potential of all Water Heating Technology Options | 3-3724 | 15 | 15 | AEO 2010 NEMS
642 | Increase adoption of R-5 replacement windows in new homes or at retrofit | R: R-5 Windows | Windows | 5 | 4 | Residential | Building | Windows | All | R-value | 5 | 1.8612 | Yes | Confidential | Confidential | Confidential | Confidential | per home, 222 ft^2 of window area (BED 2011) | 28 R: No FS: Window conduction specific | Total heating and cooling lost through windows due to conduction in all homes | 30 | 2010 | 1) Costs and energy savings from PNNL 2013 Highly Insulating Windows Volume Purchase Program Final Report. February 2013. |  | 1-114 | 30 | 30 | AEO 2014 NEMS
643 | Increase adoption of R-5 replacement windows in commercial buildings | C: R-5 Windows | Windows | 5 | 4 | Commercial | Building | Windows | All | R-value | 5 | 1.6129 | Yes | Confidential | Confidential | Confidential | Confidential | per square foot | 31 C: No FS: Window conduction specific | Total window conductive loss in all commercial buildings | 40 | 2010 | Program Primary Source: 6. Apte, J. & Arasteh, D. Window-Related Energy Consumption in the US Residential and Commercial Building Stock. Buildings 1-38 (Berkeley, CA, 2006). |  | 3-3637 | 40 | 40 | AEO 2010 NEMS
646 | Demonstrate and deploy radiative barrier in attics (above ducts) in new homes in hot climates | R: Attic Rad. Barrier (Ducts), Hot CZ (N) | Roof | 5 | 5 | Residential | Building | Roof/ attic insulation | All cooling in all homes in hot climates | Energy Savings (%) | 11.6% | 0% | Yes | $0.10 to $0.16/sq.ft. |  | 221.7025 | 221.7025 | per home; 30x40 home, 2 stories, 10' per story -- only the roof area = 30*40*0.16/cos(30*PI()/180) assuming 30 degree roof pitch | 1 C/R: No FS: All electric to all electric | Total cooling in all new homes in hot climates | 30 | 2013 | Primary Source: Medina, M; "On the performance of radiant barriers in combination with different attic insulation levels"; Energy and Buildings 33 (2000) 31-40 Other Supporting Sources: http://www.reflectixinc.com/basepage.asp?PageIndex=390; Adjusted for heating penalty and average national load as pwer cool roof calculations | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: Conservative estimate; ignores heating savings Appendix B: produced yearly heat ¯ow reductions of approximately 44, 28, and 23% TDM Mtg AI: 646 & 647 are combined under #107 in the Savings DB and in the Tech DB - #645 for hot climates (#645 is not in the UBER/AC). Measures 152 and 395 are applied to all heating and cooling lost through attic in all climates & homes, yet % savings are the same for 395 and for 645, 646, 647. All has been combined that could be combined. | 1-20 | 30 | 30 | AEO 2014 NEMS
647 | Demonstrate and deploy radiative barrier in attics (above ducts) in existing homes in hot climates | R: Attic Rad. Barrier (Ducts), Hot CZ (E) | Roof | 5 | 5 | Residential | Building | Roof/ attic insulation | All cooling in all homes in hot climates | Energy Savings (%) | 11.6% | 0% | Yes | $0.19/sq.ft. |  | 263.2717 | 263.2717 | per home; 30x40 home, 2 stories, 10' per story | 1 C/R: No FS: All electric to all electric | Total cooling in all existing (pre-2010) homes in hot climates | 30 | 2013 | Primary Source: Medina, M; "On the performance of radiant barriers in combination with different attic insulation levels"; Energy and Buildings 33 (2000) 31-40 Other Supporting Sources: http://www.reflectixinc.com/basepage.asp?PageIndex=390; Adjusted for heating penalty and average national load as pwer cool roof calculations | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: Conservative estimate; ignores heating savings Appendix B: produced yearly heat ¯ow reductions of approximately 44, 28, and 23% | 1-22 | 30 | 30 | AEO 2014 NEMS
648 | Demonstrate and deploy cool roofs in existing homes in the hottest climates | R: Cool roofs, hot CZ [E] | Roof | 5 | 4 | Residential | Building | Roof/ attic insulation | Existing | Energy Savings (%) | 4.5% | 0% | Yes | $0.50/SF premium. [Old info: $55-70/square for dark, $85-125 for white] |  | 692.8203 | 692.8203 | per home; 30x40 home, =30*40*0.50/COS(30*PI()/180) assuming 30° roof pitch | 1 C/R: No FS: All electric to all electric | Total cooling in all existing (pre-2010) homes in hot climates | 30 | 2013 | Page 8 of: http://www.ornl.gov/sci/buildings/2012/B11%20papers/64_Miller.pdf ;NREL measure database, BTP website. Primary Source: Konopacki, S., Akbari, H., Pomerantz, M., Gabersek, S. & Gartland, L. Cooling Energy Savings of Light-Colored Roofs for Residential and Commercial Buildings in 11 U.S. Metropolitan Areas. 117 (1997). | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: $1.20/sq-ft for white roof, $1.10 for dark Appendix B: Supporting calculations in tool | 1-22 | 30 | 30 | AEO 2014 NEMS
649 | Develop integrated roofing package for all homes in hot climates (with duct benefits) using phase change materials (PCM) for R-75 equivalent | R: R-75 PCM Roof, hot CZ (N) | Roof | 5 | 2 | Residential | Building | Roof/ attic insulation | New homes | Energy Savings (%) | 11.7% | 0% | Yes | $1.41/sqft: $0.16 fpr radiant barrier and $0.5 for cool roof. We will also have to add an estimate for PCM (20%) of ~ $1/sqft [avg. density of blown in insulation~ 1.4 lb/sqft, R38 = 13" thick --> mass of insulation/sqft. = 1.4 * 1.02 --> mass of PCM ~ 0.2*1.4*1.02 = 0.3 lb * $2.5 |  | 1953.7533 | 1953.7533 | per home; 30x40 home, =30*40*1.41/COS(30*PI()/180) assuming 30° roof pitch | 1 C/R: No FS: All electric to all electric | Central cooling in new single-family homes in hottest two climates | 30 | 2016 | Miller, W. & Kosny, J. Next-Generation Roofs and Attics for Homes. ACEEE Summer Study on Energy Efficiency in Buildings 180-195 (2008) | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: Try to get updated PCM quote from http://phasechange.com/m27-biopcmat-product-page-final.php ($2100 PCM installation in a restaurant) Appendix B: Analyzed savings for ducts and attic laods scaled to national average using new codes as base | 1-23 | 30 | 30 | AEO 2014 NEMS
650 | Demonstate, deploy, and increase adoption of dynamic window films in homes in the hottest climates | R: Dynamic Films [hot CZ] (MYP2025)* | Windows | 5 | 0 | Residential | Building | Windows | All in hot climates | SHGF, 50% of the time | 0.07 | 0.47 | Yes | DOE Roadmap target for 2025 of $2/sq.ft. |  | 444 | 444 | per home; 222 ft^2 of window area (BED 2011) | 1 C/R: No FS: All electric to all electric | Total cooling in all homes in hot climates | 30 | 2025 | R&D Roadmap for Emerging Window and Building Envelope Technologies 2014. |  | 1-33 | 30 | 30 | AEO 2014 NEMS
651 | Demonstate, deploy, and increase adoption of dynamic window films in homes | R: Dynamic Films (MYP2025)* | Windows | 5 | 0 | Residential | Building | Windows | All | SHGF, 50% of the time | 0.07 | 0.47 | Yes | DOE Roadmap target for 2025 of $2/sq.ft. |  | 444 | 444 | per home; 222 ft^2 of window area (BED 2011) | 29 R: No FS: Window radiation specific | Total cooling energy losses through windows due to solar radiation in all homes | 30 | 2025 | R&D Roadmap for Emerging Window and Building Envelope Technologies 2014. |  | 1-25 | 30 | 30 | AEO 2014 NEMS
652 | Demonstate, deploy, and increase adoption of dynamic window films in commercial buildings | C: Dynamic Films (MYP2025)* | Windows | 5 | 0 | Commercial | Building | Windows | All | SHGF, 50% of the time | 0.07 | 0.47 | Yes | DOE Roadmap target for 2025 of $2/sq.ft. |  | 0.72 | 0.72 | per square foot; wall: floor space of .9, window fill ratio of 0.4 | 32 C: No FS: Window radiation specific | Total cooling energy lost through windows due to solar heat gain in all commercial buildings | 40 | 2025 | R&D Roadmap for Emerging Window and Building Envelope Technologies 2014. |  | 3-3696 | 40 | 40 | AEO 2010 NEMS
654 | Research, demonstrate, and deploy phase change materials for existing home attics in all climates (cost reduction target) | R: PCM Attics [E]* | Roof | 5 | 0 | Residential | Building | Roof/ attic insulation | Existing | Energy Savings (%) | 54% | 0% | Yes | 522 lb for 1500 sqft ranch house ==> assume average ==> cost of PCM: Alderman Research from $1 to $2 per sqft, PCMEnergy $1.40−2.25/lb , Syntroleum Corporation $3-$4/lb, Entropy Solutions Inc. quotes $0.75−2.50/lb, Phase Change Energy Solutions:$4,4−6.47/lb, POLYWAX™ that costs $2/gal , Biodiesel crude glycerine (bio-crude) is $0.10−0.13/lb ($0.22−0.29/kg) CIF China Mainland. --> assume a price of $2/lb and 50% premium for retrofit! |  |  | 1566 | per home; 522 lb of PCM based on Jan Kośny, Nitin Shukla, and Ali Fallahi, 2012 "Cost Analysis of Simple PCM-Enhanced Building Envelopes in Southern U.S. Climates", Building America | 1 C/R: No FS: All electric to all electric | Attic generated electric cooling in single family homes in hottest 2 climates in existing homes | 30 | 2015 | Cost Analysis of Simple PCM-Enhanced Building Envelopes in Southern U.S. Climates Jan Kośny, Nitin Shukla, and Ali Fallahi | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Assumed cost penalty of 50% in existing | 1-26 | 30 | 30 | AEO 2014 NEMS
655 | Research, demonstrate, and deploy phase change materials for new home attics (cost reduction target) | R: PCM Attics (N)* | Roof | 5 | 0 | Residential | Building | Roof/ attic insulation | New | Energy Savings (%) | 54% | 0% | Yes | 522 lb for 1500 sqft ranch house ==> assume average ==> cost of PCM: Alderman Research from $1 to $2 per sqft, PCMEnergy $1.40−2.25/lb , Syntroleum Corporation $3-$4/lb, Entropy Solutions Inc. quotes $0.75−2.50/lb, Phase Change Energy Solutions:$4,4−6.47/lb, POLYWAX™ that costs $2/gal , Biodiesel crude glycerine (bio-crude) is $0.10−0.13/lb ($0.22−0.29/kg) CIF China Mainland. --> assume a price of $2/lb |  |  | 1044 | per home; 522 lb of PCM based on Jan Kośny, Nitin Shukla, and Ali Fallahi, 2012 "Cost Analysis of Simple PCM-Enhanced Building Envelopes in Southern U.S. Climates", Building America | 1 C/R: No FS: All electric to all electric | Attic generated electric cooling in single family homes in hottest 2 climates in new homes | 30 | 2015 | Cost Analysis of Simple PCM-Enhanced Building Envelopes in Southern U.S. Climates Jan Kośny, Nitin Shukla, and Ali Fallahi | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 1-27 | 30 | 30 | AEO 2014 NEMS
656 | Research, demonstrate, and deploy phase change materials for new home walls (cost reduction target) | R: PCM Walls (N)* | Walls | 5 | 0 | Residential | Building | Walls | New | Energy Savings (%) | 22% | 0% | Yes | 203 lb for 1500 sqft ranch house ==> assume average ==> cost of PCM: Alderman Research from $1 to $2 per sqft, PCMEnergy $1.40−2.25/lb , Syntroleum Corporation $3-$4/lb, Entropy Solutions Inc. quotes $0.75−2.50/lb, Phase Change Energy Solutions:$4,4−6.47/lb, POLYWAX™ that costs $2/gal , Biodiesel crude glycerine (bio-crude) is $0.10−0.13/lb ($0.22−0.29/kg) CIF China Mainland. --> assume a price of $2/lb |  |  | 406 | per home; 203 lb of PCM based on Jan Kośny, Nitin Shukla, and Ali Fallahi, 2012 "Cost Analysis of Simple PCM-Enhanced Building Envelopes in Southern U.S. Climates", Building America | 1 C/R: No FS: All electric to all electric | Wall generated electric cooling in single family homes in hottest 2 climates in new homes | 30 | 2015 | Cost Analysis of Simple PCM-Enhanced Building Envelopes in Southern U.S. Climates Jan Kośny, Nitin Shukla, and Ali Fallahi | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 1-28 | 30 | 30 | AEO 2014 NEMS
657 | Deploy advanced walls in existing residential buildings (EIFS with sealing benefit) | R: EIFS w/ Sealing (E) | Walls | 5 | 2 | Residential | Building | Walls | Existing | Energy Savings (%) | 68% | 0% | Yes | $8/sqft (Dryvit quote through ORNL) | 1820 | 15600 | 13780 | per home; 2,600 sq.ft. insulation | 34 R: No FS: Wall specific | Total heating and cooling lost through walls in homes built before 2010 | 30 | 2016 | Jan Kośny, Nitin Shukla, and Ali Fallahi | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: Savings is weighted average of walls and infiltration Appendix B: Costs calculated from manufacturer quotes; savings calculated from first principles | 1-126 | 30 | 30 | AEO 2014 NEMS
658 | Deploy R-6 insulation to homes when replacing siding | R: R-6 Sheathing [E] | Walls | 5 | 3 | Residential | Building | Walls | Existing | R-value | 17.1 | 11.1 | Yes | $0.98/sq-ft (As Per NREL cost measure database) |  | 2548 | 2548 | per home; 2,600 sq.ft. insulation | 34 R: No FS: Wall specific | Total heating and cooling lost through walls in homes built before 2010 | 30 | 2013 | Building Science, research report 0903, LaFrance Primary Source: Straube, J. and Smegal, J.; Building America Special Research Project: High-R Walls Case Study Analysis; Building Science Corporation 2009 (updated 2011) | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 1-126 | 30 | 30 | AEO 2014 NEMS
659 | Deploy R-6 insulation to homes when replacing siding (with sealing benefit) | R: R-6 Sheathing w/ Sealing [E] | Walls | 5 | 3 | Residential | Building | Walls | Existing | Energy Savings (%) | 50.7% | 0% | Yes | $0.98/sq-ft (As Per NREL cost measure database) + $1.40 (as per tyvek installation |  | 2548 | 2548 | per home; 2,600 sq.ft. insulation | 42 R: No FS: Wall and infiltration specific | Total energy loss through walls and infiltration (siding based) in all existing homes | 30 | 2013 | Building Science, research report 0903, LaFrance Primary Source: Straube, J. and Smegal, J.; Building America Special Research Project: High-R Walls Case Study Analysis; Building Science Corporation 2009 (updated 2011) | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: Savings is weighted average of walls and infiltration Appendix B: Costs calculated from manufacturer quotes; savings calculated from first principles | 1-127 | 30 | 30 | AEO 2014 NEMS
660 | Move from R-6 to EIFS when replacing siding (no sealing benefit; applies on both scenarios) | R: Sheathing to EIFS Upgrade [E] | Walls | 5 | 2 | Residential | Building | Walls | Existing | R-value | 36.2 | 17.1 | Yes | $3/sqft insulation premium (Andre Desjarlais consultation with DOE industrial partner) | 2548 | 15600 | 13052 | per home; 2,600 sq.ft. insulation | 34 R: No FS: Wall specific | Total heating and cooling lost through walls in single-family homes built before 2010 | 30 | 2015 | Building Science, research report 0903, LaFrance Primary Source: Straube, J. and Smegal, J.; Building America Special Research Project: High-R Walls Case Study Analysis; Building Science Corporation 2009 (updated 2011) | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 1-121 | 30 | 30 | AEO 2014 NEMS
661 | Insulate slab edges in existing homes to R-10 (exterior) | R: R-10 Slab Edge (E) | Basement | 5 | 4 | Residential | Building | Basement | Existing single family | Energy Savings (%) | 85% | 0 | Yes | $5.50/lin ft + $50/yard of soil to remove & replace |  | 1437.2222 | 1437.2222 | per home; 30x40 home, 2 stories, 10' per story | 38 R: No FS: Foundation specific | Total heating and cooling energy lost through slab foundation in all existing homes | 30 | 2010 | Kanasas: buildersguide.pdf; slab insulation technology factsheet.pdf Primary Source: "A Builder’s Guide to Residential Foundation Insulation" King, J.; Meyer, G Other Supporting Sources: FEMP Technology Fact Sheet: Slab Insulation", Southface Energy Institute, Oak Ridge National Laboratory | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Appendix B: Supporting calculations in tool take avings calculated from Kansas climate zones then scaled nationally | 1-128 | 30 | 30 | AEO 2014 NEMS
662 | Insulate slab edges in new homes to R-5 (exterior) | R: R-5 Slab Edge (N) | Basement | 5 | 4 | Residential | Building | Basement | New single family | Energy Savings (%) | 70% | 0 | Yes | $5.50/lin ft |  | 715 | 715 | per home; 30x40 home, 2 stories, 10' per story | 38 R: No FS: Foundation specific | Total heating and cooling energy lost through slab foundation in all new homes | 30 | 2010 | Kanasas: buildersguide.pdf; slab insulation technology factsheet.pdf Primary Source: "A Builder’s Guide to Residential Foundation Insulation" King, J.; Meyer, G Other Supporting Sources: FEMP Technology Fact Sheet: Slab Insulation", Southface Energy Institute, Oak Ridge National Laboratory | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Appendix B: Supporting calculations in tool take avings calculated from Kansas climate zones then scaled nationally | 1-129 | 30 | 30 | AEO 2014 NEMS
667 | Vacuum Insulated Panels (VIPs) in walls in all homes | R: VIP in Walls (+R-24) | Walls | 5 | 3 | Residential | Building | Walls | All | R-value | 35 | 11.1 | Yes | $16/SF (range from $12.6 - 22.9/SF, average: $16/sqft) | 0 | 48976 | 48976 | per home; BED: 3,061 sq. ft. of insulation for a 2,272 sq. ft. single family home built in 2000 | 34 R: No FS: Wall specific | Total residential heating and cooling lost through walls in all homes | 30 | 2013 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Target R value of 35; punctured VIP area would be reduced to R22 | 1-177 | 30 | 30 | AEO 2014 NEMS
668 | Vacuum Insulated Panels (VIPs) in walls in existing commercial buildings | C: VIP in Walls (+R-24) (E) | Walls | 5 | 3 | Commercial | Building | Walls | All | R-value | 35 | 11.1 | Yes | $16/SF (range from $12.6 - 22.9/SF, average: $16/sqft) | 0 | 8.64 | 8.64 | per square foot; wall: floor space of .9, window fill ratio of 0.4 | 35 C: No FS: Wall specific | Total heating and cooling load due to energy loss through walls in all commercial buildings | 40 | 2013 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Cost from Table 1 of http://www.nrel.gov/docs/fy13osti/55875.pdf | 3-3677 | 40 | 40 | AEO 2010 NEMS
676 | Demonstrate and deploy dual source heat pumps in homes in non-coldest climates, FS | R: Dual Source HP (FS) | System | 5 | 4 | Residential | Heating & Cooling | Heat pump | Climate zones 3-5 | Energy Savings (%) | 79% heating, 15% cooling | 0% | Yes | $3000/ton ground | 4680 | 7560 | 2880 | per home; 3 ton | 20 R: FS: All non-electric heating, proportion of cooling switch to electric | Non-electric heating, proportion of cooling not in coldest 2 climates | 15 | 2013 | FEMP Technology alert DOE/E-0220; savings and costs relative to furnace and A/C. Ground loop from Navigant 2009 (Ground‐Source Heat Pumps: Overview of Market Status, Barriers to Adoption, and Options for Overcoming Barriers) $3000/ton for residential retrofit. Baseline cost from NREL Retrofit Measures Database. Primary Source: Hadley, D., Collins, T., Parkerk, S., Cornett, G. & Cavedo, F. Energy Savings from Dual-Source Heat Pump Technology Federal Energy Management Program E-0220 (2000) | BTO Tool: Savings over ASHP: 38% heating, 15% cooling. Cost of system based on 2/3 GSHP and 1/3 ASHP. Appendix B: "At the main U.S. Post Office facility in Valrico, three air- source heat pumps were retrofitted with the dual-source technology, reducing daily energy use by nearly 38%" Multiple case studies used for average of 34% savings from ASHP | 1-131 | 15 | 15 | AEO 2014 NEMS
678 | Research, demonstrate, and deploy advanced liquid desiccant A/C (e.g., DeVAP, DuCool) in commercial buildings in dry climates | C: DEVAP, dry CZ | System | 5 | 1 | Commercial | Cooling | A/C | Central | Energy Savings (%) | 76.2% | 0% | Yes | 10 ton unit costed by NREL at $8,100 material + markup and business expense; Water consumption adds roughtly $0.47/SF; UPDATED DATA BASED ON NCI REPORT: End user equipment ocst of baseline DX rooftop unit is $9300; DEVap manufacturer cost estimate is $19,000 for 1k units/year | 9300 | 19000 | 2.0867 | per square foot; 10 tons per 6,000 sq.ft. | 1 C/R: No FS: All electric to all electric | Total cooling in dry climates by all commercial RTUs | 15 | 2016 | http://www.nrel.gov/features/20100611_ac.html Primary Source: Eric Kozubal, Jason Woods, Jay Burch, Aaron Boranian, and Tim Merrigan. Desiccant Enhanced Evaporative Air-Conditioning (DEVap): Evaluation of a New Concept in Ultra Efficient Air Conditioning http://www.nrel.gov/docs/fy11osti/49722.pdf; NCI Internal DeVAP Report Cost (listed value is not consistent with this source: "Rooftop units using DEVAP design are initially expected to cost ~30% more than competing models." Kozubal. NREL. July 2 2012. http://www.nrel.gov/docs/fy12osti/55740.pdf | BTO Tool: MTAB, NREL website, DuCool?AdvantixSystems website Appendix B: Kozubal: $15,200 for standard DX, $20,461 for DeVap (10-ton system). Assumes 10 tons per 6,000 sq.ft. for dry climates ($0.88/ft2). ($0.20/ft2 added for plumbing to unit) Total source energy 106,268 kWh for baseline and 10,506 for DeVAP. Source energy converted to site energy to estimate energy savings. | 3-3723 | 15 | 15 | AEO 2010 NEMS
679 | Research, demonstrate, and deploy advanced liquid desiccant A/C (e.g., DeVAP, DuCool) in homes in dry climates | R: DEVAP, dry CZ | System | 5 | 1 | Residential | Cooling | A/C | Central | Energy Savings (%) | 39.5% | 0% | Yes | (Assume $2600 equipment in base, $2080 installation); LDAC cost from NREL with 30% markup plus 1 day of plumbing time/cost; 2.7 gallons of site water consumption per ton, equates roughly to 18000 gallons/year, over 20 years with 6.5% discount rate results in roughly $1135 price premium; UPDATED DATA BASED ON NCI REPORT: Equipment cost of baseline DX system in hot-dry climate is $3200; DEVap equipment cost estimate is $8100; Water usage still applies | 3200 | 9235 | 6035 | per home; 3 ton | 1 C/R: No FS: All electric to all electric | Total residential central cooling in dry climates | 17 | 2017 | http://www.nrel.gov/features/20100611_ac.html Primary Source: Eric Kozubal, Jason Woods, Jay Burch, Aaron Boranian, and Tim Merrigan. Desiccant Enhanced Evaporative Air-Conditioning (DEVap): Evaluation of a New Concept in Ultra Efficient Air Conditioning http://www.nrel.gov/docs/fy11osti/49722.pdf NREL Residential Efficiency Measures Database. http://www.nrel.gov/ap/retrofits/measures.cfm?gId=2&ctId=16; NCI Internal DeVAP Report Cost (listed value is not consistent with this source: "Rooftop units using DEVAP design are initially expected to cost ~30% more than competing models." Kozubal. NREL. July 2 2012. http://www.nrel.gov/docs/fy12osti/55740.pdf | BTO Tool: MTAB, NREL website, DuCool?AdvantixSystems website Appendix B: Kozubal: $7484 for 3-ton DeVap (uninstalled). Plous $2080 for installation. Same energy savings as Measure 678. | 1-30 | 17 | 17 | AEO 2014 NEMS
680 | Engine Driven Heat Pump, commercial buildings | C: Engine Driven HP (FS to gas) | System | 5 | 3 | Commercial | Heating & Cooling | Heat pump | Replace all electric HVAC systems in commercial buildings | Energy Savings (%) | -24.63% | 0% | Yes | Measure will be about double the cost of an RTU | 9.4 | 18.8 | 9.4 | per square foot; 1 ton per 280 sq. ft. | 3 C/R: FS: All electric to all gas | Total commercial electric heating and proportion of cooling in buildings with electric heating | 15 | 2015 | Discussion with Omar Abdelaziz. Baseline cost from RS Means Assemblies Cost Data, 33rd Edition ($9.4/ft2 for twenty single-zone RTUs, 2 tons each, including ductwork and controls) Primary Source: Omar Abdelaziz. Oak Ridge National Laboratory. 2011. Personal communication RS Means. 2012. Assemblies Cost Data, 33rd Edition | BTO Tool: Uses more site energy: Goal seek solved to -24.5% energy savings to give 30% primary energy savings vs ASHP Appendix B: Abdelaziz: Savings estimate of 30% source energy savings compared to standard electric heat pump, an increase in site energy use of 25%. Cost estimated at twice the cost of an RTU. Baseline cost from RS Means ($9.4/ft2 for twenty single-zone RTUs, 2 tons each, including ductwork and controls) Explanation of Efficiency Improvement being negative, as explained in the "Notes" column for this measure: "BTO Tool: Uses more site energy: Goal seek solved to -24.5% energy savings to give 30% primary energy savings vs ASHP" Created a new market for NG Heating + Electric AC (3-3782). Emailed Bob Zogg about this on 4/19 and he responded that there is no more recent, up-to-date cost information that he knows of. Can revisit if Bill Goetzler (also emailed on 4/19) responds saying he knows of anything. | 3-3804 | 15 | 15 | AEO 2010 NEMS
681 | Demonstrate and deploy Energy Recovery Ventilation (ERV) in new commercial buildings | C: Energy Recovery Vent (N) | Use Intensity | 5 | 4 | Commercial | Building | System | New | Energy Savings (%) | 10% | 0% | Yes |  |  | 0.17 | 0.17 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | Total HVAC load in new commercial buildings | 20 | 2013 | 1) pg. 10-11 of Emerging Energy-Saving HVAC Technologies and Practices for the Building Sector (2009) by Sachs, Lin, Lowenberger. ACEEE. December 2009. 2) pg. 4-33, 34 of Energy Consumption Characteristics of Commercial Building HVAC Systems Volume III: Energy Savings Potential. Roth, Westphalen, dieckmann, Hamilton, Goetzler. TIAX. 2002. 3) p.3 of Energy Recovery Ventilation. FPL Technical Paper. 4) Paper cites incremental cost per unit as $1,150 (pg 11) for a building of 6600 sq.ft., 561 cfm, 8.5 tons RTU (pg 10). Dividing this incremental cost by the building square footage gives an incremental cost of $0.17/sqft of Emerging Energy-Saving HVAC Technologies and Practices for the Building Sector (2009) by Sachs, Lin, Lowenberger. ACEEE. December 2009. | BTO Tool: Assumes cost is half of retrofit cost. K-12 AERG suggests 20% whole building savings on average, or ~ 40% HVAC savings; Assumes 70% reduction of infiltration load Appendix B: Chiras: "Energy-recovery ventilators are a well-developed technology. Their prices range from about $500 to $1,700, not including installation." " Most energy-recovery ventilation systems on the market today recover about 70 to 80 percent of the energy in the outgoing air, transferring it to the incoming air." DOE RECS: Average ft2 = 2170 Cost estimates for residential ERVs are close to $2000 installed based on Chiara article, assuming a high-end multi-point system. Average house is 2170 ft2. Assumes 70% reduction of infiltration load, which is 37% of the heating load. | 3-3639 | 20 | 20 | AEO 2010 NEMS
682 | Demonstrate and deploy dual source heat pumps in commercial buildings in non-coldest climates (FS only) | C: Dual source HP (FS) | System | 5 | 4 | Commercial | Heating & Cooling | Heat pump | Climate zones 2-5 | Energy Savings (%) | 79% heating, 15% cooling | 0% | Yes | $7000/ton ground | 9.4 | 11.1542 | 1.7542 | per square foot; 40 ton total, 10 ton ground 11,200 sq.ft. | 21 C: FS: All non-electric heating, proportion of cooling switch to electric | Non-electric space heating, proportion of cooling, excluding coldest climate | 15 | 2013 | FEMP Technology alert DOE/E-0220; savings relative to ASHP. Savings adjusted for gas reference case. Baseline costs for gas and electric based on RS Means Assemblies Cost Data, 33rd Edition ($9.4/ft2 for twenty single-zone RTUs, 2 tons each, including ductwork and controls; $8.65/ft2 for a rooftop electric heat pump, including ductwork and controls, scaled by 75% because 25% of load is met by ground loop) Ground loop cost from ORNL Residential Retrofti Tech potential ($7000/ton for commercial retrofit), assumes precent savings similar to residential. Primary Source: Hadley, D., Collins, T., Parkerk, S., Cornett, G. & Cavedo, F. Energy Savings from Dual-Source Heat Pump Technology Federal Energy Management Program E-0220 (2000) | Appendix B: "At the main U.S. Post Office facility in Valrico, three air- source heat pumps were retrofitted with the dual-source technology, reducing daily energy use by nearly 38%" Multiple case studies used for average of 34% savings from ASHP | 3-3726 | 15 | 15 | AEO 2010 NEMS
685 | Deploy ground source heat pumps (GSHP) to all commercial buildings, no fuel switching | C: GSHP | System | 5 | 3 | Commercial | Heating/Cooling/Water | Heat pump | All | Energy Savings (%) | 64.8% | 0% | Yes |  | 9.4 | 28.5714 | 19.1714 | per square foot; 1 ton per 280 sq. ft. | 26 C: FS: Electric heating, electric cooling, and hot water in buildings with electric heating to all electric | Electric space heating (ASHP, GSHP, screw &other) and proportion of cooling and hot water in building with electric space heating (assumption) | 16 | 2013 | 1) Cost from pg. 8, energy savings from pg. 22 (assumes similar to the residential sector) of Liu, Xiaobing. Energy and Transportation Science Division, Oak Ridge National Laboratory. Assessment of National Benefits from Retrofitting Existing Single-Family Homes with Ground Source Heat Pump Systems. August 2010. 2) Cost estimate confirmed by data internal to NCI. 3) Baseline cost from RS Means Assemblies Cost Data, 33rd Edition ($9.4/ft2 for twenty single-zone RTUs, 2 tons each, including ductwork and controls) Hughes, P.J. & Shonder, J.A. The Evaluation of a 4000-Home Geothermal Heat Pump Retrofit at Fort Polk , Louisiana: Final Report. Oak Ridge National Laboratory (1998) | Phil: Worked with author to disaggregagte into fuel-switching and non-fuel-switching opportunities | 3-3724 | 16 | 25 | AEO 2010 NEMS
686 | Thermoelectric (TE) devices cooling in commercial | C: TE subcooling RTU | Heat exchanger | 2+ | 2 | Commercial | Cooling | RTU | RTUs, commercial | Energy Savings (%) | 9% | 0% | Yes |  |  |  |  | per square foot | 1 C/R: No FS: All electric to all electric | Total commercial cooling by rooftop AC units (RTUs) | 15 | 2015 | Akei et al. 2007. “Vapor Compression Circuit and Method Including a Thermoelectric Device.” U.S. Patent No: US 7,240,494 B2. July 10, 2007. Radermacher et al. 2007. “Integrated Alternative and Conventional Cooling Technologies”. ASHRAE Journal. October, 2007. p 28-35. Radermacher, Reinhard. 2011. Personal Communication. June 2011. Radhakrishnan et al. 2009. “Thermoelectric Device Based Refrigerant Subcooling.” U.S. Patent Application Publication. Pub. No: US 2009/0266084 A1. Oct. 29, 2009. Schoenfeld, Jonathan. 2008. “Integration of a Thermoelectric Subcooler into a Carbon Dioxide Transcritical Vapor Compression Cycle Refrigeration System.” University of Maryland. Yang et al. 2008. “Thermoelectric Technology Assessment: Application to Air Conditioning and Refrigeration.” HVAC&R Research. Volume 14, Number 5. September 2008. Primary Source: Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. 289 (2011). | Appendix B: Technology is in the research stage. No reliable cost data is available. Energy savings potential estimated as 0.2 Quads/year out of 2.25 Quads/year (9%). | 3-3681 | 15 | 15 | AEO 2010 NEMS
689 | Thermotunneling cooling systems - TARGET | C: Thermotunneling cooling systems* | System | 5 | 0 | Commercial | Cooling | RTU and HP | Commercial cooling - RTU and HP | Energy Savings (%) | 10% | 0% | Yes | 9000 | 7500 | 9375 | 1.3393 | per square foot (1 ton per 280 square feet); 5 ton model | 1 C/R: No FS: All electric to all electric | Commercial Cooling (HP and RTU), 100% new and 50% old | 15 | 2015 | Brown, DR. et al. “The Prospects of Alternatives to Vapor Compression Technology for Space Cooling and Food Refrigeration Applications.” PNNL-19259. PNNL. March 2010. Prepared for the U.S. DOE under contract DE-AC05-76RL01830. Sachs, H. et al. “Emerging Energy-Saving Technologies and Practices for the Building Sector as of 2004.” October 2004. Report Number A042. ACEEE. Weaver, Stan et al. “Thermotunneling Based Cooling Systems for High Efficiency Buildings.” Final Technical Report. GE Global Research. DE-FC26-04NT42324. Cool Chips PLC, Presentation. “Cool Chips – Technical Overview.” http://www.coolchips.gi/technology/Coolchipstech3Jan06.pdf Cool Chips PLC, Website. http://www.coolchips.gi/about.shtml Primary Source: Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. 289 (2011). (pg. 78, Cost and % energy savings.) | Deployment level of 1 was changed based on Brown, et al. The prospects of alternative to vapor compression technology for space cooling and food refrigereation applications. 2010. report, which states a prototype has not yet been developed that can show % efficiency increase during cooling. Appendix B: "Applied to relevant annual energy consumption by increasing system efficiency by 10%." Premium of 20% ($1.07/ft2) based on $9000, 5-ton system, 280 ft2/ton. 372 is R: Thermotunneling Refrigeration; 689 is C: Thermotunneling Cooling These measures represent the same fundamental technology but in very different applications. Thermotunneling is still a very immature technology (both measures have a deployment level of 1). The energy savings in 372 is based on theoretical max savings, so to hedge against this estimate, "Theoretical Efficiency" will be added to the measure name. The cost of 372 represents a 25% premium over the baseline, while 689 is based on a 20% premium. 689 will be changed to 25% also for consistency. | 3-3753 | 15 | 15 | AEO 2010 NEMS
690 | Magnetic Cooling | C: RTU: magnetic cooling | System | 3 | 2 | Commercial | Cooling | A/C | Vapor-compression cooling systems in chillers and rooftop AC units, commercial | Energy Savings (%) | 25% | 0% | Yes | 0 | 0 | 0 | 2.7306 | per square foot; 1 ton per 280 square foot | 10 C: No FS: All fuels cooling (elec+NG) | All commercial cooling by RTUs and chillers, 100% new and 50% old | 17 | 2018 | Boeder, A., and Zimm, C., 2006. “Magnetic Refrigeration Technology for High Efficiency Air Conditioning.” Report prepared by Astronautics Corporation of America for the U.S. Department of Energy. December. Chubu Electric, 2006. “Development of Room Temperature Magnetic Refrigeration System - World leading performance a big step forward in achieving practical systems –“. Press Release. November 7. Retrieved July 6, 2011 from http://www.chuden.co.jp/english/corporate/press2006/1107_1.html. Dieckmann, J., Roth, K., and Brodrick, J., 2007. “Emerging Technologies – Magnetic Refrigeration.” ASHRAE Journal. pp. 74-76. August. Goetzler, W., Goffri, S., Jasinski, S., Legett, R., Lisle, H., Marantan, A., Millard, M., Pinault, D., Westphalen, D., and Zogg, R., 2009. “Energy Savings Potential and RD&D Opportunities for Commercial Refrigeration.” Report prepared by Navigant Consulting, Inc. for the U.S. Department of Energy Building Technologies Program. September. Gorman, S., 2009. “As hybrid cars gobble rare metals, shortage looms”. Reuter. Retrieved July 7, 2011 from http://www.reuters.com/article/2009/08/31/us-mining-toyota-idUSTRE57U02B20090831. Gschneider, K. A., and Pecharsky, V. K., 2008. “Thirty years of near room temperature magnetic cooling: Where we are today and future prospects.” International Journal of Refrigeration. Vol. 31, pp. 945-961. January 25. Liu, D., Yue, M., Zhang, J., McQueen, T.M., Lynn, J., Wang, X., Chen, Y., Li, J., Cava, R.J., Liu, X., Altounian, Z., and Huang, Q., 2009. “Origin and tuning of the magnetocaloric effect for the magnetic refrigerant Mn1.1Fe0.9(P0.80Ge0.20).” January. Shen, J., 2011. “Pressure to be lifted on rare earth element pricing, says Information Network “. Digitimes. Retrieved July 7, 2011 from http://www.digitimes.com/news/a20110707PR201.html. Primary Source: Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. 289 (2011). | Appendix B: Technology is in the research stage. No reliable cost data is available. Energy savings estimate is 17% of whole building energy use. | 3-3754 | 17 | 17 | AEO 2010 NEMS
692 | Decrease cost & deploy indirect, active SWH w/ elec. BU to commercial (no FS) | C: Solar WH indirect active, elec. BU (no FS) | System | 5 | 2 | Commercial | Water Heating | Solar WH: indirect, active | All | Energy Savings (%) | 61% | 0 | Yes | 103.61/sqft compressed 50% as per roadmap |  | 24710.985 | 24710.985 | per unit; 477 square feet absorber | 1 C/R: No FS: All electric to all electric | Total energy consumption by all commercial electric storage water heaters | 13 | 2014 | SWH roadmap; California Center for Sustainable Energy Solar Water Heating Pilot Program 3/2011 Primary Source: Itron, Inc.; "California Center for Sustainable Energy Solar Water Heating Pilot Program" (3/2011) Federal Energy Management Program, "Solar Water Heating with Low-Cost Plastic Systems" (1/2012) Other Supporting Sources: Hudon, Burch "Solar Water Heating Roadmap" (in preperation) | BTO Tool: 3% end use penalty for 40W pump (scaled to 2 % for 20W design) Appendix B: Thorough analysis of multiple sources; represents aggregate savings net of parasitic loads Costs represent program targets informed by roadmap (in preperation) | 3-3562 | 13 | 13 | AEO 2010 NEMS
694 | R&D Residential Solar assisted ASHPWH, tech limit (no FS) | R: Solar assisted ASHPWH (no FS) | System | 5 | 1 | Residential | Water Heating | Solar assisted ASHP | All | COP | 5.25 | 1 | No | Assumed same as current HPWH plus SWH target | 552 | 2682 | 2130 | per unit | 1 C/R: No FS: All electric to all electric | Total electric water heating energy consumption | 13 | 2024 | Li. Et.al, "Experimental performance analysis on a direct-expansion solar-assisted heat pump water heater"; Applied Thermal Engineering 27 (2007) 2858–2868 Other Supporting Sources: Guoying, X; Ziaosong, Z; Lei, Y; Shiming, D.; "Performance of a solar-air source heat pump system for water heating on different weather conditions" IEEE (2009) | BTO Tool: Assume no difference in COP -> EF conversion as compared to standard tank Appendix B: "The seasonal average value of the COP and the collector efficiency was measured as 5.25 and 1.08, respectively." Used COP provided for performance; estimated cost using capital/operating cost target provided Possible explanation for collector efficiency of 1.08: The authors probably mean that the solar panel absorbs 8% more heat than it would in a conventional application, i.e., they are reporting efficiency relative to the conventional application. The lower panel temperature will lower convective losses to the ambient. In fact, the convective “losses” could actually be negative, resulting in a convective gain, if the panel temperature is below the ambient air temperature. 694-697 represent solar assisted ASHPs at costs of about $3500 for Res and $32,000 for Comm. Costs were very roughly based on a primitive rule of thumb. Measures in the Uber include Solar WH (with costs based on program roadmap targets), and ASHPWHs (with costs based on very primitive rules of thumb). Better cost sources should be used as they become available. | 1-53 | 13 | 13 | AEO 2014 NEMS
696 | R&D Commercial Solar assisted ASHPWH, tech limit (no FS) | C: Solar assisted ASHPWH (no FS) | System | 5 | 1 | Commercial | Water Heating | Solar assisted ASHP | All | COP | 5.25 | 1 | No | Assumed same as current HPWH plus SWH target | 2799 | 0 | -2799 | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by all commercial electric storage water heaters | 13 | 2028 | Li. Et.al, "Experimental performance analysis on a direct-expansion solar-assisted heat pump water heater"; Applied Thermal Engineering 27 (2007) 2858–2868 Other Supporting Sources: Guoying, X; Ziaosong, Z; Lei, Y; Shiming, D.; "Performance of a solar-air source heat pump system for water heating on different weather conditions" IEEE (2009) | BTO Tool: Assume no difference in COP -> EF conversion as compared to standard tank Appendix B: "The seasonal average value of the COP and the collector efficiency was measured as 5.25 and 1.08, respectively." Used COP provided for performance; estimated cost using capital/operating cost target provided Possible explanation for collector efficiency of 1.08: The authors probably mean that the solar panel absorbs 8% more heat than it would in a conventional application, i.e., they are reporting efficiency relative to the conventional application. The lower panel temperature will lower convective losses to the ambient. In fact, the convective “losses” could actually be negative, resulting in a convective gain, if the panel temperature is below the ambient air temperature. 694-697 represent solar assisted ASHPs at costs of about $3500 for Res and $32,000 for Comm. Costs were very roughly based on a primitive rule of thumb. Measures in the Uber include Solar WH (with costs based on program roadmap targets), and ASHPWHs (with costs based on very primitive rules of thumb). Better cost sources should be used as they become available. | 3-3562 | 13 | 13 | AEO 2010 NEMS
698 | R&D Residential Air-source HPWH, High Performance Target (no FS) | R: ASHPWH, Target (no FS) | System | 5 | 0 | Residential | Water Heating | Water heater, electric | All | COP | 4.8 | 0.9 | No | Tech. Limit per the TSD $1134 + $1000 for Variable speed compressor, $500 for electronic expansion valve and controller, $500 for optimized heat exchangers, $1000 for split system packaging and installation |  | 4134 | 4134 | per unit | 1 C/R: No FS: All electric to all electric | Total electric water heating energy consumption | 13 | 2022 | Zhang, J., Wang, R.Z. & Wu, J.Y. System optimization and experimental research on air source heat pump water heater. Applied Thermal Engineering 27, 1029-1035 (2007). Other Supporting Sources: Xu, G., Zhang, X. & Deng, S. A simulation study on the operating performance of a solar–air source heat pump water heater. Applied Thermal Engineering 26, 1257-1265 (2006). measures 698 and 700 are based on a 2007 paper not the TSD. The TSD maximum system efficiency is at EF of 2.35 with an installed cost premium of only $1703 - $569 = 1134; --> The 2007 paper refer to R22 which is no longer in use and depend on an external evaporator. Remove "Tech Limit" from title and use 4.8 as the target EF and target cost as 3* the cost of the TSD |  | 1-53 | 13 | 13 | AEO 2014 NEMS
700 | R&D Commercial Air-source HPWH, High Performance Target (no FS) | C: ASHPWH* | System | 5 | 0 | Commercial | Water Heating | Water heater, electric | All | COP | 4.8 | 0.9 | No | according to google search and http://www.hotwater.com/water-heaters/commercial/water-heaters/electric/heat-pump-awh/, the $2800 corresponds to a unit that is about 18 kW capacity which is 4 times the capacity of the residential unit; hence cost = 4 * cost of residential unit | 2799 | 18536 | 15737 | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by all commercial electric storage water heaters | 13 | 2022 | Zhang, J., Wang, R.Z. & Wu, J.Y. System optimization and experimental research on air source heat pump water heater. Applied Thermal Engineering 27, 1029-1035 (2007). Other Supporting Sources: Xu, G., Zhang, X. & Deng, S. A simulation study on the operating performance of a solar–air source heat pump water heater. Applied Thermal Engineering 26, 1257-1265 (2006). measures 698 and 700 are based on a 2007 paper not the TSD. The TSD maximum system efficiency is at EF of 2.35 with an installed cost premium of only $1703 - $569 = 1134; --> The 2007 paper refer to R22 which is no longer in use and depend on an external evaporator. Remove "Tech Limit" from title and use 4.8 as the target EF and target cost as 3* the cost of the TSD | measures 698 and 700 are based on a 2007 paper not the TSD. The TSD maximum system efficiency is at EF of 2.35 with an installed cost premium of only $1703 - $569 = 1134; --> The 2007 paper refer to R22 which is no longer in use and depend on an external evaporator. Remove "Tech Limit" from title and use 4.8 as the target EF and target cost as 3* the cost of the TSD ... on the other hand; 525 and 539 need to have the same efficient cost of 814653 Japanese Yen = $8300 (4/18/2013) or use a 50% cost compression to $4150! | 3-3562 | 13 | 13 | AEO 2010 NEMS
702 | R&D Residential engine driven/absorption HPWH, Max Tech (no FS) | R: Gas HPWH, tech limit (no FS) | System | 2+ | 1 | Residential | Water Heating | Water heater, gas | All | COP | 1.6577 | 0.59 | No | 64% "investment" cost, 36% operating at 10 MMBTU/year + $50 service biannually | 1079 | 2880 | 1801 | per unit; 50 gallon capacity | 2 C/R: No FS: All gas to all gas | Total gas water heating energy consumption | 13 | 2022 | HepBasli et. Al, Sanyae Primary Source: Zhang et. al. "Analysis on the heating performance of a gas engine driven air to water heat pump based on a steady-state model", Energy Conversion and Management 46 (2005) 1714–1730 Other Supporting Sources: Hepbasli, A. & Kalinci, Y. A review of heat pump water heating systems. Renewable and Sustainable Energy Reviews 13, 1211-1229 (2009). | BTO Tool: Scales current experimental max of 1.37 by 21% as indicated in paper Appendix B: Figure 5 shows the PER: "The primary energy ratio (PER) is deﬁned as the heat gained divided by the input energy." Cost taken as 64% "investment" cost, 36% operating at 6 MMBTU/year + $50 service biannually. Implies: $2,880 cost improvement from COP 0.59 to 1.67 | 1-61 | 13 | 13 | AEO 2014 NEMS
704 | R&D Commercial engine driven/absorption HPWH, Max Tech (no FS) | C: Gas HPWH, tech limit (no FS) | System | 5 | 1 | Commercial | Water Heating | Water heater, gas | All | COP | 1.6577 | 0.59 | No | 64% "investment" cost, 36% operating at 36 MMBTU/year + $50 service biannually; 230 TBTUs in 1.4M tanks (50% of load, 80% of units) | 4606 | 35580.9524 | 30974.9524 | per unit | 2 C/R: No FS: All gas to all gas | Total energy consumption by all commercial gas storage water heaters | 13 | 2023 | HepBasli et. Al, Sanyae Primary Source: Zhang et. al. "Analysis on the heating performance of a gas engine driven air to water heat pump based on a steady-state model", Energy Conversion and Management 46 (2005) 1714–1730 Other Supporting Sources: Hepbasli, A. & Kalinci, Y. A review of heat pump water heating systems. Renewable and Sustainable Energy Reviews 13, 1211-1229 (2009). | BTO Tool: Scales current experimental max of 1.37 by 21% as indicated in paper Appendix B: Figure 5 shows the PER: "The primary energy ratio (PER) is deﬁned as the heat gained divided by the input energy." Cost taken as 64% "investment" cost, 36% operating at 6 MMBTU/year + $50 service biannually. Implies: $2,880 cost improvement from COP 0.59 to 1.67 | 3-3561 | 13 | 13 | AEO 2010 NEMS
707 | Replace gas water heaters with tankless gas water heaters w/improved HX, direct vent, low NOx (Level 6) | R: Tankless water heater, level 6 (No FS) | Heat Exchanger | 2+ | 4 | Residential | Water Heating | Tankless Gas WH | All | Energy Factor | 0.85 | 0.59 | Yes | 3034 | 1079 | 3034 | 1955 | per unit; 199,000 BTU/hr capacity | 2 C/R: No FS: All gas to all gas | Total residential storage natural gas water heaters | 13 | 2013 | DOE TSD (2010), http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr.html | BTO Tool: Unknown gas access and cost for gas plumbing imply this is an aggressive estimate; Baseline efficiency and cost is weighted average of standard gas storage (98%) and tankless water heaters (2%) | 1-58 | 13 | 13 | AEO 2014 NEMS
708 | Replace gas water heaters with tankless gas water heaters with direct vent, condensing (Standard Level 7) | R: Tankless Water Heater, Level 7 | Heat Exchanger | 2+ | 3 | Residential | Water Heating | Tankless Gas WH | All | Energy Factor | 0.92 | 0.59 | Yes | 2884 | 1079 | 2884 | 1805 | per unit; 199,000 BTU/hr capacity | 2 C/R: No FS: All gas to all gas | Total residential storage natural gas water heaters | 13 | 2013 | DOE TSD (2010), http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr.html Primary Source: U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy (EERE). (2011, March 30). Residential Heating Products Final Rule Analytical Tools. Retrieved from Appliance & Equipment Standards: http://www1.eere.energy.gov/buildings/appliance_standards/residential/heating_products_fr_spreadsheets.html | BTO Tool: Unknown gas access and cost for gas plumbing imply this is an aggressive estimate; Baseline efficiency and cost is weighted average of standard gas storage (98%) and tankless water heaters (2%) Appendix B: Efficiency and cost from DOE 2011, Efficiency Level 7. Baseline efficiency and cost is weighted average of standard gas storage/tankless. Does not include gas access and plumbing costs. | 1-58 | 13 | 13 | AEO 2014 NEMS
718 | A heat pump coupled washer is devised such that a single heat pump is designed to provide heating for the dry cycle and for generating hot water. The device will include an internal heat exchanger and storage component capable of recovering waste heat between the wash and dry cycles. | R: Adv Washer-Dryer Pair | System | 5 | 2 | Residential | Washing & Drying | All CW and DW | Wet Cleaning, Residential and commercial | Energy Savings (%) | 40% | 0 | Yes | $2.5-$3.5k DOE target | 1200 | 3000 | 1800 | per pair | 54 R: No FS: Total clothes washing, clothes drying and water heating energy | Total residential clothes washing, drying, and water heating energy consumption | 12 | 2014 | Confidential White Paper and confidential discussion with ORNL CRADA partner Primary Source: Personal communication: Bouza, DOE (1/2012) | No notes | 1-158 | 12 | 12 | AEO 2014 NEMS
719 | Optimize whole-building control system (new software) that controls the operation of multiple systems to minimize costs based on a variety of inputs, such as occupancy, weather, fuel prices, etc. This measure is applicable to systems in large buildings (>100,000 sq.ft.) with poorly performing control systems. It also includes retro-commissioning (adjustment of thermostats, schedules, set points, calibration. It does not include equipment replacement (bad sensors, frozen dampers, etc.)) - will be an extra cost. | C: Bldg Control Opt. (>100,000SF) | Controls | 5 | 3 | Commercial | HVAC/Lighting | Building controls | All large commercial building energy (>100,000 ft2) | Energy Savings (%) | 20% | 0% | Yes | For buildings > 100,000 SF, EMCS cost (assuming similar to EIS) of $1.36/sq.ft. (TIAX). Automatic optimization software to achieve similar savings would cost an additional $100,000 per 100,000 sq.ft. more, to a total incremental cost of $2.36/sq.ft. (EMCS+OWBCS combined) | 0 | 2.36 | 2.36 | per square foot | 14 C: No FS: HVAC and lighting | All HVAC and Lighting in commercial buildings >100,000 ft2 | 10 | 2013 | 1) Savings and costs from pg. 9-91,93,95,139 of TIAX. Energy Impact of Commercial Building Controls and Performance Diagnostics: Market Characterization, Energy Impact of Building Faults and Energy Savings Potential. November 2005. “Overall, it would appear that the first cost of an OWBCS associated with an EMCS would be similar to the cost of a higher-end Whole Building Diagnostics implementation less the cost of additional sensors, i.e. on the order of $100,000.” Adding the costs of the EMCS, which is assumed to be similar to EIS of $1.36/sq.ft (pg. 9-136), and the OWBCS for a 100,000 sq.ft. building gives a cost of $2.36/sq.ft. | TIAX: "Heating: 10%, Cooling 20%, Ventilation 0%." "Overall it would appear the first cost of an OWBCS associated with an EMCS would be similar to the cost of a higher-end Whole Building Diagnostics implementation less the cost of additional sensors, i.e., on the order of $100,000" Installed cost of an EIS for a 100,000 ft2 office building was $136,000. Assumes an EMS is required ($136,000) plus an additional $100,000 for the OWBCS controls/sensors/software. Assumes 20% savings for EMS alone followed by 10% for OWBCS. | 3-3469 | 10 | 10 | AEO 2010 NEMS
720 | Outside air damper automated fault detection and diagnostics (AFDD) | C: Outside-Air Damper AFDD | Controls | 3 | 3 | Commercial | Heating & Cooling | Building controls | RTUs, commercial | Energy Savings (%) | 10% | 0% | Yes | $30 per RTU (assumes digital RTU controls/sensors) | 0 | 0.014286 | 0.014286 | per square foot; 7.5 tons/RTU, 280 ft^2/ton | 1 C/R: No FS: All electric to all electric | Total commercial cooling by rooftop AC units (RTUs) | 15 | 2013 | TIAX. Energy Impact of Commercial Building Controls and Performance Diagnostics?: Market Characterization , Energy Impact of Building Faults and Energy Savings Potential. Construction 413 (2005). | BTO Tool: Assumes an EMS is present and the RTU already has direct digital controls. Assumes 20% savings per RTU, and 50% of RTUs have malfunctioning dampers. Assumes necessary repairs are low-cost (remove obstruction, lubricate). Appendix B: ~$30 per RTU or AHU, 7.5 tons/RTU, 280 ft2/ton, new equipment only. 20% savings if there's a damper failure, 35% of dampers are malfunctioning. | 3-3681 | 15 | 15 | AEO 2010 NEMS
721 | Rooftop Unit (RTU) fault detection and diagnostics | C: RTU AFDD | Controls | 4 | 2 | Commercial | Heating & Cooling | Building controls | RTUs, commercial | Energy Savings (%) | 9% | 0% | Yes | $80 per RTU (assumes an existing EMS) | 0 | 0.038095 | 0.038095 | per square foot; 7.5 tons/RTU, 280 ft^2/ton | 1 C/R: No FS: All electric to all electric | Total commercial cooling by rooftop AC units (RTUs) | 15 | 2015 | TIAX. Energy Impact of Commercial Building Controls and Performance Diagnostics: Market Characterization , Energy Impact of Building Faults and Energy Savings Potential. Construction 413 (2005). | BTO Tool: Assumes an EMS is present. Assumes 20% savings per RTU, and 35% of RTUs have malfunctioning dampers. Maintenance savings are not included, because energy savings potential seems to depend on poor maintenance . Assumes necessary repairs are low-cost (remove obstruction, lubricate).practices. Appendix B: Energy savings from TIAX (9% = 0.075 Quads/0.8 Quads). $80 per RTU, 7.5 tons/RTU, 280 ft2/ton. Assumes an EMS is present. Maintenance savings and necessary repairs are neglected. Upon reviewing Sam Jasinski's feedback and Jim Braun and Srinivas feedback, where they propose to update savings estimate to 15%-20% for #721. However, the 9% was not changed because it is assumed that 15-20% would be savings obtained from fixing an RTU that has failed, however, because not all RTU's have failures that contribute to energy losses and we cannot model various failure rates using P-tool's capabilities, it is assumed 9% savings can be obtained throughout the entire RTU market, without having to account for failure rates. | 3-3681 | 15 | 15 | AEO 2010 NEMS
722 | Automated whole-building diagnostics (AWBD) | C: Automated whole building diagnostics | Controls | 5 | 2 | Commercial | HVAC/Lighting | Building controls | Heating, cooling, lighting, half of refrigeration | Energy Savings (%) | 12.5% | 0% | Yes | $136000 for a 100,000 ft2 office building | 0 | 2.04 | 2.04 | per square foot | 61 Manual | HVAC, lighting, and half of refrigeration | 20 | 2015 | TIAX. Energy Impact of Commercial Building Controls and Performance Diagnostics?: Market Characterization , Energy Impact of Building Faults and Energy Savings Potential. Construction 413 (2005). | BTO Tool: Approximately the same cost as a new EMS. Since the baseline doesn't have an EMS, it is assumed the total cost is about the same as 1.5 EMS. Appendix B: "it could reduce building energy consumption by 5-20%" The average of 5% and 20% was used. Cost estimated to be the same as 1.5 EMS (1.5*$1.36/ft2) (see Measure 719). The baseline is assumed to have no EMS. | 3-3470 | 20 | 20 | AEO 2010 NEMS
723 | Packaged HVAC controls for existing buildings (economizer, multi-speed fan and capacity control, demand control ventilation) | C: Packaged HVAC Controls (Retrofit) | Controls | 3 | 3 | Commercial | Heating & Cooling | Building controls | RTUs and other packaged systems, commercial | Energy Savings (%) | 30% | 0% | Yes | See existing & efficient costs | 0 | 1.32 | 1.32 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | Total commercial HVAC (HP and RTU) in all existing buildings | 15 | 2015 | W Wang, Y Huang, S Katipamula, MR Brambley. 2011. Advanced Controls for Existing Packaged A/C with gas heating. PNNL 20995. http://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20955.pdf | BTO Tool: Assumes no economizer and constant speed fans. Cost estimate of $1.32/ft2 was based on sum of component measures (129, 141, 101, 104, 722). Only half the cost of an EMS was included because of likely double-counting. Appendix B: Wang: "The results from detailed simulation analysis show significant energy (24% to 35%) and cost savings (38%) from fan, cooling and heating energy consumption when packaged units are retrofitted with advanced control packages." The average energy savings (30%) was used. Cost of $1.32/ft2 based on sum of component measures (129, 141, 101, 104, 722). Only half the cost of an EMS was included because of synergies. | 3-3756 | 15 | 15 | AEO 2010 NEMS
724 | Improve duct sealing in new small commercial buildings beyond code | C: Duct Sealing beyond code (S) | Distribution | 5 | 3 | Commercial | Building | Ducts | New | Energy Savings (%) | 5% | 0% | Yes | $0.33/sq.ft of floor space |  |  | 0.33 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | Commercial heating and cooling in small new buildings (<10,000 ft2) | 20 | 2013 | Aeroseal website: http://www.aeroseal.com/commercial_duct_sealing.html; Modera 2005: Fixing Duct Leaks, ASHRAE Journal; Primary Source: Modera, M Fixing Duct Leaks in Commercial Buildings ASHRAE Journal June 2005 ASHRAE. 2010. Energy Standard for Buildings Except Low-Rise Residential Buildings. ASHRAE 90.1 2010. | Expected & new equipment lifetime value are based on an assumption that these last 20 years. We do not have a good source to support this assumption. BTO Tool: Assumes same cost as Measure 92. Aeroseal isn't necessary to meet code, but is assumed for 5% improvement beyond code. Assumes Level A sealing level for all ducts in unconditioned space. ASHRAE 90.1 only requires Level A for supply ducts in unconditioned space, not for supply ducts in conditioned space or return ducts in unconditioned space. Level A includes sealing of all duct penetrations, while Level B does not. Given that Level A doesn't affect the most serious leakage (high pressure supply leakage in unconditioned space), savings in the range of 5% of heating and cooling energy is assumed (50% reduction in 10% of leakage outside conditioned space in code compliant new buildings). Appendix B: Modera: 80% heating season duct efficiency (See Figure 2 and measured duct efficiency data cited throughout the article. For light commercial, the duct efficiency is about 80% in half the buildings (where the ducts are in a ceiling plenum outside the thermal boundary). ASHRAE: "Ductwork and all plenums with pressure class ratings shall be constructed to seal class A, as required to meet the requirements of Section 6.4.4.2.2…" Price same as Measure 92. Aeroseal isn't necessary to meet code, but is assumed for 5% improvement beyond code. Given that the code already addresses the most serious leakage (high pressure supply leakage in unconditioned space), savings in the range of 5% is assumed (50% reduction in 10% of leakage outside conditioned space in code compliant new buildings). | 3-3759 | 20 | 20 | AEO 2010 NEMS
725 | Duct sealing in small existing commercial buildings | C: Duct Sealing (E,S) | Distribution | 5 | 3 | Commercial | Building | Ducts | Retrofits | Energy Savings (%) | 5% | 0% | Yes | $0.33/sq.ft of floor space |  |  | 0.33 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | Commercial heating and cooling in small existing buildings (<10,000 ft2) | 20 | 2013 | Aeroseal website: http://www.aeroseal.com/commercial_duct_sealing.html; Modera 2005: Fixing Duct Leaks, ASHRAE Journal; Primary Source: Modera, M Fixing Duct Leaks in Commercial Buildings ASHRAE Journal June 2005 | Expected & new equipment lifetime value are based on an assumption that these last 20 years. We do not have a good source to support this assumption. BTO Tool: Assumes same cost as Measure 92 (Aeroseal). Assumes 5% heating and cooling savings (50% reduction in 20% duct losses in 50% of small buildings) Appendix B: Modera: 80% heating season duct efficiency (See Figure 2 and measured duct efficiency data cited throughout the article. For light commercial, the duct efficiency is about 80% in half the buildings (where the ducts are in a ceiling plenum outside the thermal boundary). Calculated 5% heating and cooling savings (50% reduction in 20% duct losses in 50% of small buildings). Price same as Measure 92. | 3-3757 | 20 | 20 | AEO 2010 NEMS
726 | Duct sealing in large existing commercial buildings | C: Duct Sealing (E,L) | Distribution | 5 | 3 | Commercial | Building | Ducts | Retrofits | Energy Savings (%) | 16% | 0% | Yes | $0.33/sq.ft of floor space |  |  | 0.33 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | Commercial heating and cooling in large existing buildings (>10,000 ft2) | 20 | 2013 | Aeroseal website: http://www.aeroseal.com/commercial_duct_sealing.html; Modera 2005: Fixing Duct Leaks, ASHRAE Journal; Primary Source: Modera, M Fixing Duct Leaks in Commercial Buildings ASHRAE Journal June 2005. Other Supporting Sources: Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. 289 (2011). | Expected & new equipment lifetime value are based on an assumption that these last 20 years. We do not have a good source to support this assumption. BTO Tool: Assumes same cost as Measure 92 (Aeroseal). Assumes 21% reduction in ventilation end-use (fan energy reduced based on reduction in leakage from 15% to 7.5% and exponent of 2.4 from Modera 2005). Appendix B: Modera: "Using the power 2.4 from Franconi et al.,5 a 15% leak translates to a 40% increase in fan power." "Researchers at Lawrence Berkeley Laboratory measured duct leakage in six large commercial buildings, three of which showed 5% leakage, while the other three showed 15%, 17% and 25% supply duct leakage." Assumes 16% savings based on reduction in leakage from 15% to 7.5% and exponent of 2.4. Assumes 50% reduction in leakage rate due to aerosol sealing. Assumes same cost as Measure 92. | 3-3758 | 20 | 20 | AEO 2010 NEMS
727 | Low lift chiller system | C: Low lift cooling system (N) | System | 5 | 2 | Commercial | Cooling | A/C | Vapor-compression cooling systems in chillers and rooftop AC units, commercial | Energy Savings (%) | 40% | 0% | No | $0.58 savings for small offices, $0.70 for large offices |  |  | 0.7 | per square foot | 1 C/R: No FS: All electric to all electric | Total electric cooling and ventilation in new office buildings | 15 | 2015 | Katipamula, S. Pacific Northwest National Laboratory. "Cost-Effective Integration of Efficient Low-Lift Baseload Cooling Equipment: FY08 Final Report", PNNL-19114 (http://www.pnl.gov/main/publications/external/technical_reports/PNNL-19114.pdf) | BTO Tool: Market is all new office buildings. Used large office incremental costs to be a little conservative. Economics appear to be better if RTU is replaced. Energy savings for cooling and ventilation/fans based on Case 1 to Case 8, national average, large office buildings. Appendix B: Large office incremental costs. Energy savings for cooling and ventilation/fans based on Case 1 to Case 8, national average, large office buildings. | 3-3760 | 15 | 15 | AEO 2010 NEMS
732 | Tasklighting | C: Tasklighting | Use Intensity | 5 | 4 | Commercial | Lighting | Lighting | All | Energy Savings (%) | 50% | 0% | Yes |  |  |  | 1.96 | per square foot | 1 C/R: No FS: All electric to all electric | Total task lighting in all commercial buildings | 5 | 2012 | http://www.etcc-ca.com/images/pge0820.pdf, http://cltc.ucdavis.edu/content/view/673/359/ Primary Source: California Lighting Technology Center. (n.d.). Integrated Office Lighting System (IOLS) . Retrieved from Demonstration: http://cltc.ucdavis.edu/content/view/673/359/ Other Supporting Sources: Heschong Mahone Group, Inc. (2009). Small Office ("Encon" Building) Site Report. Pacific Gas and Electric Company. | BTO Tool: Incremental cost is referenced to "T-24, 2008 system" Appendix B: "Energy savings: 50% annual energy savings; over 15 years, one system can yield savings of 7,500 kWh" | 3-3776 | 5 | 5 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
738 | Conventional commercial Liquid Desiccant Air Conditioner (LDAC) | C: Conventional LDAC | System | 5 | 4 | Commercial | Cooling | A/C | Central | Energy Savings (%) | 40% | 0% | Yes | 1.6-5 year ROI from multiple cas studies; set incremental to 5 year ROI | 12000 | 15000 | 0.5 | per square foot | 10 C: No FS: All fuels cooling (elec+NG) | Total cooling in humid climates by all commercial RTUs | 15 | 2011 | http://www.nrel.gov/features/20100611_ac.html Primary Source: Sachs, H..; Lin, W.; Lowenberger, A.; "Emerging Energy Savings HVACTechnologies and Practices for the Buildings Sector"; ACEEE, 2009 DuCool Case Studies, Advantix Company presentations (publically available, 2011) Other Supporting Sources: Choi-Granade et. Al.; "Unlocking Energy Efficiency in the U.S. Economy"; McKinsey & Company (2009) | BTO Tool: MTAB, NREL website, DuCool?AdvantixSystems website Appendix B: Percent savings 66% elec; 85% gas (ACEEE). DuCool observed savings 35%-70% depending on configuration Most comparable case study to hot-humid climate suggests 40% savings. Cost given DuCool payback times. Note: excluded from the UBER/active cascade due to market barriers. | 3-3722 | 15 | 15 | AEO 2010 NEMS
739 | Conventional residential Liquid Desiccant Air Conditioner (LDAC) | R: Conventional LDAC | System | 5 | 3 | Residential | Cooling | A/C | Central | Energy Savings (%) | 40% | 0% | Yes | Used incremental/sqft from above scaled to 2200 | 4680 | 5780 | 1100 | per home; 3 ton | 1 C/R: No FS: All electric to all electric | Total residential central cooling in humid climates | 17 | 2011 | http://www.nrel.gov/features/20100611_ac.html Primary Source: Sachs, H..; Lin, W.; Lowenberger, A.; "Emerging Energy Savings HVACTechnologies and Practices for the Buildings Sector"; ACEEE, 2009 DuCool Case Studies, Advantix Company presentations (publically available, 2011) Other Supporting Sources: Choi-Granade et. Al.; "Unlocking Energy Efficiency in the U.S. Economy"; McKinsey & Company (2009) | BTO Tool: MTAB, NREL website, DuCool?AdvantixSystems website Appendix B: Percent savings 66% elec; 85% gas (ACEEE). DuCool observed savings 35%-70% depending on configuration Most comparable case study to hot-humid climate suggests 40% savings. Cost given DuCool payback times Note: excluded from the UBER/active cascade due to market barriers. | 1-9 | 17 | 17 | AEO 2014 NEMS
741 | Increase roof insulation to R-30 continuous or R-49 cavity for new commercial buildings | C: Highly Insulating Roofs (N) (MYP2025)* | Roof | 5 | 0 | Commercial | Building | Roof/ attic insulation | New | R-value | 30 | 15 | Yes | MYP goal of $1/sq.ft incremental cost over a standard roof | 0.81667 | 1.15 | 0.33333 | per square foot; assumes an average of 3 floors/building | 37 C: No FS: Roof specific | Total heating and cooling loads through attics in new commercial buildings | 40 | 2025 | 50% Grocery Store TSD (http://www.nrel.gov/docs/fy09osti/46101.pdf), 50% Large Office TSD (http://www.nrel.gov/docs/fy10osti/49213.pdf), 50% Medium Box Retail (http://www.nrel.gov/docs/fy08osti/42828.pdf) Primary Source: Leech, M. et. al.; "Grocery Store 50% Energy Savings Technical Support Document", National Renewable Energy Laboratory (2009) Leech, M. et. al.; "Technical Support Document: Strategies for 50% Energy Savings in Large Office Buildings", National Renewable Energy Laboratory (2010) Hale E. et. al.; "Technical Support Document: Development of the Advanced Energy Design Guide for Medium Box Retail—50% Energy Savings", National Renewable Energy Laboratory (2008) | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: Based on upgrade from R-15 to R-30 c.i., cost is average of all 3 TSDs Appendix B: Costs and performance drawn from upgrading ASHRAE code roof insulation to most cost effective point from indicated source R-15 to R-30 upgrade, $0.88/sqft average cost | 3-3763 | 40 | 40 | AEO 2010 NEMS
742 | Optimize window placement, orientation, and properties for daylighting | C: Optimize Windows for Daylight (N) | Windows | 5 | 4 | Commercial | Lighting | Windows | New | Energy Savings (%) | 8% | 0% | Yes | No added first cost except increase in design/modeling costs ($30K) | 0 | 0.15 | 0.15 | per square foot; 200,000 ft^2 ave. building | 1 C/R: No FS: All electric to all electric | All fluorescents, new commercial | 40 | 2013 | Estimate based on experience of NREL Commercial Buildings Group (both energy savings and modeling costs) Primary Source: Hendron, R. Senior Engineer - National Renewable Energy Laboratory Commercial Buildings Group. Personal communications. | BTO Tool: Assumes that the savings for daylighting is doubled over controls/dimmers alone. Savings is the same as Measure 181, but market is all fluorescent lighting instead of just the perimeter zone. No added first cost except increase in design/modeling costs ($30K) | 3-3474 | 40 | 40 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
743 | Install skylights to enhance daylighting | C: Add skylights (N) | Windows | 5 | 4 | Commercial | Lighting | Skylights | New | Energy Savings (%) | 7.6% | 0% | Yes | 3% of roof area for 45,000 ft2 grocery store @ $45.8/ft2 (Grocery TSD) | 0 | 1.374 | 1.374 | per square foot; 45,000 ft^2 ave. grocery store | 1 C/R: No FS: All electric to all electric | All fluorescents, new commercial | 40 | 2013 | Leach, M., Hale, E., Hirsch, A. & Tocellini, P. Grocery Store 50 % Energy Savings Technical Support Document Grocery Store (2009). http://www.nrel.gov/docs/fy09osti/46101.pdf | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: Assumes skylights contribute 50% of total daylighting energy savings in the TSD. Average of Miami, Chicago, and Seattle used. Appendix B: 3% of roof area for 45,000 ft2 grocery store @ $45.8/ft2. $1.37/ft2 = 0.03%*$45.8/ft2. Energy savings assumes skylights contribute 50% of total daylighting energy savings. Average of Miami, Chicago, and Seattle. | 3-3474 | 40 | 40 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
744 | Require use of controllable power outlets that are turned off during unoccupied hours using timer control | C: Controllable power outlets (N) | Controls | 5 | 4 | Commercial | MELs | Building controls | New | Energy Savings (%) | 19% | 0% | Yes | $87,500 for a 50,000 ft2 retail store (Retail TSD) | 0 | 1.75 | 1.75 | per square foot; 50,000 ft^2 retail store | 1 C/R: No FS: All electric to all electric | All plug loads in new commercial buildings | 20 | 2013 | E.T. Hale, D.L. Macumber, N.L. Long, B.T. Griffith, K.S. Benne, S.D. Pless, and P.A. Torcellini. 2008. Technical Support Document: Development of the Advanced Energy Design Guide for Medium Box Retail—50% Energy Savings. (http://www.nrel.gov/docs/fy08osti/42828.pdf) | Expected lifetime is assumed - we do not have a good source to support this assumption.BTO Tool: Assumes reduction from 40% to 15% MELs operation during unoccupied hours Appendix B: Energy savings and cost from Hale et al. $87,500 for a 50,000 ft2 retail store. Assumes reduction from 40% to 15% MELs operation during unoccupied hours | 3-3477 | 20 | 20 | AEO 2010 NEMS
746 | Add R-10 continuous roof insulation to existing commercial buildings | C: R-10 Roof Insulation (E) | Roof | 5 | 4 | Commercial | Building | Roof/ attic insulation | Retrofits | R-value | 24 | 14 | Yes | $1,082,915 for 210,800 ft2 school | 1023057 | 1082915 | 0.28396 | per square foot; 210,800 ft^2 school | 37 C: No FS: Roof specific | Total heating and cooling loads through attics in all existing commercial buildings | 40 | 2013 | AERG for K-12 Schools (unpublished) Primary Source: NREL. 2011. Advanced Energy Retrofit Guide for K-12 Schools (Draft). EERE Report DOE/GO-102011-3467. Project Lead: Robert Hendron | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: Assumes roof replacement is needed. Not close to cost-effective if roof is relatively new. Cost based on removing old roof assembly and replacing insulation with 6-in EPS (R-24). Appendix B: $108,2915 total cost, $59,858 incremental cost for replacing insulating sheathing with R-24 for 210,800 ft2 school in Chicago, Assumes roof is being replaced anyway. Energy savings based on increasing R-14 to R-24 EPS. | 3-3764 | 40 | 40 | AEO 2010 NEMS
747 | Install tubular daylighting devices for interior spaces, and add photosensor controls and dimming ballasts | C: TDDs and Controls (E) | Windows | 5 | 4 | Commercial | Lighting | Skylights | Retrofits | Energy Savings (%) | 21% | 0% | Yes | $1.9 million for 210,800 ft2 school | 0 | 8.5025 | 8.5025 | per square foot; 210,800 ft^2 school | 1 C/R: No FS: All electric to all electric | All fluorescents, existing commercial | 40 | 2013 | AERG for K-12 Schools (unpublished) Primary Source: NREL. 2011. Advanced Energy Retrofit Guide for K-12 Schools (Draft). EERE Report DOE/GO-102011-3467. Project Lead: Robert Hendron | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: Average energy savings and price for five climates in AERG. Includes effect on HVAC. Appendix B: $1.79 million for TDDS, controls, and dimming ballasts. Analysis based on a typical 210,800 ft2 high school. | 3-3475 | 40 | 40 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
748 | Use a stack economizer to recover waste heat from flue gases | C: Stack economizer [E] | System | 5 | 4 | Commercial | Heating | Boilers | Retrofits | Energy Savings (%) | 5% | 0% | Yes | $27,400 for two boilers (1000 hp) |  | 0.76202 | 0.76202 | per square foot; 5000 kW boiler, 241,000 ft2 ave. hospital | 11 C: No FS: Boiler heating (elec+NG+oil) | Space heating using boiler in all existing commercial buildings | 30 | 2013 | Energy savings from AERG for Healthcare Facilities (unpublished), cost estimated from Kemco case study (http://www.kemcosystems.com/Case-Studies/Food-Stack.html) Primary Source: NREL. 2011. Advanced Energy Retrofit Guide for Healthcare Facilities (Draft). Project Lead: Robert Hendron Kemco case study. Boiler Stack Economizer - Provides A 3 ½ Month ROI. (http://www.kemcosystems.com/Case-Studies/Food-Stack.html) | BTO Tool: DQ 0: not cost effective; Healthcare AERG estimates a few percent improvement in boiler efficiency, assumed to be about 5%. Appendix B: Energy savings from NREL 2011, which estimates a few percent improvement in boiler efficiency. Cost estimated from Kemco: "...annual savings was estimated at $32,880 with a 10 month payback." $27,400 for two boilers (5000 kW total), $36.73/kW, 241,000 ft2 ave. hospital. | 3-3765 | 30 | 30 | AEO 2010 NEMS
753 | Distribution Transformers - Dry, Low efficiency improvement | C: Dry distribution transformers, Low | Use Intensity | 5 | 4 | Commercial | MELs | Distribution Transformer | Commercial | Energy Savings (%) | 31.91% | 0% | No |  |  |  |  | per unit | 1 C/R: No FS: All electric to all electric | All dry distribution transformers (mmBTUs, site) | 32 | 2013 |  |  | 3-3767 | 32 | 32 | AEO 2010 NEMS
754 | Distribution Transformers - Dry, Medium-Low efficiency improvement | C: Dry distribution transformers, Medium-Low | Use Intensity | 5 | 4 | Commercial | MELs | Distribution Transformer | Commercial | Energy Savings (%) | 44.6% | 0% | No |  |  |  |  | per unit | 1 C/R: No FS: All electric to all electric | All dry distribution transformers (mmBTUs, site) | 32 | 2013 |  |  | 3-3767 | 32 | 32 | AEO 2010 NEMS
756 | Dry type distribution transformers (1- & 3-phase; design levels 6-13b, TSD 2013) efficiency improvement to TSL 5 of 6 total levels (44%-70% or 61% weighted average reduction in losses compared to a baseline transformer established prior to 2013 DT standard; OR ~39% reduction in losses compared to 2013 DT standard (weighted average of 22% over baseline) (TSL 1)) | C: High Eff. Dry Distr. Transformers (TSL 5 of 6) | Use Intensity | 5 | 4 | Commercial | MELs | Dry-type distribution transformers | Commercial | Energy Savings (%) | 60.95% | 0% | No | Cost is a weighted average based on MVA capacity shipped in 2009 from 2013 TSD. No cost data was found for dry type low voltage transformers, hence only the medium voltage cost was considered (low dry-type DT are significantly most common). | 25313.5028 | 43756.4972 | 18442.9944 | per MVA | 1 C/R: No FS: All electric to all electric | All dry distribution transformers (mmBTUs, site) | 32 | 2013 | 1) Energy saving were obtained from weighted average of % savings from TSL levels set in 2013 Standards. The Excel file was saved in supporting documents. 2) The weighted average for incremental cost was obtained from 2013 Standard TSD: Table 10.3.1 First Cost of DT by Trial Standard Level and Product Class (2006$/kVA, Baseline and TSL 1 - TSL 6) located on page 10-17. 3) Shipment data to obtain weighted averages for costs and savings is from 2012 NOPR presentation by James Raba during 2013 standard rulemaking. The PPT file was saved in supporting documents. | Cost is a weighted average based on MVA capacity shipped in 2009 from 2013 TSD. No cost data was found for dry type low voltage transformers, hence only the medium voltage cost was considered (low dry-type DT are significantly most common). | 3-3767 | 32 | 32 | AEO 2010 NEMS
759 | Reduce/increase temperature set-point 1 F in heating/cooling season | R: Change inside temp 1F | Use Intensity | 5 | 4 | Residential | HVAC | Behavior | Residential | Energy Savings (%) | 5% | 0% | Yes | 0 |  |  | 0 | per home | 5 R: No FS: All fuels HVAC (heating+cooling, no separate ventilation component) | Total residential heating and cooling in all homes | 1 | 2013 | EIA Brief (1997): Winter Energy Savings from Lower Thermostat Settings Primary Source: Berry, C; Swenson, A; "Winter Energy Savings from Lower Thermostat Settings", EIA Brief (2000) | Appendix B: Natural Gas. Households whose main space-heating fuel was natural gas would have consumed 5 percent less natural gas for space heating and would have spent $22 less (for the entire year of 1997) if they had set their thermostat 1° F lower | 1-132 | 1 | 1 | AEO 2014 NEMS
760 | Reduce/increase temperature set-point 1 F in heating/cooling season | C: Change inside temp 1F | Use Intensity | 5 | 4 | Commercial | HVAC | Behavior | Commercial | Energy Savings (%) | 5% | 0% | Yes | 0 |  |  | 0 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | All commercial HVAC energy use | 1 | 2013 | EIA Brief (1997): Winter Energy Savings from Lower Thermostat Settings Primary Source: Berry, C; Swenson, A; "Winter Energy Savings from Lower Thermostat Settings", EIA Brief (2000) | Appendix B: Natural Gas. Households whose main space-heating fuel was natural gas would have consumed 5 percent less natural gas for space heating and would have spent $22 less (for the entire year of 1997) if they had set their thermostat 1° F lower | 3-3617 | 1 | 1 | AEO 2010 NEMS
765 | Advanced RTU (CRADA) | C: RTU (IEER 20) | System | 5 | 3 | Commercial | Cooling | RTU | Central | IEER | 20 | 11.4 | Yes | Installed $8525 for standard unit; and $23,500 for high efficiency unit. | 0.8525 | 2.35 | 1.4975 | per square foot; 10 RTU's per 100k sq.ft | 1 C/R: No FS: All electric to all electric | Total commercial cooling by rooftop AC units (RTUs) | 15 | 2014 | 1) IEER=20 units available from McQuay and Carrier, although not for all capacity ranges. http://www.go.mcquay.com/rebel, http://www.carrierweatherexpert.com/downloads/6-10-tons/catc_10003_brochure_weatherexpert_rtus_hirez_spreads.pdf 2) Cost assumes a typical RTU size of 7.5 tons: from EIA Tech Forecast 2013. Also, DOE funded target: $9-10,000 for highest IEER unit. (Bouza) & pg. 28 of Advanced RTU Campaign. Webinar. Better Buildings. US DOE. June 17, 2013. 3) ) |  | 3-3681 | 15 | 15 | AEO 2010 NEMS
766 | Demonstrate, deploy, and develop tools for designing cost effective high performance commercial buildings | C: 50% building, modeling cost only | Whole building | 5 | 3 | Commercial | All End Uses | Whole building | New | Energy Savings (%) | 50% | 0% | No | No equipment cost, just $30k for 210k sq.ft. |  | 0.14286 | 0.14286 | per square foot; 210,000 sq.ft. ave. building | 60 C: No FS: All fuels/end-uses | All energy consumption in new buildings | 40 | 2013 | "General Merchandise 50% Energy Savings Technical Support Document" (http://www.nrel.gov/docs/fy09osti/46100.pdf) and "Technical Support Document: Strategies for 50% Energy Savings in Large Office Buildings" (http://www.nrel.gov/docs/fy10osti/49213.pdf) | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 3-3633 | 40 | 40 | AEO 2010 NEMS
767 | Thermotunneling cooling systems - TARGET | R: Thermotunneling cooling systems* | System | 5 | 0 | Residential | Cooling | RTU and HP | Residential cooling - RTU and HP | Energy Savings (%) | 10% | 0% | Yes | $5000 (p. 78, NCI Comm HVAC report) | 4167 | 5000 | 833 | per unit; 3 ton model | 1 C/R: No FS: All electric to all electric | Residential Cooling (HP & RTU), 100% New, 50% Old | 16 | 2017 | Brown, DR. et al. “The Prospects of Alternatives to Vapor Compression Technology for Space Cooling and Food Refrigeration Applications.” PNNL-19259. PNNL. March 2010. Prepared for the U.S. DOE under contract DE-AC05-76RL01830. Sachs, H. et al. “Emerging Energy-Saving Technologies and Practices for the Building Sector as of 2004.” October 2004. Report Number A042. ACEEE. Weaver, Stan et al. “Thermotunneling Based Cooling Systems for High Efficiency Buildings.” Final Technical Report. GE Global Research. DE-FC26-04NT42324. Cool Chips PLC, Presentation. “Cool Chips – Technical Overview.” http://www.coolchips.gi/technology/Coolchipstech3Jan06.pdf Cool Chips PLC, Website. http://www.coolchips.gi/about.shtml Primary Source: Goetzler, W., Zogg, R., Burgos, J., Hiraiwa, H. & Young, J. Energy Savings Potential and RD & D Opportunities for Commercial Building HVAC Systems. 289 (2011). (pg. 78, cost and % savings) | Deployment level of 1 was changed based on Brown, et al. The prospects of alternative to vapor compression technology for space cooling and food refrigereation applications. 2010. report, which states a prototype has not yet been developed that can show % efficiency increase during cooling. Appendix B: "Applied to relevant annual energy consumption by increasing system efficiency by 10%." Premium of 20% ($1.07/ft2) based on $9000, 5-ton system, 280 ft2/ton. Largely based on commercial thermotunneling cooling systems, measure 689 | 1-31 | 16 | 16 | AEO 2014 NEMS
768 | Install heat-resistant radiator reflectors between exterior walls and radiators | R: Install radiator reflectors | Use Intensity | 4 | 4 | Residential | Heating | Radiator reflector | Hydronic | Energy Savings (%) | 10% | 0% | Yes | ~$250 for 8 radiators in std. house | 250 | 0 | 250 | per home; 8 reflectors per home | 1 C/R: No FS: All electric to all electric | Total residential cooling by CAC and ASHPs as well as ASHP heating | 15 | 2010 | Novitherm website, calculation, and cost estimation tools | Appendix B: Assumes 8 radiators to treat per home, 10% savings in heating | 1-178 | 15 | 15 | AEO 2014 NEMS
775 | Close blinds/curtains/drapes/shades during the day when cooling your home especially on south and west-facing windows | R: Close blinds | Windows | 5 | 3 | Residential | HVAC | Blinds | All | Energy Savings (%) | 16% | 0% | Yes | $55/blind for automation, 0 DIY |  |  | 440 | per home; 8 south facing blinds | 30 R: No FS: Window (cond+rad) specific | Total cooling lost due to solar gain through residential windows that can benefit from attachments (assuming 50% of homes have windows that can benefit from advanced attachments (beyond typical blinds or curtains which may not be properly utilized for greater savings) | 1 | 2010 | Cho, S.-hwan, Shin, K.-S. & Zaheer-Uddin, M. The Effect of Slat Angle of Windows With Venetian Blinds on Heating and Cooling Loads in South Korea. Energy 20, 1225-1236 (1995) | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Appendix B: "Results show that the use of windows with Venetian blinds can reduce the building heating load by about 5% and cooling loads by as much as 30%" Used conservative weighted average of savings range | 1-117 | 1 | 1 | AEO 2014 NEMS
776 | Close blinds in commercial buildings | C: Close blinds | Use Intensity | 5 | 3 | Commercial | HVAC | Blinds | All | Energy Savings (%) | 16% | 0% | Yes | $55/blind for automation, 0 DIY |  |  | 0.1375 | per square foot; one unit per 6x6 window on south face | 33 C: No FS: Window (cond+rad) specific | All commercial windows that can benefit from attachments in pre-2010 buildings | 10 | 2010 | Cho, S.-hwan, Shin, K.-S. & Zaheer-Uddin, M. The Effect of Slat Angle of Windows With Venetian Blinds on Heating and Cooling Loads in South Korea. Energy 20, 1225-1236 (1995) | Appendix B: "Results show that the use of windows with Venetian blinds can reduce the building heating load by about 5% and cooling loads by as much as 30%" Used conservative weighted average of savings range | 3-3768 | 10 | 10 | AEO 2010 NEMS
777 | Develop integrated roofing package for existing homes in hot climates (with duct benefits) using phase change material (PCM) for R-75 equivalent (DOE FOA Target) | R: R-75 PCM Roof, hot CZ [E]* | Roof | 5 | 2 | Residential | Building | Roof | All homes | Energy Savings (%) | 35% | 0% | Yes | $2.30/sq-ft; asumed $1.00 premium for retrofit; UPDATE (FOA TARGET): $300 per 100 SF |  | 4156.9219 | 4156.9219 | per home; 30x40 home, 2 stories, 10' per story | 1 C/R: No FS: All electric to all electric | Total central cooling in all existing single-family homes in hottest two climates | 30 | 2025 | Miller, W. & Kosny, J. Next-Generation Roofs and Attics for Homes. ACEEE Summer Study on Energy Efficiency in Buildings 180-195 (2008); FOA TARGET | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Appendix B: Analyzed savings for ducts and attic loads scaled to national average using new codes as base | 1-32 | 30 | 30 | AEO 2014 NEMS
782 | Commercial CHP, serving all heating load using a CHP system and displacing some of the electrical end use | C: CHP, EPA (2), 47% heat, 24.6% electricity | CHP | 5 | 4 | Commercial | Heating | CHP | All Commercial Heating | Energy Savings (%) | 71.6% | 55.47% | Yes | $2490/kW |  |  | 56.5377 | per square foot; 1 ton per 280 square foot | 2 C/R: No FS: All gas to all gas | CHP Commercial Buildings | 20 | 2012 | EPA Technology Characterization: Microturbines. Prepared for EPA by ICF International. 2008. | 47% heating; 24.6% electric | 3-3778 | 20 | 20 | AEO 2010 NEMS
785 | Install PVT Collectors on Commercial Roofs to Meet Hot Water Demand and Supply Site Renewable Energy | C: PVT Collectors | Other | 3 | 4 | Commercial | Water Heating | Hybrid Solar PV/T Collector | Commercial HW and Electricity Gen | Energy Savings (%) | 79.4% | 0% | No | $114,000 for 30,000 kWh Electricity and 4262 therms of NG (equivalent to 426.2 MMBtu); Average WH capacity = 98.9 MMBtu/unit | 0 | 26453.7776 | 26453.7776 | per unit | 48 C: No FS: All fuels WH to all fuels WH | Total energy consumption by all commercial storage water heaters | 13 | 2010 | J. Paidipati, L. Frantzis, H. Sawyer, and A. Kurrasch, Rooftop Photovoltaics Market Penetration Scenarios, Navigant Consulting, Inc. Burlington, Mass, 2008 - NREL Report NREL/SR-581-42306; Masters Thesis from U. Michigan (http://deepblue.lib.umich.edu/bitstream/2027.42/83664/3/The_Green_Brewery_Project-updated.pdf) pages 56-60 and attached brochure from manufacturing company. |  | 3-3560 | 13 | 13 | AEO 2010 NEMS
786 | Create and deploy technology for direct use of local DC renewable supply in DC-powered products | R: Use of DC Renewable Supply | Whole building | 5 | 2 | Residential | Building | Hardware for direct use of DC power | New Residential | Energy Savings (%) | 0.884% | 0% | Yes | $20k per home (includes $5k for bi-directional inverter, $1k for DC/DC converter, $10k avg for onsite batteries, and $4k for charge controls) | 0 | 20000 | 20000 | per home | 59 R: No FS: All fuels/end-uses | Total residential energy consumption in all single-family homes | 10 | 2017 | Garbesi, K., Vossos, V., Sanstad, A., and G. Burch, "Optimizing Energy Savings from Direct DC in US Residential Buildings," LBNL-5193E, 2011. | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. BTO Tool: Applied to 13.6% of entire residential primary load (7.6% Electronics, 2.4% computers, 3.6% other) | 1-179 | 10 | 10 | AEO 2014 NEMS
792 | Low cost solar water heater, gas back up with no fuel switching to replace all gas water heater | R: NREL Solar WH, Gas BU, $1200 | System | 5 | 2 | Residential | Water Heating | Solar WH: indirect, passive | All | Energy Savings (%) | 32% | 0 | Yes | $1200 - lower bound based on NREL |  |  | 1200 | per home; 48.3 sq. ft absorber | 2 C/R: No FS: All gas to all gas | Total gas water heating energy consumption | 13 | 2017 | Bahman Habibzadeh |  | 1-61 | 13 | 13 | AEO 2014 NEMS
793 | Low cost solar water heater, gas BU with no FS to replace all gas water heater | R: NREL Solar WH, Gas BU, $3000 | System | 5 | 2 | Residential | Water Heating | Solar WH: indirect, passive | All | Energy Savings (%) | 32% | 0 | Yes | $3000 - maximum bound based on NREL |  |  | 3000 | per home; 48.3 sq. ft absorber | 2 C/R: No FS: All gas to all gas | Total gas water heating energy consumption | 13 | 2017 | Bahman Habibzadeh |  | 1-61 | 13 | 13 | AEO 2014 NEMS
794 | Low cost solar water heater, gas back up with no fuel switching to replace gas storage water heater in all except hottest climate | R: NREL Solar WH, Gas BU, $1200 (Exc. Hot CZ) | System | 5 | 2 | Residential | Water Heating | Solar WH: indirect, passive | All | Energy Savings (%) | 32% | 0 | Yes | $1200 - lower bound based on NREL |  |  | 1200 | per home; 48.3 sq. ft absorber | 2 C/R: No FS: All gas to all gas | All residential gas storage water heaters in all except hottest climates | 13 | 2017 | Bahman Habibzadeh |  | 1-68 | 13 | 13 | AEO 2014 NEMS
795 | Low cost solar water heater, gas BU with no FS to replace gas storage water heater in all except hottest climate | R: NREL Solar WH, Gas BU, $3000 (Exc. Hot CZ) | System | 5 | 2 | Residential | Water Heating | Solar WH: indirect, passive | All | Energy Savings (%) | 32% | 0 | Yes | $3000 - maximum bound based on NREL |  |  | 3000 | per home; 48.3 sq. ft absorber | 2 C/R: No FS: All gas to all gas | All residential gas storage water heaters in all except hottest climates | 13 | 2017 | Bahman Habibzadeh |  | 1-68 | 13 | 13 | AEO 2014 NEMS
796 | Demonstrate and deploy NG Adsorption Heat Pump WHs in commercial buildings - TARGET | C: Gas Adsorption HPWH* | System | 5 | 0 | Commercial | Water Heating | Heat pump | All | Energy Factor | 1.5 | 0.6 | Yes | Target cost | 4900 | 13250 | 8350 | per unit | 2 C/R: No FS: All gas to all gas | Total energy consumption by all commercial gas storage water heaters | 13 | 2019 | 1) Baseline operation: Estimated based on typical energy factors for residential gas-fired WH (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) 2) Target EF is based on max heating COP listed for SorTech adsorption chiller in heat pump mode (Source: http://www.kpwsolutions.com.au/global/brochures/KPW-Solutions-Cooling-Data-Sheets.pdf) 3) Baseline cost: Average cost (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) 4) Target price assumes a 50% cost reduction from current price (Source: http://www.r718.com/news/view/3745). Current price for a 200,000 Btu/Hr adsorption heat pump (~$26,500) extrapolated based on prices for 25 and 50 kw adsorption chillers in heat pump mode (Equipment Performance Source: http://www.kpwsolutions.com.au/global/brochures/KPW-Solutions-Cooling-Data-Sheets.pdf) (Pricing Sources: http://www.sortech.de/uploads/media/SorTech_Prices_Information_ACS08.pdf http://www.sortech.de/uploads/media/SorTech_Prices_Information_ACS15.pdf) Prices converted from euros to dollars using the 2013 annual average conversion rate of 1.27 (Source: http://www.irs.gov/Individuals/International-Taxpayers/Yearly-Average-Currency-Exchange-Rates) | Original notes from peer review 2012-2013: "Savings will be less than measure 501; EF will be near 1.0 (Target); Target cost near $1,000." | 3-3561 | 13 | 13 | AEO 2010 NEMS
797 | Engine Driven Heat Pump, residential buildings - TARGET | R: Engine Driven HP (FS to gas)* | System | 3 | 0 | Residential | Heating & Cooling | Heat pump | Replace all electric HVAC systems in residential buildings | Energy Factor | 1.295 | 2.8949 | Yes | Average cost of $3000/ton | 3075 | 9000 | 5925 | per unit; assume 3 ton system | 3 C/R: FS: All electric to all gas | All electric heating, proportion of cooling in homes with electric heating | 15 | 2016 | 1) Efficient unit performance: Heating primary EF of 1.4; cooling primary EF of 1.1. Total Primary EF based on 65-35 average of heating and cooling primary EF, average EF can be adjusted for specific building types by weighting based on relative heating /cooling loads (65-35 split of heating and cooling energy consumption based on average residential building primary energy use for space heating and cooling in Buildings Energy Data Book). Heating and cooling primary EF based on typical COPs for Commercial Gas-Fired Engine-Driven Rooftop Air Conditioners (Source: EIA - Technology Forecast Updates – Residential and Commercial Building Technologies, September 2013) 2) Base unit performance: 0.75 heating primary EF; 1.2 cooling primary EF. Total Primary EF based on 65-35 average of heating and cooling primary EF, average EF can be adjusted for specific building types by weighting based on relative heating /cooling loads (65-35 split of heating and cooling energy consumption based on average residential building primary energy use for space heating and cooling in Buildings Energy Data Book). Heating: 8 HSPF (Source: EIA - Technology Forecast Updates – Residential and Commercial Building Technologies, September 2013), Converted to 2.34 COP (via COP = 0.293*HSPF), Converted to Primary EF assuming a site-to-source conversion factor of 3.1 (Source: Buildings Energy Data Book). Cooling: converted 14 SEER to roughly 3.7 COP, converted to 1.2 primary EF. 3) Standard unit average cost for a residential air source heat pump. (EIA - Technology Forecast Updates – Residential and Commercial Building Technologies, September 2013) 4) Efficient unit cost for Commercial Gas-Fired Engine-Driven Rooftop Air Conditioners (Source: EIA - Technology Forecast Updates – Residential and Commercial Building Technologies, September 2013) |  | 1-124 | 15 | 15 | AEO 2014 NEMS
802 | Research and demonstrate R-10 windows in homes (DOE Roadmap 2025 Cost Target) | R: R-10 Windows*(2025, $6/SF) | Windows | 5 | 0 | Residential | Building | Windows | All | R-value | 10 | 1.8612 | Yes | $6/SF Premium | 0 | 1332 | 1332 | per home; 222 ft^2 of window area (BED 2011) | 28 R: No FS: Window conduction specific | Total heating and cooling lost through windows due to conduction in all homes | 30 | 2025 | Cost target: Windows Roadmap Goals provided by Karma. Southwall, Alpeninc, PNNL Lost Opportunities Primary Source: 6. Apte, J. & Arasteh, D. Window-Related Energy Consumption in the US Residential and Commercial Building Stock. Buildings 1-38 (Berkeley, CA, 2006). Personal communication: various window experts Other Supporting Sources: Arasteh, Dariush; Selkowitz, Steve; Apte, Josh; LaFrance, Marc. Energy Impacts of Today’ s Window Stock ; FOA TARGET | BTO Tool: Does not include system benefits Appendix B: See tables 4 and 7 for use and savings Calculated from first principles; costs from NREL bottom-up VIG build | 1-114 | 30 | 30 | AEO 2014 NEMS
803 | Research and demonstrate R-10 windows in commercial buildings (DOE Roadmap 2025 Cost Target) | C: R-10 Windows* (2025, $6/SF) | Windows | 5 | 0 | Commercial | Building | Windows | All | R-value | 10 | 1.6129 | Yes | $6/SF Premium | 0 | 2.16 | 2.16 | per square foot; wall: floor space of .9, window fill ratio of 0.4 | 31 C: No FS: Window conduction specific | Total window conductive loss in all commercial buildings | 40 | 2025 | Cost target: Windows Roadmap Goals provided by Karma. Southwall, Alpeninc, PNNL Lost Opportunities Primary Source: 6. Apte, J. & Arasteh, D. Window-Related Energy Consumption in the US Residential and Commercial Building Stock. Buildings 1-38 (Berkeley, CA, 2006). Personal communication: various window experts Other Supporting Sources: Arasteh, Dariush; Selkowitz, Steve; Apte, Josh; LaFrance, Marc. Energy Impacts of Today’ s Window Stock ; FOA TARGET | BTO Tool: Does not include system benefits Appendix B: See tables 4 and 7 for use and savings Calculated from first principles; costs from NREL bottom-up VIG build | 3-3637 | 40 | 40 | AEO 2010 NEMS
804 | Develop and Deploy Cold Climate Heat Pumps - Target based on UTRC project | C: Cold Climate HP* | System | 5 | 0 | Commercial | Heating/Cooling/Water | Heat pump | All | Energy Savings (%) | 51.79% | 0 | No | Simple payback < 5 years! |  |  | 0.095 | per square foot | 1 C/R: No FS: All electric to all electric | Total commercial electric heating and proportion of cooling in buildings with electric heating in 2 coldest climates | 15 | 2016 | Program Goal | Program goal based on current efforts by UTRC under DE-FOA-0000621 | 3-3792 | 15 | 15 | AEO 2010 NEMS
805 | Develop and Deploy Low-Cost Gas Heat Pump for Building Space Heating (DOE FOA Target) | R: Low-Cost Gas HP* | System | 5 | 0 | Residential | Building | Heat pump | Residential heating using NG | Energy Savings (%) | 30% | 0 | No | Simple payback 3-5 years! |  |  | 1000 | per home | 2 C/R: No FS: All gas to all gas | Total residential heating energy use by natural gas furnaces in all homes. | 15 | 2016 | Program goal | Program goal based on current efforts by Stone Mountain Technologies, Inc.: Alternative Space-Heating Systems under DE-FOA-0000621 | 1-46 | 15 | 15 | AEO 2014 NEMS
806 | Reduce air infiltration due to windows with better flashing at EOL or New Construction | R: Improved Window Flashing | Infiltration | 3 | 4 | Residential | Building | Infiltration control | All | Energy Savings (%) | 7% | 0% | Yes | $20 per window |  | 296 | 296 | per home; 222 window square feet per home; 3x5 windows | 40 R: No FS: Infiltration specific | Total heating and cooling lost through infiltration in all homes | 30 | 2012 | Window Area: BED Table 2.1.15; Energy Savings: BED Table 2.1.15; ASHRAE 2007, ORNL Study "An Exploration of Wall Retrofit Best Practices". Cost: Need a source! | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. % Savings: Improvement of 70% for caulking/flashing/reducing infiltration load for uncaulked window (1.7 cm^2/m^2) to caulked window (0.5 cm^2/m^2). Given that infiltration accounts for 16% of the cooling load and 28% of the heating load (BED 2011, Table 2.1.15); and windows account for 10% of total infiltration load (US Dept. of Interior: http://www.nps.gov/tps/sustainability/energy-efficiency/weatherization/air-infiltration.htm); So better flashing can improve 10% of the infiltration load by 70% (so 7% savings). Assuming all 3 x 5 windows in the home with an average of 222 SF of window space | 1-109 | 30 | 30 | AEO 2014 NEMS
807 | Vacuum Insulated Panels (VIPs) in walls in new homes | R: VIP in Walls (N) | Walls | 5 | 3 | Residential | Building | Walls | All | R-value | 35 | 11.1 | Yes | $16/SF (range from $12.6 - 22.9/SF, average: $16/sqft) | 3364 | 48976 | 45612 | per home; BED: 3,061 sq. ft. of insulation for a 2,272 sq. ft. single family home built in 2000 | 34 R: No FS: Wall specific | Total heating and cooling lost through walls in new single/multi/mobile homes | 30 | 2013 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Target R value of 35; punctured VIP area would be reduced to R22 | 1-120 | 30 | 30 | AEO 2014 NEMS
808 | Vacuum Insulated Panels (VIPs) in walls in new commercial buildings | C: VIP in Walls (N) | Walls | 5 | 3 | Commercial | Building | Walls | All | R-value | 35 | 17 | Yes | $16/SF (range from $12.6 - 22.9/SF, average: $16/sqft); typical insulation cost: $1.09/sq.ft. (RS Means) | 0.5886 | 8.64 | 8.0514 | per square foot; wall to floor ratio: 0.9 m inus window ratio of 0.4 | 35 C: No FS: Wall specific | Total heating and cooling energy lost through wall in all new commercial buildings | 40 | 2013 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Cost from Table 1 of http://www.nrel.gov/docs/fy13osti/55875.pdf ; RS means for cost of existing insulation (including installation). Costs for resid and comm applications are assumed the same. (Data saved in supp. Documentations.) | 3-3688 | 40 | 40 | AEO 2010 NEMS
812 | Retrofit using aerogel in walls in pre-2010 single-family homes (interior insulation (R-4)). TARGET- cost | R: Aerogel in walls, interior R-4 [E]* | Walls | 5 | 0 | Residential | Building | Walls | All | R-value | 15.1 | 11.1 | Yes | Current: $3.33/SF (2.75/SF material + 0.51 SF installation); see Table 5, and use a 50% cost compression of Aerogel as per the recommendations of pg. 4 http://www.nrel.gov/docs/fy13osti/55875.pdf | 0 | 5096.565 | 5096.565 | per home; BED: 3,061 sq. ft. of insulation for a 2,272 sq. ft. single family home built in 2000 | 34 R: No FS: Wall specific | Total heating and cooling lost through walls in single-family homes built before 2010 | 30 | 2017 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Picked the R12 target at 50% cost compression of Areogel in addition to R-11 standard home's wall. | 1-121 | 30 | 30 | AEO 2014 NEMS
813 | Aerogel in walls in all commercial buildings, interior insulation (R-4). TARGET - cost | C: Aerogel in walls, int R-4* | Walls | 5 | 0 | Commercial | Building | Walls | All | R-value | 15.1 | 11.1 | Yes | Current: $3.33/SF (2.75/SF material + 0.51 SF installation); see Table 5, and use a 50% cost compression of Aerogel as per the recommendations of pg. 4 http://www.nrel.gov/docs/fy13osti/55875.pdf | 0 | 0.8991 | 0.8991 | per square foot; wall: floor space of .9, window fill ratio of 0.4 | 35 C: No FS: Wall specific | Total heating and cooling load due to energy loss through walls in all commercial buildings | 40 | 2017 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Picked the R20 target at 50% cost compression of Areogel. This is assumed to be additional insulation to the baseline insulation of R-11. | 3-3677 | 40 | 40 | AEO 2010 NEMS
814 | Advanced Rooftop Unit (RTU) (DOE CRADA TARGET) | C: Adv. RTU (IEER 22)* | System | 3 | 0 | Commercial | Cooling | RTU | Central | IEER | 22 | 11.2 | Yes | DOE funded target: $9-10k | 1.3333 | 2.3 | 0.96667 | per square foot; 10 tons per 6,000 sq.ft. | 1 C/R: No FS: All electric to all electric | Total commercial cooling by rooftop AC units (RTUs) | 15 | 2016 | CRADA with BTP, Primary Source: Personal communication: Bouza | Cost was approximated by interpolating between the IEER 20 (#765) and SEER 24 AC targets. (#97) | 3-3681 | 15 | 15 | AEO 2010 NEMS
815 | Retrofit walls with blown-in aerogel in pre-2010 homes. TARGET (R-value & cost) | R: Blown-in Aerogel, Walls* [E] | Walls | 5 | 0 | Residential | Building | Walls | All | R-value | 31.1 | 11.1 | Yes | $13/SF (includes the cost of all retrofit tasks as well as material) | 0 | 39793 | 39793 | per home; BED: 3,061 sq. ft. of insulation for a 2,272 sq. ft. single family home built in 2000 | 34 R: No FS: Wall specific | Total heating and cooling lost through walls in homes built before 2010 | 30 | 2017 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Picked the R12 target at 50% cost compression of Areogel in addition to R-11 standard home's wall. | 1-126 | 30 | 30 | AEO 2014 NEMS
816 | Research, develop and demonstrate lighting energy savings of improved daylighting over 50 foot floor plate in commercial buildings | C: Perimeter Zone Daylighting (MYP2020)* | Windows | 5 | 0 | Commercial | Lighting | Windows | All | Energy Savings (%) | 35% | 0% | Yes | <$13/ft^2 cost target (including controls and sensors) | 0 | 195 | 195 | per fluorescent lamp; wall: floor space of .9, window fill ratio of 0.4 | 1 C/R: No FS: All electric to all electric | All commercial fluorescents in a perimeter zone | 20 | 2020 | Source: Karma Sawyer: Windows Roadmap Goals (May 30, 2013) | Cost calculations: $13/ 1 sqft of window * sqft of window/sqft of floor(0.36) * sqft of floor/ fluorescent lamp (1/0.024). Window to floor ratio: 0.4 * 0.9(space filled by glass) = 0.36; 0.024 lamps/sqft (LMC 2010, NCI: 811 xcl file calc.) | 3-3471 | 20 | 20 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
817 | Replace metal halide parking lot lighting with LEDs, and install timer and motion sensor controls | O: Parking Lot LEDs + Cntrls | System | 5 | 4 | Outdoor | Lighting | Luminaire | MH in Parking lots | lumens/watt | 112.88 | 60 | Yes | Standard and efficient unit costs are first costs; incremental cost includes relamping an maintenance calculations. | 240 | 573.46 | 90.4 | per luminaire | 1 C/R: No FS: All electric to all electric | All metal halide lighting in parking lots | 4 | 2013 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 3-3468 | 4 | 11 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
818 | LEDs for residential general use lighting in place of incandescents | R: LEDs to replace Incandescents | Lamp | 5 | 4 | Residential | Lighting | Lamp | Incandescent | lumens/watt | 73 | 13 | Yes | Standard and efficient unit costs are first costs; incremental cost includes relamping an maintenance calculations. | 1.2 | 25.34 | -24.36 | per lamp | 1 C/R: No FS: All electric to all electric | Total incandescent (MSB, reflectors, and other) lighting energy consumption all homes | 2 | 2013 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization 4) Daily operating hours from the PNNL: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/2012_residential-lighting-study.pdf | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 1-166 | 2 | 43 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
819 | Vacuum Insulated Panels (VIPs) in walls in existing commercial buildings | C: VIP in Walls [E]* | Walls | 5 | 0 | Commercial | Building | Walls | All | R-value | 35 | 11.1 | Yes | $16/SF (range from $12.6 - 22.9/SF, average: $16/sqft); typical insulation cost: $1.09/sq.ft. (RS Means), target: 50% cost compression | 0 | 4.32 | 4.32 | per square foot; wall: floor space of .9, window fill ratio of 0.4 | 35 C: No FS: Wall specific | Total heating and cooling load due to energy loss through walls in all commercial buildings | 40 | 2017 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Cost from Table 1 of http://www.nrel.gov/docs/fy13osti/55875.pdf | 3-3677 | 40 | 40 | AEO 2010 NEMS
820 | Vacuum Insulated Panels (VIPs) in walls in new commercial buildings | C: VIP in Walls [N]* | Walls | 5 | 0 | Commercial | Building | Walls | All | R-value | 35 | 17 | Yes | $16/SF (range from $12.6 - 22.9/SF, average: $16/sqft); typical insulation cost: $1.09/sq.ft. (RS Means), target: 50% cost compression | 0.5886 | 4.32 | 3.7314 | per square foot; wall to floor ratio: 0.9 m inus window ratio of 0.4 | 35 C: No FS: Wall specific | Total heating and cooling energy lost through wall in all new commercial buildings | 40 | 2017 | Cost and Performance Data: Kosny, Jan. et al. Cold Climate Building Enclosure Solutions. 2013. Figure 3 & Table 1, http://www.nrel.gov/docs/fy13osti/55875.pdf | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Cost from Table 1 of http://www.nrel.gov/docs/fy13osti/55875.pdf ; RS means for cost of existing insulation (including installation). Costs for resid and comm applications are assumed the same. (Data saved in supp. Documentations.) | 3-3688 | 40 | 40 | AEO 2010 NEMS
824 | Replace all outdoor lighting with LEDs | O: LED, General Illumination | System | 5 | 4 | Outdoor | Lighting | Luminaire | All | lumens/watt | 83 | 63 | Yes | Standard and efficient unit costs are first costs; incremental cost includes relamping an maintenance calculations. | 240 | 477.56 | 62.46 | per luminaire | 1 C/R: No FS: All electric to all electric | All lighting, Outdoor | 8 | 2013 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 3-3428 | 8 | 15 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
825 | Replace all outdoor lighting with LEDs - TARGET | O: LEDs, SSL Program Goal (2020)* | System | 5 | 0 | Outdoor | Lighting | Luminaire | All | lumens/watt | 210 | 63 | Yes | The DOE SSL Program goal is for LED luminaires to reach a first cost of $17/klm by 2020. It is expected that there will be little to no change to outdoor conventional lighting. This is estimated at a weighted average of $32/klm. Assume a 10,000 lumen output is typical for outdoor fixtures. | 240 | 170 | -420 | per luminaire | 1 C/R: No FS: All electric to all electric | All lighting, Outdoor | 8 | 2020 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 3-3428 | 8 | 30 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
826 | Replace all commercial, residential and industrial downlighting (incandescent, screw base CFL or pin base CFL) with LEDs | C/R/I: Replace Downlight w/ LEDs | System | 5 | 4 | Commercial/Residential/Industrial | Lighting | Luminaire | Downlights | lumens/watt | 64 | 20 | Yes | Standard and efficient unit costs are first costs; incremental cost includes relamping an maintenance calculations. | 3.6 | 41.82 | -41.58 | per luminaire | 1 C/R: No FS: All electric to all electric | All downlighting in all commercial, residential and industrial buildings | 3 | 2013 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 3-3465 | 3 | 46 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
827 | Replace all MR16s with LEDs | R/C: Replace MR16s w/ LEDs | Lamp | 5 | 4 | Residential and Commercial | Lighting | Lamp | MR16 | lumens/watt | 62 | 17 | Yes | Standard and efficient unit costs are first costs; incremental cost includes relamping an maintenance calculations. | 2.25 | 34.05 | 13.24 | per luminaire | 1 C/R: No FS: All electric to all electric | All commercial and residential MR16s | 1 | 2013 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 3-3480 | 1 | 9 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
828 | Replace metal halide streetlighting with LEDs | O: LED Streetlights | System | 5 | 4 | Outdoor | Lighting | Luminaire | Streetlights | lumens/watt | 83 | 60 | Yes | Standard and efficient unit costs are first costs; incremental cost includes relamping an maintenance calculations. | 250 | 716.19 | 101.61 | per luminaire | 1 C/R: No FS: All electric to all electric | All metal halide street lighting | 4 | 2013 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 3-3481 | 4 | 11 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
829 | Replace metal halide streetlighting with LEDs with controls | O: LED Streetlights + Controls | System | 5 | 4 | Outdoor | Lighting | Luminaire | Streetlights | lumens/watt | 106 | 60 | Yes | Standard and efficient unit costs are first costs; incremental cost includes relamping an maintenance calculations. | 250 | 812.19 | 197.61 | per luminaire | 1 C/R: No FS: All electric to all electric | All metal halide street lighting | 4 | 2013 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 3-3481 | 4 | 11 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
830 | Replace metal halide parking garage lights with LEDs | O: Parking Garage LEDs | System | 5 | 4 | Outdoor | Lighting | Luminaire | Parking Garage | lumens/watt | 78 | 60 | Yes | Standard and efficient unit costs are first costs; incremental cost includes relamping an maintenance calculations. | 97.5 | 238.73 | 19.7 | per luminaire | 1 C/R: No FS: All electric to all electric | All metal halide lighting in parking garages | 3 | 2013 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 3-3466 | 3 | 8 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
831 | Replace metal halide parking garage lights with LEDs with controls | O: Parking Garage LEDs + Cntrls | System | 5 | 4 | Outdoor | Lighting | Luminaire | Parking Garage | lumens/watt | 106 | 60 | Yes | Standard and efficient unit costs are first costs; incremental cost includes relamping an maintenance calculations. | 97.5 | 334.73 | 115.7 | per luminaire | 1 C/R: No FS: All electric to all electric | All metal halide lighting in parking garages | 3 | 2013 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 3-3466 | 3 | 8 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
832 | LEDs to replace high bay | C: High Bay LEDs | System | 5 | 4 | Commercial | Lighting | Luminaire | High bay | lumens/watt | 80 | 65 | Yes | Standard and efficient unit costs are first costs; incremental cost includes relamping an maintenance calculations. | 225 | 1494.15 | 1146.15 | per luminaire | 1 C/R: No FS: All electric to all electric | All high bay lighting in all commercial and industrial buildings | 3 | 2013 | 1) LED efficacy from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf 2) LED Prices from PNNL 2013: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_trend-analysis_2013.pdf (see Excel tab 'PNNL Price Data' in "Lighting Measures_Relamp and Labor Costs_4-2-14") 3) Standard lamp performance and cost: Navigant Product Database; U.S. Lighting Market Characterization | Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". | 3-3464 | 3 | 8 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
833 | OLED Tasklighting target for 2020 to partially (50%) replace linear fluorescent ceiling lighting in new construction | C: OLED Tasklighting* (N) | System | 5 | 0 | Commercial | Lighting | Luminaire | Commercial linear fluorescent (50%) | Energy Savings (%) | 25% | 0% | Yes | Linear fluorescent lamp cost (2 lamps + ballast per fixture): $4/klumen (MYP2013); Fixture (2’x4’) from google search is $70 (varies) with 2 lamps producing 2500 lumens. 2500 lumens x 2 lamps = 5,000 lumens * 0.8 (efficiency) = 4 klumens. Fixture cost per lumen = $70/4 klumens = $17.5/klumen. Total cost = $4+$17.5=$21.5/klumen. Average troffer system provides 5,000 lumens. OLED cost: $24/klumen (Manufacturing Roadmap) However, only 2500 lumen OLED task lighting lamp is required. Due to the fact that for OLEDs the whole fixture would need to be replaced, and for fluorescent lighting, only the bulb will need to be replaced after 5 years, a one time first incremental cost equivalent is needed. In order to obtain this one time incremental cost equivalent, assume the average cost over 20 years (4 incurred cost periods) can be used. Assume the entire linear fluorescent fixture would need to be replaced after 20 years. | 42 | 60 | 18 | per luminaire | 1 C/R: No FS: All electric to all electric | All fluorescents, new commercial | 5 | 2019 | Cost and efficiency data is from Internal Solid State Program White Papers: 1) Cost Competitiveness of Solid State Lighting. (2013,not published). 2) Energy Savings Potential of OLEDs in Office Buildings (July 2013). OLED cost source: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_manuf-roadmap_sept2013.pdf Flourescent lamp and ballast cost: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/ssl_mypp2013_web.pdf Google search for cost of linear fluorescent fixtures. | Watts/lumen consumption between OLED and linear fluorescents is not significantly different, however, 50% less lumens will be required if OLEDs are used as task lighting to replace 50% of new buildings’ linear fluorescents. There is no significant difference in lifetimes for these lamps, assumed to be 5 years (24000hrs). | 3-3474 | 5 | 5 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
834 | Wireless temperature sensors | C: Wireless Temperature Sensors | Controls | 5 | 4 | Commercial | HVAC | Wireless Sensors | Building Automation Systems | Energy Savings (%) | 10% | 0% | Yes | $7000 total installed cost for 37 sensors at 90,000 SF facility |  | 0.077778 | 0.077778 | per square foot | 7 C: No FS: All fuels heating and cooling | Total heating and cooling in all commercial buildings | 10 | 2013 | FEMP Technology Installation Review: Wireless Temperature Sensors for Improved HVAC Control (DOE/EE-0319); Navigant Report: Energy Savings Potential and RD&D Opportunities for Residential HVAC Technologies, September 2012. | Expected lifetime is assumed - we do not have a good source to support this assumption. 5-15% indirect savings of HVAC energy consumption reduction. | 3-3628 | 10 | 10 | AEO 2010 NEMS
843 | Deploy advanced walls using EIFS with VIPs in all commercial buildings. DOE DE-EE0003915 project lead by Dow Corning, Dryvit, Inc., and Fraunhofer CSE. | C: EIFS+VIP R-30 Walls | Walls | 5 | 3 | Commercial | Building | Walls | All | R-value | 31.8 | 11.1 | Yes | $20/SF for baseline unit; $35/SF for EIFS+VIP. Additional cost to existing systems include the VIP, the effort to encapsulate the VIP into foam plastic insulation, and the engineering of proper placement on the façade. (DOW Corning) | 10.8 | 18.9 | 8.1 | per square foot; wall to floor space ratio of 0.9 | 35 C: No FS: Wall specific | Total heating and cooling load due to energy loss through walls in all commercial buildings | 40 | 2013 | Data obtained from RFI Measure Addition Form submitted by Lawrence Carbary from Dow Corning in 2013. He specified that the data is obtianed from the PI of this project (DOE DE-EE0003915) funded by DOE ($1,241,120 USD/3years from saved report). | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 3-3677 | 40 | 40 | AEO 2010 NEMS
844 | Research, demonstrate and deploy Sandia rotating heat exchangers in residential refrigerators and freezers | R: Rotary Cooler in Refrigerators and Freezers* | Heat Exchanger | 2+ | 0 | Residential | Refrigeration | Heat exchanger | All | Energy Savings (%) | 10% | 0% | Yes | Place holder |  | 22.4971 | 22.4971 | per home | 1 C/R: No FS: All electric to all electric | All residential refrigerators and freezers | 17 | 2018 | Market Assessment and Commercialization Strategy for the Radia Sandia Cooler. 2014. BTO. DOE. Not published yet. |  | 1-92 | 17 | 17 | AEO 2014 NEMS
846 | Research, demonstrate and deploy Sandia rotating heat exchangers in residential central air conditioners, room air conditioners, and ASHPs. | R: Rotary Cooler in CAC, room ACs, and HPs* | Heat Exchanger | 2+ | 0 | Residential | Heating & Cooling | Heat exchanger | All | Energy Savings (%) | 10% | 0% | Yes | Place holder |  | 57.4655 | 57.4655 | per home | 1 C/R: No FS: All electric to all electric | Total residential CAC, room AC, and electric heat pump heating and cooling | 20 | 2018 | Market Assessment and Commercialization Strategy for the Radia Sandia Cooler. 2014. BTO. DOE. Not published yet. |  | 1-34 | 20 | 20 | AEO 2014 NEMS
848 | Research and demonstrate R-10 windows in homes at a 2025 DOE Roadmap target premium cost (2014) | R: R-10 Windows (MYP2020, $10/SF)* | Windows | 5 | 0 | Residential | Building | Windows | All | R-value | 10 | 1.61 | Yes | $20/sq.ft. vs. $10/sq.ft. for uninstalled IGU; 2020 target: $10/sq.ft. incremental cost compared to the 2010 standard base of windows | 2220 | 4440 | 2220 | per home; 222 ft^2 of window area (BED 2011) | 28 R: No FS: Window conduction specific | Total heating and cooling lost through windows due to conduction in all homes | 30 | 2020 | Cost Targets from Windows and Envelope Roadmap Report 2014 |  | 1-114 | 30 | 30 | AEO 2014 NEMS
849 | Research and demonstrate R-7 windows in commercial buildings a 2025 DOE Roadmap target premium cost (2014) | C: R-7 Windows (MYP2020, $8/SF)* | Windows | 5 | 0 | Commercial | Building | Windows | All | R-value | 7 | 1.86 | Yes | $18/sq.ft. vs. $10/sq.ft. for uninstalled IGU; 2020 target: $8/sq.ft. incremental cost compared to the 2010 standard base of windows | 3.6 | 6.48 | 2.88 | per square foot; wall: floor space of .9, window fill ratio of 0.4 | 31 C: No FS: Window conduction specific | Total window conductive loss in all commercial buildings | 40 | 2020 | Cost Targets from Windows and Envelope Roadmap Report 2014 |  | 3-3637 | 40 | 40 | AEO 2010 NEMS
850 | Increase adoption of low-e interior panel storm windows on existing 1-pane metal framed windows in homes | R: Interior Low-e Panels [E] | Windows | 5 | 4 | Residential | Building | Windows | Existing | Energy Savings (%) | 54.63% | 0% | Yes | Average total cost for 2.5'x5'=12ft^2 low-e window $120 (or $10/sq.f.t), and for a non-low-e plastic panel $60. | 0 | 1800 | 1800 | per home; 15 storms/home, assumes 15 windows/home, 2.5x5 ft^2 (BED 2011) | 30 R: No FS: Window (cond+rad) specific | Total energy losses due to conduction and radiation for single pane glass windows for all homes built before 2010 | 30 | 2012 | Kohler, C Letter report for low-e storm window retrofits, 2006 | 1) Costs were adjusted based on PNNL RFI response: $120 per 30"x60" window, uninstalled from http://www.efficientwindowcoverings.org/understanding-window-coverings/interior-panel/ 2) Report indicates 18% savings of whole home heating for low-e storms, scaled to address conductive and radiative loss; 18% of home heating and cooling is 55% of window load heating/cooling. "A simulation study in 2004 has shown that by using pyrolitic “hard” low-e coatings.. will increase from approximately 15% of the home’s heating energy to 18%. The additional cost is...on the order of $100." 3) Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 1-119 | 30 | 30 | AEO 2014 NEMS
851 | Increase adoption of low-e interior panel storm windows on existing 1-pane metal framed windows in commercial buildings | C: Interior Low-e Panels [E] | Windows | 5 | 4 | Commercial | Building | Windows | Existing | Energy Savings (%) | 54.63% | 0% | Yes | Assumes similar cost per sq.ft. for commercial windows and residential windows. Average total uninstalled cost for residential 2.5'x5'=12ft^2 low-e window $120 (or $10/sq.ft), and for a non-low-e plastic panel $60. | 0 | 3.6 | 3.6 | per square foot; wall: floor space of .9, window fill ratio of 0.4 | 33 C: No FS: Window (cond+rad) specific | Total commercial radiative and conductive window load for pre-2010 buildings with single pane windows (includes solar heat gain loss during cooling season as well as solar heat gain benefit during heating season) | 40 | 2012 | Kohler, C Letter report for low-e storm window retrofits, 2006 | 1) Costs were adjusted based on PNNL RFI response: $120 per 30"x60" window, uninstalled from http://www.efficientwindowcoverings.org/understanding-window-coverings/interior-panel/ 2) Report indicates 18% savings of whole home heating for low-e storms, scaled to address conductive and radiative loss; 18% of home heating and cooling is 55% of window load heating/cooling. "A simulation study in 2004 has shown that by using pyrolitic “hard” low-e coatings.. will increase from approximately 15% of the home’s heating energy to 18%. The additional cost is...on the order of $100." 3) Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 3-3674 | 40 | 40 | AEO 2010 NEMS
870 | Develop and deploy a controller pack to RTU accomponied by a gas furnace for demand controlled ventilation and upgrade to a digital economizer with differential high limit control. In the process reduce excess baseline ventilation with acceptance testing on setup. | C: RTU Control Retrofit (DCV+Economizer) | Controls | 5 | 3 | Commercial | Heating & Cooling | Building controls | RTUs and gas furnaces | Energy Savings (%) | 20% | 0% | Yes | Installed cost of $1400/RTU. Incremental cost derived from retrofitting of a 5 ton unit, which is most common; per ton costs for 15 ton unit will be significantly lower. | 0 | 1 | 1 | per square foot, assuming 1 ton per 280 sq.ft. | 12 C: No FS: gas heating and electric cooling (RTU) | Total Furnace gas heating and electric RTU AC in all commercial buildings | 15 | 2013 | 1) Costs and energy savings obtained from pg. 60-61, RTU Premium Ventilation: Proof of Concept Field Test. May 2012. Bonneville Power Administration. http://www.bpa.gov/energy/n/emerging_technology/pdf/38702_RTU_Premium_Ventilation_Proof_Of_Concept_FINAL.pdf a. Baseline: Energy intensity of NEMSConsFcast3!$L$3792/EquipStockTable3!$L$3792 = 0.039 mmBTU/sq.ft per year. b. Savings in electricity of 0.00117 mmBTU/sq.ft. per year; and 0.006 mmBTU/sq.ft. in gas. 2) Other supporting sources confirming the data: Tables ES 1, 2, 3, etc. PNNL 2011. Wang, Katipamula. Huang. Brambley. Enegy Savings and Economics of Advanced Control Strategies for Packaged Air-Conditioning Units with Gas Heat. | Assume controls last as long as RTUs themselves. Calculations for costs and savings are saved in a separate document under measure #870, 871, 872. | 3-3782 | 15 | 15 | AEO 2010 NEMS
871 | Develop and deploy a controller pack to RTU accomponied by a gas furnace for demand controlled ventilation and upgrade to a digital economizer with differential high limit control. In the process reduce excess baseline ventilation with acceptance testing on setup. Add fan control, either VSD or fan cycling to reduce fan energy use. | C: RTU Control Retrofit (DCV+Econ+VSD) | Controls | 5 | 3 | Commercial | Heating & Cooling | Building controls | RTUs and gas furnaces | Energy Savings (%) | 24% | 0% | Yes | Installed cost of $4250/RTU. Incremental cost derived from retrofitting of a 5 ton unit, which is most common; per ton costs for 15 ton unit will be significantly lower. | 0 | 3.04 | 3.04 | per square foot, assuming 1 ton per 280 sq.ft. | 12 C: No FS: gas heating and electric cooling (RTU) | Total Furnace gas heating and electric RTU AC in all commercial buildings | 15 | 2013 | 1) Costs and energy savings obtained from pg. 60-61, RTU Premium Ventilation: Proof of Concept Field Test. May 2012. Bonneville Power Administration. http://www.bpa.gov/energy/n/emerging_technology/pdf/38702_RTU_Premium_Ventilation_Proof_Of_Concept_FINAL.pdf a. Baseline: Energy intensity of NEMSConsFcast3!$L$3792/EquipStockTable3!$L$3792 = 0.039 mmBTU/sq.ft per year. b. Savings in electricity of 0.00317 mmBTU/sq.ft. per year; and 0.00562 mmBTU/sq.ft. in gas. =(NEMSConsFcast3!$L$3806/EquipStockTable3!$L$3806-0.00562)+(NEMSConsFcast3!$F$3807/EquipStockTable3!$F$3807-0.00317) 2) Other supporting sources confirming the data: Tables ES 1, 2, 3, etc. PNNL 2011. Wang, Katipamula. Huang. Brambley. Enegy Savings and Economics of Advanced Control Strategies for Packaged Air-Conditioning Units with Gas Heat. | Assume controls last as long as RTUs themselves. Calculations for costs and savings are saved in a separate document under measure #870, 871, 872. | 3-3782 | 15 | 15 | AEO 2010 NEMS
872 | Develop and deploy a controller pack to RTU accomponied by a gas furnace for demand controlled ventilation and upgrade to a digital economizer with differential high limit control. In the process reduce excess baseline ventilation with acceptance testing on setup. Add fan control, either VSD or fan cycling to reduce fan energy use, as well as robust optimum start, ventilation lockout during warmup, occupancy sensor standby, and temperature setpoint limits. | C: RTU Control Retrofit (DCV+Econ+VSD+prem) | Controls | 5 | 3 | Commercial | Heating & Cooling | Building controls | RTUs and gas furnaces | Energy Savings (%) | 34% | 0% | Yes | Installed cost of $3100/RTU. Incremental cost derived from retrofitting of a 5 ton unit, which is most common; per ton costs for 15 ton unit will be significantly lower. | 0 | 2.21 | 2.21 | per square foot, assuming 1 ton per 280 sq.ft. | 12 C: No FS: gas heating and electric cooling (RTU) | Total Furnace gas heating and electric RTU AC in all commercial buildings | 15 | 2017 | 1) Costs and energy savings obtained from pg. 60-61, RTU Premium Ventilation: Proof of Concept Field Test. May 2012. Bonneville Power Administration. http://www.bpa.gov/energy/n/emerging_technology/pdf/38702_RTU_Premium_Ventilation_Proof_Of_Concept_FINAL.pdf a. Baseline: Energy intensity of NEMSConsFcast3!$L$3792/EquipStockTable3!$L$3792 = 0.039 mmBTU/sq.ft per year. b. Savings in electricity of 0.00355 mmBTU/sq.ft. per year; and 0.00919 mmBTU/sq.ft. in gas. =(NEMSConsFcast3!$L$3806/EquipStockTable3!$L$3806-0.00919)+(NEMSConsFcast3!$F$3807/EquipStockTable3!$F$3807-0.00355) 2) Other supporting sources confirming the data: Tables ES 1, 2, 3, etc. PNNL 2011. Wang, Katipamula. Huang. Brambley. Enegy Savings and Economics of Advanced Control Strategies for Packaged Air-Conditioning Units with Gas Heat. | Assume controls last as long as RTUs themselves. Calculations for costs and savings are saved in a separate document under measure #870, 871, 872. | 3-3782 | 15 | 15 | AEO 2010 NEMS
876 | Goal for 2030: deploy a suite of energy saving technologies to accomplish the Building America goal of 30% energy savings in existing homes | R: Building America, 2030 (E)* | System | 2+ | 0 | Residential | All End Uses | All | Retrofit | Energy Savings (%) | 30% | 0% | Yes | Not available; assumed 3 year payback in 2010 | 0 | 1628.8415 | 1628.8415 | per home | 59 R: No FS: All fuels/end-uses | Total Energy Consumption for all single and multi-family homes built pre-2010 | 30 | 2014 |  |  | 1-3 | 30 | 30 | AEO 2014 NEMS
877 | Goal for 2030: deploy a suite of energy saving technologies to accomplish the Building America goal of 50% energy savings in new homes | R: Building America, 2030 (N)* | System | 2+ | 0 | Residential | All End Uses | All | Retrofit | Energy Savings (%) | 50% | 0% | Yes | Not available; assumed 3 year payback in 2010 | 0 | 2615.6318 | 2615.6318 | per home | 59 R: No FS: All fuels/end-uses | Total Energy Consumption for all single and multi-family homes built after 2010 | 30 | 2014 |  |  | 1-4 | 30 | 30 | AEO 2014 NEMS
878 | Improving Buildings Energy Performance by Integrating EnergyPlus Energy Modeling in the Design Stage, New Buildings | C: EnergyPlus Integration in Building Design (N) | Whole building | 5 | 3 | Commercial | All End Uses | Whole building | New commercial buildings | Energy Savings (%) | 20% | 0% | Yes | Not available; assumed based on Amir Roth email on Monday 6/3/2013 "max adoption lens" with $30,000 per project plus $0.1 /sqft and using data from http://buildingsdatabook.eren.doe.gov/TableView.aspx?table=3.2.5 we find that the stock weighted average incremental cost is $0.33/sft |  |  | 0.32984 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | Total HVAC load in new commercial buildings | 40 | 2013 | Source: Amir Roth and AIA data 1) No good incremental cost data available, costs were estimated; 2) The energy savings estimates are for architectural firms that are participating in the AIA 2030 Commitment. These are generally large architecture firms that we consider to be aggressive in pursuing energy efficiency (i.e. data is not from a random or representative sample) 3) The energy savings estimate is for the marginal energy savings improvement of simulation/integrative design measures on building designs that already meet “beyond-code prescriptive” performance levels 4) Modeling improves all areas of building consumption, although currently savings were only applied to HVAC because that's the largest active component and because we don't have good data at this point to partition the savings at a finer granularity. | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 3-3639 | 40 | 40 | AEO 2010 NEMS
879 | Improving Buildings Energy Performance by Integrating EnergyPlus Energy Modeling in the Design Stage, Existing Buildings | C: EnergyPlus Integration in Building Retrofit (E) | Whole building | 5 | 3 | Commercial | All End Uses | Whole building | Retrofit commercial buildings | Energy Savings (%) | 10% | 0% | Yes | Not available; assumed based on Amir Roth email on Monday 6/3/2013 "max adoption lens" with $30,000 per project plus $0.1 /sqft and using data from http://buildingsdatabook.eren.doe.gov/TableView.aspx?table=3.2.5 we find that the stock weighted average incremental cost is $0.33/sft |  |  | 0.32984 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | Total HVAC load in existing commercial buildings | 40 | 2013 | Source: Amir Roth 1) This measure is based on #878, but due to retrofit applications was estimated to be half the benefit of new construction. 2) Modeling improves all areas of building consumption, although currently savings were only applied to HVAC because that's the largest active component and because we don't have good data at this point to partition the savings at a finer granularity. | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 3-3798 | 40 | 40 | AEO 2010 NEMS
880 | Deploy a suite of energy saving technologies to accomplish the Better Buildings Challenge goal of 20% energy savings in new buildings | C: Better Buildings Challenge (N)* | System | 2+ | 0 | Commercial | All End Uses | All | Retrofit | Energy Savings (%) | 20% | 0% | Yes | Not available; assumed 5 year payback in 2010 | 0 | 2.2409 | 2.2409 | per square foot | 60 C: No FS: All fuels/end-uses | All energy consumption in new buildings | 40 | 2014 |  | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 3-3633 | 40 | 40 | AEO 2010 NEMS
881 | Deploy a suite of energy saving technologies to accomplish the Better Buildings Challenge goal of 20% energy savings in Existing buildings | C: Better Buildings Challenge (E)* | System | 2+ | 0 | Commercial | All End Uses | All | Retrofit | Energy Savings (%) | 20% | 0% | Yes | Not available; assumed 5 year payback in 2010 | 0 | 2.2409 | 2.2409 | per square foot | 60 C: No FS: All fuels/end-uses | All energy consumption in Existing buildings | 40 | 2014 |  | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 3-3799 | 40 | 40 | AEO 2010 NEMS
882 | Integrating "smart controls" into residential WH systems giving them the capability to learn and adapt to building WH usage patterns, raising or lowering the temp accordingly, and activating re-circulation loops as needed. Smart WH controls can also incorporate FDD capabilities, intuitive interfaces, adaptive algorithms, and integrate seamlessly with other smart building systems. This system is intended to replace the baseline residential gas/oil-fired and electric WH without a smart control system or programmable thermostat. | R: WH Smart Controls* | Controls | 5 | 0 | Residential | Water Heating | All water heaters | New | Energy Savings (%) | 15% | 0% | Yes | $250 per thermostat plus $120 for NEST installation | 0 | 370 | 370 | per unit | 47 R: No FS: All fuels WH to all fuels WH | Total residential storage electric and natural gas water heaters | 13 | 2016 | DOE WH R&D Roadmap Initiative "Expand smart controls for water heating and integrate WH into smart building control systems" 1) % savings: target, NREL has developed a predictive control system for electric heat pump water heaters and gas fired WH. Simulations estimate this technology can reduce energy consumption by up to 20% for a HPWH, therefore we are using 15% energy savings as a target for this technology when applied to all WH (source: http://techportal.eere.energy.gov/technology.do/techID=1181) 2) Cost: target, assumed same as measure 122, "Demonstrate and deploy predictive control thermostats in all homes" ($250 per thermostat plus $120 for NEST installation). Assuming no smart control system or programmable thermostat for a baseline cost. 3) Lifetime of 13 years: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment |  | 1-71 | 13 | 13 | AEO 2014 NEMS
883 | Integrating "smart controls" into commercial WH systems giving them the capability to learn and adapt to building WH usage patterns, raising or lowering the temp accordingly, and activating re-circulation loops as needed. Smart WH controls can also incorporate FDD capabilities, intuitive interfaces, adaptive algorithms, and integrate seamlessly with other smart building systems. This system is intended to replace the baseline commercial gas/oil-fired and electric WH without a smart control system or programmable thermostat. | C: WH Smart Controls* | Controls | 5 | 0 | Commercial | Water Heating | All water heaters | New | Energy Savings (%) | 15% | 0% | Yes | Assume $250 per thermostat and $300 for control system; assume 10 tehrmostats for a 15,000 sq.ft. building. | 0 | 2800 | 2800 | per unit | 48 C: No FS: All fuels WH to all fuels WH | Total energy consumption by all commercial storage water heaters | 13 | 2016 | 1) % savings: NREL has developed a predictive control system for electric heat pump water heaters and gas fired WH. Simulations estimate this technology can reduce energy consumption by up to 20% for a HPWH, therefore we are using 15% energy savings as a target for this technology when applied to all WH (source: http://techportal.eere.energy.gov/technology.do/techID=1181) 2) Costs: Assuming $250 per thermostat and $300 for control system. Based on measure 122, "Demonstrate and deploy predictive control thermostats in all homes" 3) Lifetime: Assumes smart control system has no impact on WH life. Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013 |  | 3-3560 | 13 | 13 | AEO 2010 NEMS
884 | Residential absorption cycle heat pumps (including ammonia-water and LiBr systems) replacing gas-fired storage water heaters. | R: Gas-fired Absorption HPWH* | System | 5 | 0 | Residential | Water Heating | All gas storage water heaters | New | Energy Factor | 1.5 | 0.59 | Yes | Standard unit: $1027 ($2008), cost adjusted to $2014; efficient unit: 2030 target cost | 1116 | 1800 | 684 | per unit | 2 C/R: No FS: All gas to all gas | Total residential storage natural gas water heaters | 13 | 2019 | 1) % Savings: Standard unit: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment; Efficient unit with EF of 1.5 is a target EF for manufacturers, based on ammonia-water system (Source: M. Garrabrant, Stone Mountain Technologies Inc, Development & Validation of a Gas-Fired Residential Heat Pump Water Heater, January 2013, Report DE-EE0003985) 2) Cost of standard unit: Total installed cost is $1027 ($2008) (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses). Cost adjusted from $2008 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl). 3) Cost of efficient unit: target installed cost for 2030, based on ammonia-water absorption system (Source: M. Garrabrant, Stone Mountain Technologies Inc, Development & Validation of a Gas-Fired Residential Heat Pump Water Heater, January 2013, Report DE-EE0003985, http://www.osti.gov/scitech/servlets/purl/1060285 http://techportal.eere.energy.gov/technology.do/techID=1181) |  | 1-58 | 13 | 13 | AEO 2014 NEMS
885 | Commercial absorption cycle heat pumps (including ammonia-water and LiBr systems) replacing gas-fired storage water heaters. Assume no impact on space heating and cooling of this measure. | C: Gas-fired Absorption HPWH* | System | 5 | 0 | Commercial | Water Heating | All gas storage water heaters | New | Energy Factor | 1.5 | 0.6 | Yes |  | 5430 | 7900 | 2470 | per unit | 2 C/R: No FS: All gas to all gas | Total energy consumption by all commercial gas storage water heaters | 13 | 2019 | 1) % savings: Assuming roughly the same EF as a residential gas-fired storage WH for standard unit (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment); for efficient unit, EF of 1.5 is a target EF for manufacturers, based on ammonia-water system (Source: M. Garrabrant, Stone Mountain Technologies Inc, Development & Validation of a Gas-Fired Residential Heat Pump Water Heater, January 2013, Report DE-EE0003985). Standard unit performance: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment. 2) Cost of standard unit: Average installed cost for a 200kBtu/Hr gas storage WH is $5,430 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) 3) Cost of efficient unit: target installed cost for 2030 is $7,900, based on incremental cost ratio for residential units of 1.6 times the cost of a baseline unit - See "Residential gas-fired absorption HPWH" measure |  | 3-3561 | 13 | 13 | AEO 2010 NEMS
886 | Thermally driven heat pump water heater which is targeted to replace residential gas-fired storage WH (typical capacity of 40 gallons and EF of 0.59). Not analyzing benefits of space heating or cooling. Assume no impact on space heating and cooling of this measure. | R: Non-sorption Gas-fired HPWH* | System | 5 | 0 | Residential | Water Heating | All gas storage water heaters | New | Energy Factor | 1.5 | 0.59 | Yes | Standard unit: $1027 ($2008), cost adjusted to $2014 | 1116 | 2630 | 1514 | per unit | 2 C/R: No FS: All gas to all gas | Total residential storage natural gas water heaters | 13 | 2020 | 1) % savings: 1.5 EF; target COP of 2.2, based on ThermoLift Vuilleumier cycle heat pump (Source: Comparative Analysis of Current Thermally-Driven Refrigeration Devices, ThermoLift, Inc.) Converted to 1.5 using a 0.698 conversion factor which accounts for differences between lab rating and typical field performance (Source: Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007)) 2) Costs: This is a target installed cost, based on the fact that ThermoLift aims to design a product that is cost competitive with state-of-the-art HPWH (Source: Comparative Analysis of Current Thermally-Driven Refrigeration Devices, ThermoLift, Inc.) |  | 1-58 | 13 | 13 | AEO 2014 NEMS
887 | Thermally driven heat pump water heater, targeting to replace commercial gas-fired storage water heaters with 200kBtu/hr capacity, and EF of ~0.6. Not analyzing benefits of space heating or cooling. Assume no impact on space heating and cooling of this measure. | C: Non-sorption Gas-fired HPWH* | System | 5 | 0 | Commercial | Water Heating | All gas storage water heaters | New | Energy Factor | 1.5 | 0.6 | Yes |  | 5430 | 12760.5 | 7330.5 | per unit | 2 C/R: No FS: All gas to all gas | Total energy consumption by all commercial gas storage water heaters | 13 | 2020 | 1) % savings: Assuming roughly the same EF as a residential gas-fired storage WH for standard unit (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment); for efficient unit, 2.2 is a target COP, based on ThermoLift Vuilleumier cycle heat pump (Source: Comparative Analysis of Current Thermally-Driven Refrigeration Devices, ThermoLift, Inc.) Converted to EF 1.5 using a 0.698 conversion factor which accounts for differences between lab rating and typical field performance (Source: Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007)) 2) Cost of standard unit: Average installed cost for a 200kBtu/Hr gas storage WH is $5,430 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) 3) Cost of efficient unit: Assumes the same incremental cost ratio of 2.35 as between residential baseline and state-of-the-art HPWH (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) The residentail cost is a target installed cost, based on the fact that ThermoLift aims to design a product that is cost competitive with state-of-the-art HPWH (Source: Comparative Analysis of Current Thermally-Driven Refrigeration Devices, ThermoLift, Inc.) |  | 3-3561 | 13 | 13 | AEO 2010 NEMS
888 | Residential thermoelectric HPWH will likely not exceed the efficiency of conventional high-efficiency HPWH, they do have the potential to be significantly cheaper while still providing better performance than a traditional electric resistance WH. The system intends to replace a residential baseline 50 gal, 0.92 EF electric storage WH unit. Assume no impact on space heating and cooling of this measure. | R: Thermoelectric HPWH* | System | 5 | 0 | Residential | Water Heating | All electric water heaters | New | Energy Factor | 1.6 | 0.92 | Yes |  | 615 | 1035 | 420 | per unit | 1 C/R: No FS: All electric to all electric | Total residential storage electric water heaters | 13 | 2018 | 1) Baseline unit performance: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment; 2) Efficient unit performance: Assuming TE HPWH with a 1.6 EF (Low Cost Heat Pump Water Heaters, Oct 5, 2013, http://aceee.org/files/pdf/conferences/hwf/2013/7A-pokharna.pdf) 3) Baseline unit cost: Total installed cost is $566 ($2008) (2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses) Cost adjusted from $2008 to $2014 (http://data.bls.gov/cgi-bin/cpicalc.pl) 4) Efficient unit cost: TARGET Installed Cost -Assuming $200 increase in retail price for TE HP (Source: Low Cost Heat Pump Water Heaters, Oct 5, 2013, http://aceee.org/files/pdf/conferences/hwf/2013/7A-pokharna.pdf) -Assuming $344 for product cost of baseline electric WH (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses), Cost adjusted from $2008 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl) -Assuming $491 for installation cost, based on installation cost for typical HPWH (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses), Cost adjusted from $2008 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl) |  | 1-69 | 13 | 13 | AEO 2014 NEMS
890 | A grey-water-source heat pump water heater can greatly reduce WH energy consumption when replacing a standard electric stoarage WH with 54kW capacity and thermal efficiency of 98%, especially in commercial buildings that have high WH loads (restaurants, laundromats, hotels, etc.) by recovering heat in grey water replacing electric storage WH via a water-to-water heat pump. Assume no impact on space heating and cooling of this measure. | C: Grey-Water HPWH* | System | 5 | 0 | Commercial | Water Heating | All electric storage water heaters | New | Energy Factor | 2.4 | 0.92 | Yes |  | 5430 | 9200 | 3770 | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by all commercial electric storage water heaters | 13 | 2016 | 1) Baseline unit performance: Assuming roughly the same EF as a residential gas-fired storage WH for standard unit (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment) 2) Efficient unit performance: Assuming roughly the same performance as a ground-source heat pump, 3.5 COP (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) -Converting to 2.4 EF using a 0.698 conversion factor which accounts for differences between lab rating and typical field performance (Source: Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007)) 3) Baseline unit cost: Average installed cost for a 54 kW electric storage WH is $5,430 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) 4) Efficient unit cost: TARGET Installed Cost -Assuming a 48kBtu/Hr ground-source heat pump has a retail equipment cost of $7,000 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) -Assuming roughly 30% of that cost represents the water-to-air heat pump gives a cost of $2,100 (Source: COST CONTAINMENT FOR GROUND-SOURCE HEAT PUMPS, S. Kavanaugh, http://geoheat.oit.edu/pdf/tp72.pdf) -Assuming that the water-to-air heat pump is a reasonable proxy for a water-to-water heat pump and scaling this cost up to 200,000 kBtu/Hr capacity gives a cost of $8,750, and adding 40% for installation gives $12,250 -Assuming a 25% cost reduction for improved design results in a target installed cost of roughly $9,200 |  | 3-3562 | 13 | 13 | AEO 2010 NEMS
891 | Heat pump water heater connected directly to a PV array (i.e., without grid interconnection). It may utilize DC compressor and other components to avoid need for DC-AC converter. Baseline technology is assumed to be a typical residential electric storage WH with 50 gal tank and 0.92 EF. Assume no impact on space heating and cooling of this measure. | R: PV-assisted HPWH* | System | 5 | 0 | Residential | Water Heating | All electric storage water heaters | New | Energy Usage, kWh/yr | 340 | 2250 | Yes |  | 615 | 4590 | 3975 | per unit | 1 C/R: No FS: All electric to all electric | Total residential electric storage water heaters energy consumption in homes suitable for PV installations (35% of homes) | 13 | 2016 | DOE WH R&D Roadmap Initiative "Develop optimal configurations for PV assisted HPWH by supporting lab testing and product development efforts " 1) Baseline unit performance: Assuming an average electric water heater consumes 2550 kwh/yr (2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 7 - Energy Use Chara) 2) Efficient unit performance: Average water heating energy use of HPWH (COP of 2.4) is 1830 kWh/yr (www.geappliances.com/heat-pump-hot-water-heater/water-heater-features.htm) -Using a PV Array with (4) 300W panels for a total of 1.2kW installed on a home in Boston MA would produce ~1490 kWh/Yr (usable), (PVWatts) In a best case scenario, 100% of the electricity output can all be used for water heating. The system will use 340 kWh/yr of site electricity. 3) Baseline unit cost: Total installed cost is $566 ($2008) (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses) Cost adjusted from $2008 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl) 4) Efficient unit cost: TARGET Installed Cost 5$/Watt Installed cost of PV; 1.2 kW of PV for $6,000 -Total installed cost for a HPWH is $1,517 ($2008) (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses), Cost adjusted to $1,654, from $2008 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl) -Assumes 40% achievable price reduction for 2030 target - including PV reduction to $3/W or less and additional HPWH reductions. -Added costs for PV to HPWH control module offset by no need for grid interconnection |  | 1-70 | 13 | 13 | AEO 2014 NEMS
893 | Integrating advanced thermal storage tanks into residential gas and electric storage water heaters, thereby reducing tank losses and extending equipment lifetimes. Baseline technology is assumed to be gas-fired and electric storage WH with conventional storage tanks. | R: Adv. Thermal Storage WH* | System | 5 | 0 | Residential | Water Heating | All gas and electric water heaters | New | Energy Factor | 0.805 | 0.755 | Yes |  | N/A | N/A | 185 | per unit | 47 R: No FS: All fuels WH to all fuels WH | Total residential storage electric and natural gas water heaters | 13 | 2017 | DOE WH R&D Roadmap Initiative "Develop advanced thermal storage tanks" 1) Baseline unit performance: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment 2) Efficient unit performance: Estimated target increase 3) Incremental cost: TARGET Increase in Installed Cost based on $145 installed cost associated with increasing the insulation in a storage WH to improve 5 EF points (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses), cost adjusted from $2008 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl) Including $40 premium for longer lasting tank materials. | -Gas fired storage WH Insalled Cost: $615 -Electric storage WH Installed Cost: $1,116 | 1-71 | 13 | 20 | AEO 2014 NEMS
894 | Integrating advanced thermal storage tanks into commercial gas and electric storage water heaters, thereby reducing tank losses and extending equipment lifetimes. | C: Adv. Thermal Storage WH* | System | 5 | 0 | Commercial | Water Heating | All gas and electric water heaters | New | Energy Factor | 0.805 | 0.755 | Yes |  | N/A | N/A | 1850 | per unit | 48 C: No FS: All fuels WH to all fuels WH | Total energy consumption by all commercial storage water heaters | 13 | 2017 | DOE WH R&D Roadmap Initiative "Develop advanced thermal storage tanks" 1) Baseline unit performance: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment 2) Efficient unit performance: Estimated target increase 3) Incremental cost: TARGET Increase in Installed Cost based on $145 installed cost associated with increasing the insulation in a storage WH to improve 5 EF points (Source: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses), cost adjusted from $2008 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl). Including $40 premium for longer lasting tank materials. | -Gas fired storage WH Insalled Cost: $5,290 (200 kBtu/h) -Electric storage WH Installed Cost: $5,430 (54 kW) | 3-3560 | 13 | 20 | AEO 2010 NEMS
896 | Improved commercial HPWHs with variable capacity to meet demands of commercial building environments, particularly those with large water heating loads. Not analyzing benefits of space cooling. Baseline technology: commercial electric storage WH 54kW, TE 98%. Assume no impact on space heating and cooling of this measure. | C: Variable Capacity HPWH* | System | 5 | 0 | Commercial | Water Heating | All electric storage water heaters | New | Energy Factor | 2.8 | 0.92 | Yes |  | 5430 | 16000 | 10570 | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by all commercial electric storage water heaters | 13 | 2018 | DOE WH R&D Roadmap Initiative "Develop commercial HPWH with flexibility to meet base load demands, peak demands, and recovery time requirements" 1) Baseline unit performance: Assuming similar EF to residential electric storage WH (2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment) 2) Efficient unit performance: Assuming max performance, 4.0 COP (A.O. Smith AWH-170 Spec Sheet, http://www.hotwater.com/lit/spec/com_hp/aosze15000.pdf) -Converting to 2.8 EF using a 0.698 conversion factor which accounts for differences between lab rating and typical field performance (Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007)) 3) Baseline unit cost: Average installed cost for a 54 kW electric storage WH is $5,430 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013 4) Efficient unit cost: TARGET Installed Cost estimated using commercial rooftop heat pump as a proxy for commercial HPWH. Average equipment cost for a 90 kBtu/H rooftop heat pump is $7,325, scaling up to 200 kBtu/H equals roughly $16,000 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) |  | 3-3562 | 13 | 13 | AEO 2010 NEMS
898 | Develop more cost-effective compressors to make residential HPWH more cost competitive with conventional WH. Assume no impact on space heating and cooling of this measure. | R: Imp. HPWH Compressors* | System | 5 | 0 | Residential | Water Heating | All electric water heaters | New | Energy Factor | 2.45 | 0.92 | Yes |  | 615 | 1500 | 885 | per unit | 1 C/R: No FS: All electric to all electric | Total residential storage electric water heaters | 13 | 2018 | DOE WH R&D Roadmap Initiative "Improve compressor technologies for HPWH" 1) Baseline performance: 2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment 2) Efficient unit performance: Assuming 2.45 EF (Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) Primary EF is 0.9, Assuming 3.1 site-to-source conversion factor (DOE Buildings Energy Data Book) 3) Base unit cost: Total installed cost is $566 ($2008) (2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 8 - Life-Cycle Cost and Payback Period Analyses) -Cost adjusted from $2008 to $2014 (Source: http://data.bls.gov/cgi-bin/cpicalc.pl) 4) Efficient unit cost: This is a target installed cost, assuming a 10% reduction in the total installed cost due to reduction in cost of the compressor. Low installed cost estimate for a 50 gal, 2.45 EF HPWH is $1,710 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) |  | 1-69 | 13 | 13 | AEO 2014 NEMS
900 | Develop more cost-effective compressors to make commercial HPWH more cost competitive with conventional WH. Not analyzing benefits of space cooling. Assume no impact on space heating and cooling of this measure. | C: Imp. HPWH Compressors* | System | 5 | 0 | Commercial | Water Heating | All electric water heaters | New | Energy Factor | 2.5 | 0.92 | Yes |  | 5430 | 14400 | 8970 | per unit | 1 C/R: No FS: All electric to all electric | Total energy consumption by all commercial electric storage water heaters | 13 | 2018 | DOE WH R&D Roadmap Initiative "Improve compressor technologies for HPWH" 1) Baseline performance: Assuming similar EF to residential electric storage WH (2010 DOE Energy Conservation Standards for Residential Water Heaters TSD, Chapter 3 - Market and Technology Assessment) 2) Efficient unit performance: Assuming average performance of 3.6 COP (Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013 , and A.O. Smith AWH-170 Spec Sheet, http://www.hotwater.com/lit/spec/com_hp/aosze15000.pdf) Converting to 2.5 EF using a 0.698 conversion factor which accounts for differences between lab rating and typical field performance (Zogg, Robert, et al. "CO2 Heat pump water heaters." ASHRAE Journal (Nov, 2007)) 3) Base unit cost: Average installed cost for a 54 kW electric storage WH is $5,430 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) 4) Efficient unit cost: $14,400, this is a target installed cost, assuming a 10% reduction in the total installed cost due to reduction in cost of the compressor -Estimated using commercial rooftop heat pump as a proxy for commercial HPWH. Average equipment cost for a 90 kBtu/H rooftop heat pump is $7,325, scaling up to 200 kBtu/H equals roughly $16,000 (Source: Navigant Consulting, Inc., Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case, Sept 2013) Based on a 15,000 sq ft commercial building, assuming 200 kBtu/H water heater is appropriate for a 15,000 sq ft building |  | 3-3562 | 13 | 13 | AEO 2010 NEMS
902 | ≥R-12/in building envelope thermal insulation material that can be added to walls to retrofit existing buildings and can also be applicable to other portions of the building enclosure (e.g., reduce the impact of thermal bridging between building components). The material must meet durability requirements and minimize occupant disturbance. | R: Envelope Insulation (MYP2025)* | Walls | 5 | 0 | Residential | Building | Walls | All | R-value | 23.1 | 11.1 | Yes | Projected installed cost premium ≤$0.25/ft2, including insulation material and associated labor, assuming an R-12/in performance to enable a payback period less than 10 years. | 0 | 765.25 | 765.25 | per home; BED: 3,061 sq. ft. of insulation for a 2,272 sq. ft. single family home built in 2000 | 34 R: No FS: Wall specific | Total residential heating and cooling lost through walls in all homes | 30 | 2025 | R&D Roadmap for Emerging Window and Building Envelope Technologies 2014. | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 1-177 | 30 | 30 | AEO 2014 NEMS
903 | ≥R-12/in building envelope thermal insulation material that can be added to walls to retrofit existing buildings and can also be applicable to other portions of the building enclosure (e.g., reduce the impact of thermal bridging between building components). The material must meet durability requirements and minimize occupant disturbance. | C: Envelope Insulation (MYP2025)* | Walls | 5 | 0 | Commercial | Building | Walls | All | R-value | 29 | 17 | Yes | Projected installed cost premium ≤$0.25/ft2, including insulation material and associated labor, assuming an R-12/in performance to enable a payback period less than 10 years. | 0 | 0.135 | 0.135 | per square foot; wall to floor space ratio of 0.9, window fill ratio of 0.4 | 35 C: No FS: Wall specific | Total heating and cooling load due to energy loss through walls in all commercial buildings | 40 | 2025 | R&D Roadmap for Emerging Window and Building Envelope Technologies 2014. | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 3-3677 | 40 | 40 | AEO 2010 NEMS
904 | A system capable of concurrently regulating heat, air, and moisture flow to achieve the following performance specifications: <1 ACH50 | R: Air-Sealing, (MYP2025)* (N) | Infiltration | 5 | 0 | Residential | Building | Infiltration control | Single family, new | Energy savings (%) | 67% | 0% | Yes | Projected installed cost premium of ≤$0.5/ft2 (0.22-0.82, 0.5 is average) finished floor (25% of current average costs, including mechanical ventilation costs). | 0 | 1136 | 1136 | per home; BED: 2000, 2,272 sq ft single family home | 5 R: No FS: All fuels HVAC (heating+cooling, no separate ventilation component) | Total heating and cooling in all new single-family homes | 30 | 2025 | R&D Roadmap for Emerging Window and Building Envelope Technologies 2014. | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 1-123 | 30 | 30 | AEO 2014 NEMS
905 | A system capable of concurrently regulating heat, air, and moisture flow to achieve the following performance specifications: <1 ACH51 | R: Air-Sealing, (MYP2025)* (E) | Infiltration | 5 | 0 | Residential | Building | Infiltration control | Single family, existing | Energy savings (%) | 90% | 0% | Yes | 0.25 * (0.84-3.1, which is an avgerage of 2)$/Conditioned Floor Area | 0 | 1136 | 1136 | per home; BED: 2000, 2,272 sq ft single family home | 5 R: No FS: All fuels HVAC (heating+cooling, no separate ventilation component) | Pre-2010 homes heating and cooling: Single family | 30 | 2025 | R&D Roadmap for Emerging Window and Building Envelope Technologies 2014. | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 1-137 | 30 | 30 | AEO 2014 NEMS
906 | A system capable of concurrently regulating heat, air, and moisture flow to achieve the following performance specifications: <0.25 CFM75/ft2 (5-sided envelope) | C: Air-Sealing (MYP2025)* | Infiltration | 5 | 0 | Commercial | Building | Infiltration control | All | CFM/ft2@75 Pa | 0.25 | 1.38 | Yes |  | 0 | 0.5 | 0.5 | per square foot of floor space | 41 C: No FS: Infiltration specific | All commercial heating and cooling lost due to infiltration | 40 | 2025 | R&D Roadmap for Emerging Window and Building Envelope Technologies 2014. | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. Cost numbers require more attention! Bohac et al. study indicates cost ranges $1.2 - $15 /CFM saved for baselines ranging in air tightness from 0.15 to 0.31 CFM/ft @75 Pa. | 3-3638 | 40 | 40 | AEO 2010 NEMS
907 | Residential Advanced Vapor Compression Technologies (MYP 2020) | R: Adv. Vapor Compression (MYP2020)* | System | 5 | 0 | Residential | HVAC | Heat pump | All | Energy Savings (%) | 34% | 0 | Yes | Simple payback = 5 years |  |  | 0.45 | per square foot of floor space | 1 C/R: No FS: All electric to all electric | Remainder of all residential and commercial electric heating and cooling | 15 | 2020 | Tony Bouza |  | 1-167 | 15 | 15 | AEO 2014 NEMS
908 | Residential Target Air Source Integrated Heat Pump (2-speed and variable speed, electric) | R: Air-Source IHP (MYP2020)* | System | 5 | 0 | Residential | HVAC | Heat pump | All | Energy Savings (%) | 46% | 0 | Yes | $0.33 for commercial building and 2914 per home with avg home sqft of 1819 ==> 1.6; the avg sqft of r to sqft of c is 18 ==> weighted avg premium per sqft is (18*1.6+0.33)/19 = 1.53 |  |  | 1.53 | per square foot of floor space | 1 C/R: No FS: All electric to all electric | 30% of Residential and Commercial IHP market (30% of electric heating, electric WH, and proportion of cooling) | 15 | 2020 | Tony Bouza |  | 1-168 | 15 | 15 | AEO 2014 NEMS
909 | Residential Target Air Source Cold Climate Heat Pump | R: Air-Source Cold Climate HP (MYP2020)* | System | 5 | 0 | Residential | HVAC | Heat pump | All | Energy Savings (%) | 46% | 0 | Yes | Simple payback = 5 years |  |  | 2.08 | per square foot of floor space | 1 C/R: No FS: All electric to all electric | Residential and Commercial Electric Heating + proportion of cooling in buildings with electric heating in CZ 1&2 | 15 | 2020 | Tony Bouza |  | 1-138 | 15 | 15 | AEO 2014 NEMS
910 | Residential Target Non-Vapor Compression HVAC systems (magnetocaloric, electrocaloric and others) | R: Non-vapor Compr. HVAC (MYP2020)* | System | 5 | 0 | Residential | HVAC | Heat pump | All | Energy Savings (%) | 40% | 0 | Yes | Simple payback = 5 years |  |  | 0.4 | per square foot of floor space | 1 C/R: No FS: All electric to all electric | Commercial and residential NIK gradual market entry for all electric heating and cooling | 15 | 2020 | Tony Bouza |  | 1-169 | 15 | 15 | AEO 2014 NEMS
911 | Residential Target Gas Engine Driven HP | R: Gas Engine HP (MYP2020)* | System | 5 | 0 | Residential | HVAC | Heat pump | All | Energy Savings (%) | 42% | 0 | Yes | Simple payback = 5 years |  |  | 1.03 | per square foot of floor space | 2 C/R: No FS: All gas to all gas | Residential and Commercial Gas Heating and Gas Cooling | 15 | 2020 | Tony Bouza |  | 1-139 | 15 | 15 | AEO 2014 NEMS
912 | Target Gas Heat Pump Heating | R+C: Gas Heat Pump (MYP2020)* | System | 5 | 0 | Residential and Commercial | HVAC | Heat pump | all | Energy Savings (%) | 40% | 0 | Yes | Simple payback = 5 years |  |  | 0.98 | per square foot of floor space | 2 C/R: No FS: All gas to all gas | Residential and Commercial Gas Heating and Gas Cooling | 15 | 2020 | Tony Bouza |  | 1-139 | 15 | 15
913 | Target Residential heat pump clothes dryers | R: HP Clothes Dryer (MYP2020)* | System | 5 | 0 | Residential | Washing & Drying | Standard-Capacity Clothes Dryer | All | Energy Savings (%) | 50% | 0% | Yes | See existing & efficient costs |  |  | 500 | per unit | 1 C/R: No FS: All electric to all electric | Total energy use by all electric clothes dryers | 12 | 2020 | Tony Bouza |  | 1-42 | 12 | 12 | AEO 2014 NEMS
914 | Target residential advanced compressor for refrigeration | R: Compressor Refrig.(MYP2020)* | System | 5 | 0 | Residential | Refrigeration | Rfrg/Frz | All | Energy Savings (%) | 20% | 0% | Yes | See incremental cost |  |  | 100 | per unit | 1 C/R: No FS: All electric to all electric | Residential Refrigerators and Freezers (excluding non-vapor compression refrigeration, assuming its entrance into market in 2016 with 20% market share by 2030 | 17 | 2020 | Program goal | program goal based on current effort by Whirlpool through ARRA funded project | 1-170 | 17 | 17 | AEO 2014 NEMS
915 | Target Advanced Refrigeration | R: Adv Refrigerator (MYP2020)* | System | 5 | 0 | Residential | Refrigeration | Rfrg/Frz | all | Energy Savings (%) | 50% | 0% | Yes | See incremental cost |  |  | 250 | per unit | 1 C/R: No FS: All electric to all electric | Residential Refrigerators and Freezers (excluding non-vapor compression refrigeration, assuming its entrance into market in 2016 with 20% market share by 2030 | 17 | 2020 | Program goal | program goal based on current effort by Whirlpool through ARRA funded project | 1-170 | 17 | 17 | AEO 2014 NEMS
916 | Target Non-Vapor Compression Refrigeration (magnetocaloric) | R: Non-Vapor Compr. Refrig.(MYP2020)* | System | 5 | 0 | Residential | Refrigeration | Rfrg/Frz | all | Energy Savings (%) | 60% | 0% | Yes | See incremental cost |  |  | 300 | per unit | 1 C/R: No FS: All electric to all electric | Residential Non Vapor Compression Refrigeration (assuming its entrance into market in 2016 with 20% market share by 2030) | 17 | 2020 | Program goal | program goal based on current effort by Whirlpool through ARRA funded project | 1-171 | 17 | 17 | AEO 2014 NEMS
917 | Target commercial advanced compressor for refrigeration | C: Compressor Refrig.(MYP2020)* | Compressor | 5 | 0 | Commercial | Refrigeration | Food Prep Table, Reach-In Rfgr/Frz, Bev Machines, Vending Machines | all | Energy Savings (%) | 10% | 0% | Yes | $138-$201 |  |  | 1000 | per unit | 1 C/R: No FS: All electric to all electric | All commercial compressors (DC) | 15 | 2020 |  |  | 3-3512 | 15 | 15 | AEO 2010 NEMS
918 | Target Advanced Refrigeration | C: Adv Refrigerator (MYP2020)* | System | 5 | 0 | Commercial | Refrigeration | Rfrg/Frz | Various | Energy Savings (%) | 10% | 0% | Yes | $23-171 |  |  | 1000 | per unit | 1 C/R: No FS: All electric to all electric | All commercial refrigeration equipment (including compressors, excluding condensers and non-vapor compression refrigeration, assuming its entrance into market in 2016 with 20% market share by 2030) | 12 | 2020 |  |  | 3-3813 | 12 | 12 | AEO 2010 NEMS
919 | Target Non-Vapor Compression Refrigeration (magnetocaloric) | C: Non-Vapor Compr. Refrig.(MYP2020)* | System | 5 | 0 | Commercial | Refrigeration | Rfrg/Frz | Various | Energy Savings (%) | 10% | 0% | Yes | $23-171 |  |  | 1000 | per unit | 1 C/R: No FS: All electric to all electric | Commercial Non-vapor Compression Refrigeration | 12 | 2020 |  |  | 3-3812 | 12 | 12 | AEO 2010 NEMS
920 | Target for non-CO2 vapor compression HPWH (MYP 2020). Similar to measure #526. Assume no impact on space heating and cooling of this measure. | R: Non-CO2 Vap-Comp HPWH (MYP2020)* | System | 5 | 0 | Residential | Water Heating | All electric storage water heaters | New | Energy Factor | 2.5815 | 0.92 | Yes | Target cost premium per first hour rating $8.13/gal; typical installed capacity in 2013: 50 gal. Typical installed cost: $640. | 640 | 1046.5 | 406.5 | per unit | 1 C/R: No FS: All electric to all electric | Total residential storage electric water heaters | 13 | 2020 | 1) Performance and cost targets from MYP 2014 Report; 2) Baseline cost and performance from EIA- Technology Forecast Updates - Residential and Commercial Building Technologies- Reference Case. September 2013. |  | 1-69 | 13 | 13 | AEO 2014 NEMS
921 | Target for CO2 vapor compression HPWH (MYP 2020). Similar to measure #525. Assume no impact on space heating and cooling of this measure. | R: CO2 Vap-Comp HPWH (MYP2020)* | System | 5 | 0 | Residential | Water Heating | All electric storage water heaters | New | Energy Factor | 2.9958 | 0.92 | Yes | Target cost premium per first hour rating $11.94/gal; typical installed capacity in 2013: 50 gal. Typical installed cost: $640. | 640 | 1237 | 597 | per unit | 1 C/R: No FS: All electric to all electric | Total residential storage electric water heaters | 13 | 2020 | 1) Performance and cost targets from MYP 2014 Report; 2) Baseline cost and performance from EIA- Technology Forecast Updates - Residential and Commercial Building Technologies- Reference Case. September 2013. |  | 1-69 | 13 | 13 | AEO 2014 NEMS
922 | Target for non-vapor compression HPWH (MYP 2020). Similar to measure #798. Assume no impact on space heating and cooling of this measure. | R:Non-Vap-comp HPWH (MYP2020)* | System | 5 | 0 | Residential | Water Heating | All electric storage water heaters | New | Energy Factor | 1.6572 | 0.92 | Yes | Target cost premium per first hour rating $4/gal; typical installed capacity in 2013: 50 gal. Typical installed cost: $640. | 640 | 840 | 150 | per unit | 1 C/R: No FS: All electric to all electric | Total residential storage electric water heaters | 13 | 2020 | 1) Performance and cost targets from MYP 2014 Report; 2) Baseline cost and performance from EIA- Technology Forecast Updates - Residential and Commercial Building Technologies- Reference Case. September 2013. |  | 1-69 | 13 | 13 | AEO 2014 NEMS
923 | Target for gas-fired absorption or adsorption HPWH (MYP 2020). Assume no impact on space heating and cooling of this measure. | R: Ab/Ad-sorption Gas HPWH (MYP2020)* | System | 5 | 0 | Residential | Water Heating | All gas storage water heaters | New | Energy Factor | 1.2 | 0.59 | Yes | Target cost premium per first hour rating $7.14/gal; typical installed capacity in 2013: 40 gal. Typical installed cost: $1000 | 1000 | 1285.6 | 285.6 | per unit | 2 C/R: No FS: All gas to all gas | Total residential storage natural gas water heaters | 13 | 2020 | 1) Performance and cost targets from MYP 2014 Report; 2) Baseline cost and performance from EIA- Technology Forecast Updates - Residential and Commercial Building Technologies- Reference Case. September 2013. |  | 1-58 | 13 | 13 | AEO 2014 NEMS
925 | Optimize whole-building control system (new software) that controls the operation of multiple systems to minimize costs based on a variety of inputs, such as occupancy, weather, fuel prices, etc. This measure is applicable to systems in large buildings (>100,000 sq.ft.) with poorly performing control systems. It also includes retro-commissioning (adjustment of thermostats, schedules, set points, calibration. It does not include equipment replacement (bad sensors, frozen dampers, etc.)) - will be an extra cost. | C: Bldg Control Opt. (all bldgs)* | Controls | 2+ | 0 | Commercial | HVAC/Lighting | Building controls | All commercial buildings | Energy Savings (%) | 20% | 0% | Yes | Assume similar cost for all buildings as for buildings > 100,000 SF, EMCS cost (assuming similar to EIS) of $1.36/sq.ft. (TIAX). Automatic optimization software to achieve similar savings would cost an additional $100,000 per 100,000 sq.ft. more, to a total incremental cost of $2.36/sq.ft. (EMCS+OWBCS combined) | 0 | 2.36 | 2.36 | per square foot of floor space | 14 C: No FS: HVAC and lighting | All HVAC and Lighting energy use in commercial buildings | 15 | 2015 | 1) Savings and costs from pg. 9-91,93,95,139 of TIAX. Energy Impact of Commercial Building Controls and Performance Diagnostics: Market Characterization, Energy Impact of Building Faults and Energy Savings Potential. November 2005. “Overall, it would appear that the first cost of an OWBCS associated with an EMCS would be similar to the cost of a higher-end Whole Building Diagnostics implementation less the cost of additional sensors, i.e. on the order of $100,000.” Adding the costs of the EMCS, which is assumed to be similar to EIS of $1.36/sq.ft (pg. 9-136), and the OWBCS for a 100,000 sq.ft. building gives a cost of $2.36/sq.ft. | This measure was developed directly based on measure #719. Savings and costs were assumed to be similar. Better data is necessary in order to more accurately represent this measure. TIAX: "Heating: 10%, Cooling 20%, Ventilation 0%." "Overall it would appear the first cost of an OWBCS associated with an EMCS would be similar to the cost of a higher-end Whole Building Diagnostics implementation less the cost of additional sensors, i.e., on the order of $100,000" Installed cost of an EIS for a 100,000 ft2 office building was $136,000. Assumes an EMS is required ($136,000) plus an additional $100,000 for the OWBCS controls/sensors/software. Assumes 20% savings for EMS alone followed by 10% for OWBCS. | 3-3483 | 15 | 15 | AEO 2010 NEMS
937 | Upgrade medium or small sized office buildings (<100,000SF) from standalone thermostat control design to a building automation system control design (HVAC benefit only), which includes new thermostats that communicate with BAS head-end; wireless temperature sensors to cover 50% of the office spaces; communications network which allows for sharing and configuration of common data points like ouside air temp, occupancy and holiday scheduling, trend logs and historical data; whole building electrical metering system that provides real-time and historical data naalysis of the building; holiday scheduling, optimal start capability, schedules tightened, auto night low and high limits set, 4F dead band gap created, and auto air low temp override added. The buildings had rooftop heat pump units, and were located in Richland, Washington. | C: Bldg Auto System (<100,000SF) | Controls | 5 | 3 | Commercial | HVAC | Building controls | Small and medium commercial buildings (<100,000 ft2) | Energy Savings (%) | 22% | 0% | Yes | $20,000 installed cost for the entire system upgrade for a 20,530 SF building. | 0 | 1 | 1 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | All HVAC energy use in small and medium commercial buildings <100,000 sq.ft. | 15 | 2013 | Cost and energy savings from Small- and Medium Sized Commercial Building Monitoring and Controls Needs: A Scoping Study. Katipamula, Underhill, Goddard, Taasevigen, Piette, Granderson, et al. PNNL 22169. October 2012. pg. 48-54. | Case study analyzed three 20,530 sq.ft single story on concrete slab office buildings designed for 80-90 occupants with 11 all electric rooftop heat pump units (except 1 unit). Buildings were selected based on primary problem encountered by the oeprational staff being occupant complaints related to comfort (too hot/too cold). Assume savings would be similar for buildings that use gas furnaces and RTUs. | 3-3486 | 15 | 15 | AEO 2010 NEMS
938 | Demonstrate and deploy smart thermostat that uses occupancy sensors to automatically turn off the HVAC system when the occupants are sleeping or away from home. The wireless motion and door sensors cost ~$5 each off the shelf and can be installed in minutes using double-sided tape. The smart thermostat has a fast reaction algorithm with a probabilistic model that uses these sensors and processes the sensor data to quickly estimate whether occupants are active, sleeping, or away. This algorithm can typically respond within minutes of the occupants leaving the house, without introducing false vacancy detections. Second, the system combines historical occupancy patterns with on-line sensor data to decide whether to preheat the home or to heat after the occupants arrive. Finally, the system saves additional energy by using deep setback, allowing the temperature to drift further from the setpoint temperature when it is confident that the home is unoccupied. | R: Smart Thermostats (UVA) | Controls | 5 | 2 | Residential | Building | Building controls | All | Energy Savings (%) | 28% | 0% | Yes | Sensors: $5/each; 3-5 per home (p.2) | 0 | 25 | 25 | per home | 5 R: No FS: All fuels HVAC (heating+cooling, no separate ventilation component) | Total residential central AC and heating energy consumption | 35 | 2016 | Energy savings and cost - pg. 1 of The Smart Thermostat: Using Occupancy Sensors to Save Energy in Homes. Jiakang Lu, Tamim Sookoor, et al. University of Virginia. SenSys November 305, 2010. |  | 1-101 | 35 | 35 | AEO 2014 NEMS
940 | Demonstrate and deploy demand control ventilation with an a cheaper metal-oxide indoor air quality sensor that will enable demand control ventilation in compliance with the ASHRAE standard 61-1989. | C: DCV, VOC metal-oxide sensors | Use intensity | 2+ | 1 | Commercial | Ventilation | Control | All | Energy Savings (%) | 15% | 0% | Yes | ORNL (David Fugate/Teja): $50 per sensor node. Metal oxide sensors that sense indoor air quality are highly correlated with presence of CO2 and are approximated to be $50 cheaper than standard CO2 sensors. |  | 0.15622 | 0.15622 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | All commercial HVAC energy use | 15 | 2018 | 1) Measures is based on #141, which showed 20% savings for DCV, however, because VOC/metal oxide sensors seems more sensitive/will do more ventilation work, potential savings were reduced by 25%. This is based on Figures 6 & 7 of Beyond CO2: Sensing VOCs in Indoor Air Protects Health, Saves Energy. Applied Sensor White Paper. https://www.appliedsensor.com/pdfs/IndoorAirQuality_WhitePaper_0609.pdf) 2) Cost was based on a form submitted by ORNL and email confirmation from Teja Kuruganti that claimed $50/metal oxide sensor cost. Hence cost of #141 C: DCV was taken and reduced by $50 (derivation explanation can be found in notes). Final cost per sq.ft. was not significantly affected. | Cost discrepancies between info form data submitted by ORNL and actual final incremental cost deduction: "ORNL $50/ metal oxide sensor sensor, but their original estimate of $600/ CO2 sensor (resulting in reduction of $550/sensor) then does not seem consistent with any of our other DCV measures. Looking at #870 and #141 both have DCV data coming from good recently published reports. Report for #141 used different assumptions, but if we use same assumptions as #870 of typical RTU size and 1ton/280 sq.ft, cost of #141 is coming out to be $0.73/sq.ft., which is very consistent compared to $1/sq.ft. for #870 from a different report. Hence $617/zone (or $1028 /RTU, installed) being slightly lower than $1400/RTU, installed makes total sense. From NCI Report: “Sand (2004) studied the various U.S. installations of DCV and their usage. He found that sensors typically retailed for $200-250 with installation costs of $600-700 per zone for new construction. For retrofit situations, he determined that systems using direct digital controls (DDC) cost $700-900 per zone while those using pneumatic controls cost $900-1200 per zone. Hong and Fisk (2010) modeled DCV for various office buildings in 5 California climates. They estimated typical installation costs of $617 per zone and an average total cost of $.173/sq.ft.” It is also recommended 1 sensor per zone (NCI report), hence $617 total DCV cost would include ~3-5 sensors which by 2009 must have been < $100-$150 /installed CO2 sensor (assuming 5 zones, 3 RTUs and 1 sensor/zone or perhaps per RTU). Given metal oxide cost per sensor of $50 (uninstalled), is at most $50/sensor reduction in installed sensor cost in 2009. | 3-3617 | 15 | 15 | AEO 2010 NEMS
943 | Develop and evaluate techniques for separate sensible and latent control for residential central A/Cs. Air-conditioning systems remove both sensible heat (temperature) and latent heat (the energy required to evaporate or condense water) from supply air to create comfortable conditions for building occupants. Many options for latent control exist, but typically as an add-on component and may increase energy consumption. Incorporating these technologies into packaged solutions can lower the installation cost/ complexity, especially for retrofit applications, and better coordinate the control of sensible and latent cooling mechanisms. | R: Latent Heat Controls Package to replace CAC and ASHP cooling (HVAC RM)* | Controls | 5 | 0 | Residential | Cooling | A/C |  | Energy Savings (%) | 30% | 0% | Yes | Assumes cost premium equal to residential high efficiency central A/Cs from EIA Technology Forecast Update | 2300 | 5300 | 3000 | per home, 3 ton model | 1 C/R: No FS: All electric to all electric | Total residential cooling (CAC & ASHP) other than room A/Cs | 16 | 2020 | 1. Savings estimated from Ling et al. 2010 "Enhancement of the Separate Sensible and Latent Cooling Air-Conditioning Systems" and similar research papers 2. Cost premium: Assumes cost premium equal to residential high efficiency central A/Cs from EIA Technology Forecast Update 3. Lifetime: Median of Residential central A/C from EIA Technology Forecast Update |  | 1-21 | 16 | 16 | AEO 2014 NEMS
944 | Develop and evaluate techniques for separate sensible and latent control for residential room A/Cs. Air-conditioning systems remove both sensible heat (temperature) and latent heat (the energy required to evaporate or condense water) from supply air to create comfortable conditions for building occupants. Many options for latent control exist, but typically as an add-on component and may increase energy consumption. Incorporating these technologies into packaged solutions can lower the installation cost/ complexity, especially for retrofit applications, and better coordinate the control of sensible and latent cooling mechanisms. | R: Latent Heat Controls Package for Room A/C (HVAC RM)* | Controls | 5 | 0 | Residential | Cooling | A/C |  | Energy Savings (%) | 30% | 0% | Yes | Assumes cost premium equal to residential high efficiency room A/Cs from EIA Technology Forecast Update | 440 | 600 | 160 | per unit, 10.5 kBtu/hr model | 1 C/R: No FS: All electric to all electric | All residential cooling using room A/Cs | 10 | 2020 | 1. Savings estimated from Ling et al. 2010 "Enhancement of the Separate Sensible and Latent Cooling Air-Conditioning Systems" and similar research papers 2. Cost premium: Assumes cost premium equal to residential high efficiency room A/Cs from EIA Technology Forecast Update 3. Lifetime: Median of Residential room A/C from EIA Technology Forecast Update |  | 1-12 | 10 | 10 | AEO 2014 NEMS
945 | Develop and evaluate techniques for separate sensible and latent control for rooftop A/C units and ASHPs. Air-conditioning systems remove both sensible heat (temperature) and latent heat (the energy required to evaporate or condense water) from supply air to create comfortable conditions for building occupants. Many options for latent control exist, but typically as an add-on component and may increase energy consumption. Incorporating these technologies into packaged solutions can lower the installation cost/ complexity, especially for retrofit applications, and better coordinate the control of sensible and latent cooling mechanisms. | C: Latent Heat Controls Package (HVAC RM)* | Controls | 5 | 0 | Commercial | Cooling | A/C |  | Energy Savings (%) | 30% | 0% | Yes | Assumes cost premium equal to commercial high efficiency Rooftop unit from EIA Technology Forecast Update | 4.3095 | 12.1429 | 7.8333 | per sqft, 7.5 ton model, 280 sqft/ton | 1 C/R: No FS: All electric to all electric | Total commercial cooling by RTUs and ASHPs | 15 | 2020 | 1. Savings estimated from Ling et al. 2010 "Enhancement of the Separate Sensible and Latent Cooling Air-Conditioning Systems" and similar research papers 2. Cost premium: Assumes cost premium equal to commercial high efficiency Rooftop unit from EIA Technology Forecast Update 3. Lifetime: Commercial Rooftop Unit AC from EIA Technology Forecast Update |  | 3-3750 | 15 | 15 | AEO 2010 NEMS
946 | Develop electrochemical compression systems to replace residential central AC and ASHP heating. Electrochemical compressors raise the pressure of a hydrogen working fluid using a proton exchange membrane and electricity source, and replace motor-driven compressors for a heat pump system. Additional development is needed to develop the technology, working fluids, and system aspects to drive a vapor-compression cycle. | R: Electrochemical Compressors to replace CAC & ASHP* | System | 5 | 0 | Residential | Heating & Cooling | HVAC |  | Energy Savings (%) | 20% | 0% | Yes | Xergy estimates $55 incremental cost for 1-ton compressor, assumes other costs are equal, Xergy presentation 2013 http://aceee.org/files/pdf/conferences/hwf/2013/7A-bahar.pdf | 0 | 165 | 165 | per unit, 3 ton model | 1 C/R: No FS: All electric to all electric | Total residential cooling by CAC and ASHPs as well as ASHP heating | 18 | 2020 | 1. Savings estimates from Xergy presentation 2013 http://aceee.org/files/pdf/conferences/hwf/2013/7A-bahar.pdf 2. Cost premium: Xergy estimates $55 incremental cost for 1-ton compressor, assumes other costs are equal, Xergy presentation 2013 http://aceee.org/files/pdf/conferences/hwf/2013/7A-bahar.pdf 3. Lifetime: Median of Residential central A/C from EIA Technology Forecast Update |  | 1-178 | 18 | 18 | AEO 2014 NEMS
947 | Develop electrochemical compression systems to replace room ACs. Electrochemical compressors raise the pressure of a hydrogen working fluid using a proton exchange membrane and electricity source and replace motor-driven compressors for a heat pump system. Additional development is needed to develop the technology, working fluids, and system aspects to drive a vapor-compression cycle. | R: Electrochemical Compressors to replace room AC* | System | 5 | 0 | Residential | Heating & Cooling | HVAC |  | Energy Savings (%) | 20% | 0% | Yes | Xergy estimates $55 incremental cost for 1-ton compressor, assumes other costs are equal, Xergy presentation 2013 http://aceee.org/files/pdf/conferences/hwf/2013/7A-bahar.pdf | 0 | 55 | 55 | per unit, 10.5 kBtu/hr model | 1 C/R: No FS: All electric to all electric | All residential cooling using room A/Cs | 9 | 2020 | 1. Savings estimates from Xergy presentation 2013 http://aceee.org/files/pdf/conferences/hwf/2013/7A-bahar.pdf 2. Cost premium: Xergy estimates $55 incremental cost for 1-ton compressor, assumes other costs are equal, Xergy presentation 2013 http://aceee.org/files/pdf/conferences/hwf/2013/7A-bahar.pdf 3. Lifetime: Median of Residential room A/C from EIA Technology Forecast Update |  | 1-12 | 9 | 9 | AEO 2014 NEMS
948 | Develop electrochemical compression systems to replace rooftop AC units (RTUs) and ASHP's cooling and heating. Electrochemical compressors raise the pressure of a hydrogen working fluid using a proton exchange membrane and electricity source and replace motor-driven compressors for a heat pump system. Additional development is needed to develop the technology, working fluids, and system aspects to drive a vapor-compression cycle. | C: Electrochemical Compressors to replace RTUs & ASHPs* | System | 5 | 0 | Commercial | Heating & Cooling | HVAC |  | Energy Savings (%) | 20% | 0% | Yes | Xergy estimates $55 incremental cost for 1-ton compressor, assumes other costs are equal, Xergy presentation 2013 http://aceee.org/files/pdf/conferences/hwf/2013/7A-bahar.pdf | 0 | 0.19643 | 0.19643 | per sqft, 7.5 ton model, 280 sqft/ton | 1 C/R: No FS: All electric to all electric | All commercial cooling by ASHPs and RTUs; and heating by ASHPs | 15 | 2020 | 1. Savings estimates from Xergy presentation 2013 http://aceee.org/files/pdf/conferences/hwf/2013/7A-bahar.pdf 2. Cost premium: Xergy estimates $55 incremental cost for 1-ton compressor, assumes other costs are equal, Xergy presentation 2013 http://aceee.org/files/pdf/conferences/hwf/2013/7A-bahar.pdf 3. Lifetime: Commercial Rooftop Unit AC from EIA Technology Forecast Update |  | 3-3755 | 15 | 15 | AEO 2010 NEMS
949 | Develop techniques to raise heat pump performance at low-ambient temperature; consider elimination of defrost (or frost buildup) and backup heat sources to improve the application of cold-climate heat pumps. Traditionally, vapor-compression heat pumps have had limited use in colder climates due to decreasing heating capacity and COP as outdoor temperatures decrease because of the increased temperature lift across the compressor. Several technologies could improve heat pump performance at low-ambient conditions and improve electric or gas heat pump efficiency in colder climates. | R: Cold Climate HP to replace ASHP* | System | 5 | 0 | Residential | Heating | Heat Pump |  | Energy Savings (%) | 25% | 0% | Yes | Navigant assumption of $3000 premium from Residential HVAC Report | 0 | 3000 | 3000 | per unit, 3 ton model | 1 C/R: No FS: All electric to all electric | Total residential electric heating using ASHP | 15 | 2020 | 1. Savings estimated from Navigant Residential HVAC Report 2. Cost premium: Navigant assumption of $3000 premium from Residential HVAC Report 3. Lifetime: Median of residential central ASHPs, from EIA Technology Forecast Update |  | 1-175 | 15 | 15 | AEO 2014 NEMS
950 | Develop techniques to raise heat pump performance at low-ambient temperature; consider elimination of defrost (or frost buildup) and backup heat sources to improve the application of cold-climate heat pumps. Traditionally, vapor-compression heat pumps have had limited use in colder climates due to decreasing heating capacity and COP as outdoor temperatures decrease because of the increased temperature lift across the compressor. Several technologies could improve heat pump performance at low-ambient conditions and improve electric or gas heat pump efficiency in colder climates. | R: Cold Climate Gas HP to replace gas heating* | System | 5 | 0 | Residential | Heating | Furnace/boiler |  | Energy Savings (%) | 40% | 0% | No | Navigant assumption of $3000 premium from Residential HVAC Report | 0 | 3000 | 3000 | per unit, 3 ton model | 2 C/R: No FS: All gas to all gas | Total residential heating using natural gas furnaces and boilers | 15 | 2020 | 1. Savings estimated from Navigant Residential HVAC Report 2. Cost premium: Navigant assumption of $3000 premium from Residential HVAC Report 3. Lifetime: Residential gas-fired heat pump from EIA Technology Forecast Update |  | 1-174 | 15 | 15 | AEO 2014 NEMS
951 | Develop techniques to raise heat pump performance at low-ambient temperature; consider elimination of defrost (or frost buildup) and backup heat sources to improve the application of cold-climate heat pumps. Traditionally, vapor-compression heat pumps have had limited use in colder climates due to decreasing heating capacity and COP as outdoor temperatures decrease because of the increased temperature lift across the compressor. Several technologies could improve heat pump performance at low-ambient conditions and improve electric or gas heat pump efficiency in colder climates. | C: Cold Climate HP to replace ASHP* | System | 5 | 0 | Commercial | Heating | Heat Pump |  | Energy Savings (%) | 25% | 0% | Yes | Navigant assumption of $4000 premium Residential and Commercial HVAC Report | 0 | 1.9 | 1.9048 | per sqft, 7.5 ton model, 280 sqft/ton | 1 C/R: No FS: All electric to all electric | Total commercial ASHP heating | 15 | 2020 | 1. Savings estimated from Navigant Commercial HVAC Report 2. Cost premium: Navigant assumption of $4000 premium Residential and Commercial HVAC Report 3. Lifetime: Commercial central ASHPs, from EIA Technology Forecast Update |  | 3-3794 | 15 | 15 | AEO 2010 NEMS
952 | Develop techniques to raise heat pump performance at low-ambient temperature; consider elimination of defrost (or frost buildup) and backup heat sources to improve the application of cold-climate heat pumps. Traditionally, vapor-compression heat pumps have had limited use in colder climates due to decreasing heating capacity and COP as outdoor temperatures decrease because of the increased temperature lift across the compressor. Several technologies could improve heat pump performance at low-ambient conditions and improve electric or gas heat pump efficiency in colder climates. | C: Cold Climate Gas HP to replace gas heating* | System | 5 | 0 | Commercial | Heating | Furnace/boiler |  | Energy Savings (%) | 40% | 0% | No | Navigant assumption of $4000 premium Residential and Commercial HVAC Report | 0 | 1.9 | 1.9048 | per sqft, 7.5 ton model, 280 sqft/ton | 2 C/R: No FS: All gas to all gas | Total natural gas heating | 15 | 2020 | 1. Savings estimated from Navigant Residential HVAC Report, because systems will use modular units of similar technology to residential 2. Cost premium: Navigant assumption of $4000 premium Residential and Commercial HVAC Report 3. Lifetime: Commercial Gas-Fired Engine-Driven Rooftop Air Conditioners from EIA Technology Forecast Update |  | 3-3805 | 15 | 15 | AEO 2010 NEMS
953 | Develop non-VC cooling systems (Thermoelectric, magnetic, etc.) to replace residential ASHP heating with suitable efficiency, cost, and performance compared to next generation HVAC equipment. This measure intends to replace residential ASHP heating. Various non-vapor compression cooling cycles exist that offer the potential for significant energy savings over current and future vapor-compression systems, but require additional development before wide commercialization for HVAC systems. | R: Non-VC System to replace ASHP for heating* | System | 5 | 0 | Residential | Heating | HVAC |  | Energy Savings (%) | 25% | 0% | Yes | Assumes cost premium equal to residential high efficiency central ASHPs from EIA Technology Forecast Update | 3300 | 4500 | 1200 | per unit, 3 ton model | 1 C/R: No FS: All electric to all electric | Total residential electric heating using ASHP | 15 | 2025 | 1. Savings estimated from Navigant Non-Vapor-Compression Report, vuilleumier and magnetocaloric heating 2. Cost premium: Assumes cost premium equal to residential high efficiency central ASHPs from EIA Technology Forecast Update 3. Lifetime: Median of residential central ASHPs, from EIA Technology Forecast Update |  | 1-175 | 15 | 15 | AEO 2014 NEMS
954 | Develop non-VC cooling systems (Thermoelectric, magnetic, etc.) to replace commercial ASHP heating with suitable efficiency, cost, and performance compared to next generation HVAC equipment. Various non-vapor compression cooling cycles exist that offer the potential for significant energy savings over current and future vapor-compression systems, but require additional development before wide commercialization for HVAC systems. | C: Non-VC System to replace ASHP for heating* | System | 5 | 0 | Commercial | Heating | HVAC |  | Energy Savings (%) | 25% | 0% | Yes | Assumes cost premium equal to commercial high efficiency Rooftop unit from EIA Technology Forecast Update | 4.3095 | 12.1667 | 7.8571 | per sqft, 7.5 ton model, 280 sqft/ton | 1 C/R: No FS: All electric to all electric | Total commercial ASHP heating | 15 | 2025 | 1. Savings estimated from Navigant Non-Vapor-Compression Report, vuilleumier and magnetocaloric heating 2. Cost premium: Assumes cost premium equal to commercial high efficiency Rooftop unit from EIA Technology Forecast Update 3. Lifetime: Commercial central ASHPs, from EIA Technology Forecast Update |  | 3-3794 | 15 | 15 | AEO 2010 NEMS
955 | Develop non-VC cooling systems (Thermoelectric, magnetic, etc.) to replace all residential cooling other than room ACs with suitable efficiency, cost, and performance compared to next generation HVAC equipment. Various non-vapor compression cooling cycles exist that offer the potential for significant energy savings over current and future vapor-compression systems, but require additional development before wide commercialization for HVAC systems. | R: Non-VC System to replace CAC* | System | 5 | 0 | Residential | Cooling | HVAC |  | Energy Savings (%) | 40% | 0% | Yes | Assumes cost premium equal to residential high efficiency central A/Cs from EIA Technology Forecast Update | 2300 | 5300 | 3000 | per unit, 3 ton model | 1 C/R: No FS: All electric to all electric | Total residential cooling (CAC & ASHP) other than room A/Cs | 16 | 2025 | 1. Savings estimated from Navigant Non-Vapor-Compression Report, thermoelastic and membrane cooling 2. Cost premium: Assumes cost premium equal to residential high efficiency central A/Cs from EIA Technology Forecast Update 3. Lifetime: Median of Residential central A/C from EIA Technology Forecast Update |  | 1-21 | 16 | 16 | AEO 2014 NEMS
956 | Develop non-VC cooling systems (Thermoelectric, magnetic, etc.) to replace all room AC cooling with suitable efficiency, cost, and performance compared to next generation HVAC equipment. Various non-vapor compression cooling cycles exist that offer the potential for significant energy savings over current and future vapor-compression systems, but require additional development before wide commercialization for HVAC systems. | R: Non-VC System to replace Room AC* | System | 5 | 0 | Residential | Cooling | HVAC |  | Energy Savings (%) | 40% | 0% | Yes | Assumes cost premium equal to residential high efficiency room A/Cs from EIA Technology Forecast Update | 440 | 600 | 160 | per unit, 10.5 kBtu/hr model | 1 C/R: No FS: All electric to all electric | All residential cooling using room A/Cs | 10 | 2025 | 1. Savings estimated from Navigant Non-Vapor-Compression Report, thermoelastic and membrane cooling 2. Cost premium: Assumes cost premium equal to residential high efficiency room A/Cs from EIA Technology Forecast Update 3. Lifetime: Median of Residential room A/C from EIA Technology Forecast Update |  | 1-12 | 10 | 10 | AEO 2014 NEMS
957 | Develop non-VC cooling systems (Thermoelectric, magnetic, etc.) to replace commercial cooling by RTUs and ASHPs with suitable efficiency, cost, and performance compared to next generation HVAC equipment. Various non-vapor compression cooling cycles exist that offer the potential for significant energy savings over current and future vapor-compression systems, but require additional development before wide commercialization for HVAC systems. | C: Non-VC System to replace RTU and ASHP cooling* | System | 5 | 0 | Commercial | Cooling | HVAC |  | Energy Savings (%) | 40% | 0% | Yes | Assumes cost premium equal to commercial high efficiency Rooftop unit from EIA Technology Forecast Update | 4.3095 | 12.1429 | 7.8333 | per sqft, 7.5 ton model, 280 sqft/ton | 1 C/R: No FS: All electric to all electric | Total commercial cooling by RTUs and ASHPs | 15 | 2025 | 1. Savings estimated from Navigant Non-Vapor-Compression Report, thermoelastic and membrane cooling 2. Cost premium: Assumes cost premium equal to commercial high efficiency Rooftop unit from EIA Technology Forecast Update 3. Lifetime: Commercial Rooftop Unit AC from EIA Technology Forecast Update |  | 3-3750 | 15 | 15 | AEO 2010 NEMS
958 | Develop hybrid systems to combine mechanical and natural ventilation techniques, aka mixed-mode conditioning or integrated window ventilation. When conditions allow, automatic window dampers can allow outside air into a space and offset ventilation and/or cooling provided by mechanical systems. | C: Hybrid Mechanical & Natural Ventilation* | Windows | 5 | 0 | Commercial | HVAC | HVAC |  | Energy Savings (%) | 15% | 0% | Yes | Assumes $5/SF from NSF/IUCRC. 2004. “Guidelines for High Performance Buildings 2004.” | 0 | 5 | 5 | per sqft | 61 Manual | Total commercial cooling and ventilation | 40 | 2022 | 1. Savings estimated from LBNL http://www.cbe.berkeley.edu/mixedmode/aboutmm.html 2. Cost premium: Assumes $5/SF from NSF/IUCRC. 2004. “Guidelines for High Performance Buildings 2004.” 3. Lifetime for efficient unit: Navigant estimate for lifetime, assumes motor/actuator replacement and maintenance 4. Lifetime for old unit is set at the expected life of a window. |  | 3-3806 | 40 | 15 | AEO 2010 NEMS
959 | Investigate new absorption pairs, compact heat exchangers, and other material advances to reduce the cost of absorption systems for residential gas heating applications. Absorption systems utilize thermal energy to drive a heat-pump cycle where a refrigerant is cyclically absorbed and desorbed from a secondary fluid, but barriers exist with regard to size/weight, operating risk, and cost compared to conventional systems. Advances in absorption pairs, heat and mass exchanger designs, and other advances could improve their viability for residential systems. | R: Advances in Absorption Gas Systems* | System | 5 | 0 | Residential | Heating | Furnace/boiler |  | Energy Savings (%) | 40% | 0% | No | Estimated as residential gas heat pump (low range) against furnace for EIA Technology Forecast Update | 2300 | 12000 | 9700 | per unit, 75kBtu model | 2 C/R: No FS: All gas to all gas | Total residential heating energy use by natural gas furnaces in all homes. | 15 | 2022 | 1. Savings estimated from Navigant Residential HVAC Report 2. Cost premium: Estimated as residential gas heat pump (low range) against furnace for EIA Technology Forecast Update 3. Lifetime: Residential gas-fired heat pump from EIA Technology Forecast Update |  | 1-46 | 15 | 15 | AEO 2014 NEMS
960 | Investigate new absorption pairs, compact heat exchangers, and other material advances to reduce the cost of absorption systems for commercial gas heating applications. Absorption systems utilize thermal energy to drive a heat-pump cycle where a refrigerant is cyclically absorbed and desorbed from a secondary fluid, but barriers exist with regard to size/weight, operating risk, and cost compared to conventional systems. Advances in absorption pairs, heat and mass exchanger designs, and other advances could improve their viability for light commercial systems. | C: Advances in Absorption Gas Systems* | System | 5 | 0 | Commercial | Heating | Furnace/boiler |  | Energy Savings (%) | 40% | 0% | No | Estimated as 200% increase (Navigant Residential HVAC Report) on gas-fired boiler ($22.3k per 800kBtuh) for EIA Technology Forecast Update | 22300 | 66900 | 1.7422 | per sqft, 40 ton model serving 15,000 sqft (~32 SF/kBtuh from previous Ptool runs) | 2 C/R: No FS: All gas to all gas | Total natural gas heating | 15 | 2022 | 1. Savings estimated from Navigant Residential HVAC Report 2. Cost premium: Estimated as 200% increase (Navigant Residential HVAC Report) on gas-fired boiler ($22.3k per 800kBtuh) for EIA Technology Forecast Update 3. Lifetime: Residential gas-fired heat pump from EIA Technology Forecast Update (commercial will be similar to modular residential) |  | 3-3805 | 15 | 15 | AEO 2010 NEMS
961 | Develop a direct-current (DC)-powered HVAC system to utilize DC power from a solar photovoltaic (PV) system ,or other distributed DC generation, without inverter losses and facilitate micro grid integration. As one of the largest building loads, HVAC systems designed for DC-power would reduce the losses normally incurred from conversion of solar PV and battery electricity to AC power. While some products exist for telecommunications, electronics, and transportation systems, research into DC-based air conditioners could enable greater usage of microgrid and renewable systems. | R: DC-powered HVAC* | System | 5 | 0 | Residential | Heating & Cooling | Heat Pump |  | Energy Savings (%) | 66% | 0% | Yes | Baseline cost for 1-ton ductless minisplit assumed as 50% of 3-ton split system. Efficient unit costs obtained from Hotspot Energy http://www.hotspotenergy.com/DC-air-conditioner/DC-AC-Complete-Systems.php | 1150 | 5870 | 4720 | per unit, 1 ton | 1 C/R: No FS: All electric to all electric | Total residential cooling by CAC and ASHPs as well as ASHP heating | 18 | 2018 | 1. Savings assumed by eliminating site-to-source losses 2. Cost premium: Baseline cost for 1-ton ductless minisplit assumed as 50% of 3-ton split system. Efficient unit costs obtained from Hotspot Energy http://www.hotspotenergy.com/DC-air-conditioner/DC-AC-Complete-Systems.php 3. Lifetime: Median of Residential central A/C from EIA Technology Forecast Update |  | 1-178 | 18 | 18 | AEO 2014 NEMS
962 | Develop less expensive magnets for magnetocaloric cooling systems. Magnetocaloric cooling systems can potentially provide space cooling (and potentially heating) without high-GWP refrigerants, but requires further advances on cost, size, weight, etc. | R: Magnets for magnetocaloric systems to replace CAC and ASHP heating* | System | 5 | 0 | Residential | Heating & Cooling | Heat Pump |  | Energy Savings (%) | 20% | 0% | Yes | Assumes cost premium equal to residential high efficiency central A/Cs from EIA Technology Forecast Update | 2300 | 5300 | 3000 | per unit, 3 ton model | 1 C/R: No FS: All electric to all electric | Total residential cooling by CAC and ASHPs as well as ASHP heating | 18 | 2025 | 1. Savings estimated from Navigant Non-Vapor-Compression Report 2. Cost premium: Assumes cost premium equal to residential high efficiency central A/Cs from EIA Technology Forecast Update 3. Lifetime: Median of Residential central A/C from EIA Technology Forecast Update |  | 1-178 | 18 | 18 | AEO 2014 NEMS
963 | Develop less expensive magnets for magnetocaloric cooling systems. Magnetocaloric cooling systems can potentially provide space cooling (and potentially heating) without high-GWP refrigerants, but requires further advances on cost, size, weight, etc. | R: Magnets for magnetocaloric room AC cooling* | System | 5 | 0 | Residential | Cooling | Heat Pump |  | Energy Savings (%) | 20% | 0% | Yes | Assumes cost premium equal to residential high efficiency room A/Cs from EIA Technology Forecast Update | 440 | 600 | 160 | per unit, 10.5 kBtu/hr model | 1 C/R: No FS: All electric to all electric | All residential cooling using room A/Cs | 10 | 2025 | 1. Savings estimated from Navigant Non-Vapor-Compression Report 2. Cost premium: Assumes cost premium equal to residential high efficiency room A/Cs from EIA Technology Forecast Update 3. Lifetime: Median of Residential room A/C from EIA Technology Forecast Update |  | 1-12 | 10 | 10 | AEO 2014 NEMS
964 | Develop less expensive magnets for magnetocaloric cooling systems. Magnetocaloric cooling systems can potentially provide space cooling (and potentially heating) without high-GWP refrigerants, but requires further advances on cost, size, weight, etc. | C: Magnets for magnetocaloric systems to replace RTU and ASHP* | System | 5 | 0 | Commercial | Heating & Cooling | Heat Pump |  | Energy Savings (%) | 20% | 0% | Yes | Assumes cost premium equal to commercial high efficiency Rooftop unit from EIA Technology Forecast Update | 4.3095 | 12.1429 | 7.8333 | per sqft, 7.5 ton model, 280 sqft/ton | 1 C/R: No FS: All electric to all electric | All commercial cooling by ASHPs and RTUs; and heating by ASHPs | 15 | 2025 | 1. Savings estimated from Navigant Non-Vapor-Compression Report 2. Cost premium: Assumes cost premium equal to commercial high efficiency Rooftop unit from EIA Technology Forecast Update 3. Lifetime: Commercial Rooftop Unit AC from EIA Technology Forecast Update |  | 3-3755 | 15 | 15 | AEO 2010 NEMS
965 | Develop methods, technologies, and other innovations to easily integrate seasonal energy storage. Thermal energy storage allows heating and cooling loads to be met by low-cost energy produced at a different time, including the integration of renewables, or improves the seasonal efficiency of GSHPs. Currently high cost of installation, design, etc. prohibit usage. | R: Seasonal Thermal Energy Storage* | Distribution | 5 | 0 | Residential | Heating | Furnace/boiler |  | Energy Savings (%) | 30% | 0% | No | Cost estimate for 20m^3 storage system in addition to baseline furnace/boiler at $600/m^3 (@$1.35/1 Euro) from http://www.rhc-platform.org/fileadmin/Events/4_-_Kerskes_seasonal_TES.pdf | 0 | 1200 | 1200 | per unit, 75 kbtu model | 61 Manual | Total primary and secondary heating (electricity, distillate, geothermal, LPG and Kerosene) | 25 | 2020 | 1. Savings estimated at 30% based on solar thermal system storage, can vary much higher, http://www.itw.uni-stuttgart.de/dokumente/Publikationen/publikationen_03-09.pdf 2. Cost premium: Cost estimate for 20m^3 storage system in addition to baseline furnace/boiler at $600/m^3 (@$1.35/1 Euro) from http://www.rhc-platform.org/fileadmin/Events/4_-_Kerskes_seasonal_TES.pdf 3. Lifetime: Navigant assumption for minimal maintenance and degradation over time |  | 1-48 | 25 | 25 | AEO 2014 NEMS
966 | Develop methods, technologies, and other innovations to easily integrate seasonal energy storage. Thermal energy storage allows heating and cooling loads to be met by low-cost energy produced at a different time, including the integration of renewables, or improves the seasonal efficiency of GSHPs. Currently high cost of installation, design, etc. prohibit usage. | C: Seasonal Thermal Energy Storage* | Distribution | 5 | 0 | Commercial | Heating | Furnace/boiler |  | Energy Savings (%) | 30% | 0% | No | Cost estimate for large scale hot water storage system $4.7/SF (@$1.35/1 Euro)based on survey of Systems http://www.itw.uni-stuttgart.de/dokumente/Publikationen/publikationen_03-09.pdf, and costs from http://www.rhc-platform.org/fileadmin/Events/4_-_Kerskes_seasonal_TES.pdf | 0 | 4.7 | 4.7 | per sqft | 9 C: No FS: All fuels heating | All commercial heating | 15 | 2020 | 1. Savings estimated at 30% based on solar thermal system storage, can vary much higher, http://www.itw.uni-stuttgart.de/dokumente/Publikationen/publikationen_03-09.pdf 2. Cost premium: Cost estimate for large scale hot water storage system $4.7/SF (@$1.35/1 Euro)based on survey of Systems http://www.itw.uni-stuttgart.de/dokumente/Publikationen/publikationen_03-09.pdf, and costs from http://www.rhc-platform.org/fileadmin/Events/4_-_Kerskes_seasonal_TES.pdf 3. Lifetime: Navigant assumption for minimal maintenance and degradation over time |  | 3-3626 | 15 | 15 | AEO 2010 NEMS
967 | Research strategies to improve ground-source heat pump (GSHP) ground-loop cost and performance; also consider siting, installation, and modeling to reduce costs. GSHPs utilize the relatively stable temperatures of the ground, water, or other thermal mass, as a thermal source/sink for a heat pump, decreasing the temperature lift compared to air-systems. Currently high cost of installation, design, etc. prohibit usage. | R: GSHP - only HVAC* | System | 5 | 0 | Residential | Heating & Cooling | Heat Pump |  | Energy Savings (%) | 30% | 0% | Yes | Assumes cost premium equal to commercial GSHP (low estimate) vs. standard commercial ASHP from EIA Technology Forecast Update | 2300 | 10000 | 7700 | per unit, 3 ton model | 1 C/R: No FS: All electric to all electric | All electric heating, proportion of cooling in homes with electric heating | 20 | 2020 | 1. Savings estimate from Navigant Residential HVAC Report 2. Cost premium: Assumes cost premium equal to commercial GSHP (low estimate) vs. standard commercial ASHP from EIA Technology Forecast Update 3. Lifetime: Residential GSHP from EIA Technology Forecast Update |  | 1-124 | 20 | 25 | AEO 2014 NEMS
968 | Research strategies to improve ground-source heat pump (GSHP) ground-loop cost and performance; also consider siting, installation, and modeling to reduce costs. GSHPs utilize the relatively stable temperatures of the ground, water, or other thermal mass, as a thermal source/sink for a heat pump, decreasing the temperature lift compared to air-systems. Currently high cost of installation, design, etc. prohibit usage. | C: GSHP - only HVAC* | System | 5 | 0 | Commercial | Heating & Cooling | Heat Pump |  | Energy Savings (%) | 30% | 0% | Yes | Assumes cost premium equal to residential GSHP (low estimate) vs. standard central ASHP from EIA Technology Forecast Update | 7700 | 16500 | 4.1905 | per sqft, 7.5 ton model, 280 sqft/ton | 1 C/R: No FS: All electric to all electric | Total commercial electric heating and proportion of cooling in buildings with electric heating | 16 | 2020 | 1. Savings estimate from Navigant Residential HVAC Report 2. Cost premium: Assumes cost premium equal to residential GSHP (low estimate) vs. standard central ASHP from EIA Technology Forecast Update 3. Lifetime: Commercial GSHP from EIA Technology Forecast Update |  | 3-3804 | 15 | 25 | AEO 2010 NEMS
969 | Improving Buildings Energy Performance by Integrating non-Energy Plus Energy Modeling in the Design Stage, New Buildings | C: Modeling Integration in Building Design (N) | Whole building | 4 | 3 | Commercial | All End Uses | Whole building | New commercial buildings | Energy Savings (%) | 15% | 0% | Yes | Not available; assumed based on Amir Roth email on Monday 6/3/2013 "max adoption lens" with $30,000 per project plus $0.1 /sqft and using data from http://buildingsdatabook.eren.doe.gov/TableView.aspx?table=3.2.5 we find that the stock weighted average incremental cost is $0.33/sft |  |  | 0 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | Total HVAC load in new commercial buildings | 40 | 2013 | 2013 AIA 2030 Commitment Annual Report (to be published on the AIA website soon) 1) No good incremental cost data available, costs were estimated to be similar to EnergyPlus integration modeling #878; 2) The energy savings estimates are for architectural firms that are participating in the AIA 2030 Commitment. These are generally large architecture firms that we consider to be aggressive in pursuing energy efficiency (i.e. data is not from a random or representative sample) 3) The energy savings estimate is for the marginal energy savings improvement of simulation/integrative design measures on building designs that already meet “beyond-code prescriptive” performance levels 4) Modeling improves all areas of building consumption, although currently savings were only applied to HVAC because that's the largest active component and because we don't have good data at this point to partition the savings at a finer granularity. | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 3-3639 | 40 | 40 | AEO 2010 NEMS
970 | Improving Buildings Energy Performance by Integrating non-Energy Plus Energy Modeling in the Design Stage, Existing Buildings | C: Modeling Integration in Building Retrofit (E) | Whole building | 4 | 3 | Commercial | All End Uses | Whole building | Retrofit commercial buildings | Energy Savings (%) | 7.5% | 0% | Yes | Not available; assumed based on Amir Roth email on Monday 6/3/2013 "max adoption lens" with $30,000 per project plus $0.1 /sqft and using data from http://buildingsdatabook.eren.doe.gov/TableView.aspx?table=3.2.5 we find that the stock weighted average incremental cost is $0.33/sft |  |  | 0 | per square foot | 6 C: No FS: All fuels HVAC (heating+cooling+ventilation) | Total HVAC load in existing commercial buildings | 40 | 2013 | 2013 AIA 2030 Commitment Annual Report (to be published on the AIA website soon) 1) This measure is based on #969, but due to retrofit applications was estimated to be half the benefit of new construction. 2) Modeling improves all areas of building consumption, although currently savings were only applied to HVAC because that's the largest active component and because we don't have good data at this point to partition the savings at a finer granularity. | Expected and new equipment lifetimes are assumed - we do not have a good source to support this assumption. | 3-3798 | 40 | 40 | AEO 2010 NEMS
983 | Commercialize and deploy advanced sequential dual evaporator cycle in residential refrigeration applications. It provides individual cooling needs of freezer and fresh food compartments; uses a single compressor and a three way diverter valve to deliver refrigerant to dual evaporators; improves refrigerator COP by operating the fresh food compartment evaporator at a higher temperatrue and pressure than the freezer compartment evaporator. | R: Sequential Dual Evaporator in Refrigerators | System | 5 | 2 | Residential | Refrigeration | Rfrg/Frz | All | Energy Savings (%) | 20% | 0% | Yes | See incremental cost |  |  | 100 | per unit | 1 C/R: No FS: All electric to all electric | All residential refrigerators and freezers | 17 | 2016 | 1) Saving and incremental cost from pg. D-20 of DOE BTP Building R&D Breakthroughs: Technologies and Products supported by the Building Technologies Program. April 2012. | This technology has not been commercialized because it ended up being slightly more expensive than what the company originally expected. | 1-92 | 17 | 17 | AEO 2014 NEMS
986 | UTRC and University of Illinois, Urbana Champaign with funding from DOE in 2013 designed, developed and demonstrated a safe, very low global warming potential, and very high performance air conditioning (VHPAC) residential system. Direct GWP reduction: >350X, one prototype has shown 31% reduction in energy consumpmtion, and 25% reduction in outdoor unit size. | R: Natural Refrigerant AC System | System | 2+ | 2 | Residential | Cooling | A/C | Central | Energy Savings (%) | 30% | 0% | Yes | Derived based on a 3 year payback. |  |  | 451.6313 | per home; 3 ton | 1 C/R: No FS: All electric to all electric | Total residential cooling (CAC & ASHP) other than room A/Cs | 16 | 2015 | 1) Energy savings from Y. Feng; P. Verma; J. Wang; F. Zhao, etc. Natural Refrigerant Very High Efficiency Residential AC System. United Technologies Research Center. May 20th, 2013. DOE Award #: DE-EE0003955. http://www.osti.gov/scitech/servlets/purl/1081327 2) Expected incremental costs were not provided in the report. Cost was estimated based on a typcial 3 year payback. | This technology is market ready, but has not been introduced because UTRC is waiting for the market to accept the idea of using a small amount of flamable working fluid outside the home. European market may be more agreeable to this type of configuration in the near future. | 1-21 | 16 | 16 | AEO 2014 NEMS
987 | Energy Star Specification in 2010 Residential Electric Heating | R: Energy Star Electric Heating | System | 2+ | 3 | Residential | Heating | Heat Pump | All | HSPF | 8.2 | 8 | Yes |  | 4950 | 6450 | 1500 | per unit, 36 kBTU/h model | 1 C/R: No FS: All electric to all electric | Total residential electric heating using ASHP | 15 | 2010 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010. |  | 1-175 | 15 | 15 | AEO 2014 NEMS
988 | Energy Star Specification in 2010 for Residential Central Air Conditioning | R: Energy Star CAC | System | 2+ | 3 | Residential | Cooling | A/C | All | SEER | 14.5 | 13 | Yes |  | 3000 | 4100 | 1100 | per home; 3 ton | 1 C/R: No FS: All electric to all electric | Total energy consumption by residential central air conditioning in single- and multi-family homes | 17 | 2010 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010. |  | 1-13 | 17 | 17 | AEO 2014 NEMS
989 | Energy Star Specification in 2010 Residential Electric Water Heating | R: Energy Star Electric WH | System | 2+ | 3 | Residential | Water Heating | Water heater, electric | All | Energy Factor | 2 | 0.9 | Yes |  | 575 | 1850 | 1275 | per unit | 1 C/R: No FS: All electric to all electric | Total electric water heating energy consumption | 13 | 2010 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010. |  | 1-53 | 13 | 13 | AEO 2014 NEMS
990 | Energy Star Specification in 2010 Residential Refrigeration | R: Energy Star Refrigeration | System | 2+ | 3 | Residential | Refrigeration | Rfrg/Frz | All | kWh/yr | 408 | 453 | Yes |  | 500 | 525 | 25 | per unit | 1 C/R: No FS: All electric to all electric | All residential refrigerators and freezers | 16 | 2010 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010. |  | 1-92 | 16 | 16 | AEO 2014 NEMS
991 | Residential Electric Dryer (No Energy Star Spec in 2010, only 2015. Took high performance for 2010.) | R: Energy Star Electric Dryer (2015) | System | 2+ | 3 | Residential | Washing & Drying | All electric clothes dryers | All | lb/kWh | 3.16 | 3.01 | Yes |  | 550 | 750 | 200 | per unit | 1 C/R: No FS: All electric to all electric | Total energy use by all electric clothes dryers | 12 | 2010 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010. | Vented standard-sized electric clothes dryers make up 98.5% of the total electric clothes dryer market. Clothes Dryer Product Class Market Shares: Table 9.3.1 from TSD 2011: Vented Electric Standard: 77.7%; vented electric compact 120V: 0.2%; vented electric compact 240V: 0.8%; Vented gas: 20.9%; ventless electric compact (240V): 0.5%; ventless combination washer/dryer: 0.5%. | 1-42 | 12 | 12 | AEO 2014 NEMS
992 | Energy Star Specification in 2010 Residential Gas Heating (furnaces and boilers) | R: Energy Star Gas Heating | System | 2+ | 3 | Residential | Heating | Furnace/ boiler | All | AFUE | 0.88 | 0.79 | Yes | $9/kBTU/hr | 2900 | 3500 | 600 | per unit | 2 C/R: No FS: All gas to all gas | Total residential heating using natural gas furnaces and boilers | 15 | 2010 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010. |  | 1-174 | 15 | 15 | AEO 2014 NEMS
993 | Energy Star Specification in 2010 Residential Gas Water Heating | R: Energy Star Gas WH | System | 2+ | 3 | Residential | Water Heating | All gas storage water heaters | All | Energy Factor | 0.67 | 0.59 | Yes |  | 940 | 1245 | 305 | per unit | 2 C/R: No FS: All gas to all gas | Total gas water heating energy consumption | 13 | 2010 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010. |  | 1-61 | 13 | 13 | AEO 2014 NEMS
994 | Energy Star Specification in 2010 Commercial Electric Heating | C: Energy Star Electric Heating | System | 2+ | 3 | Commercial | Heating | Heat Pump | All | COP | 3.4 | 3.3 | Yes |  | 3.2857 | 4.1429 | 1.9048 | per sqft, 7.5 ton model, 280 sqft/ton | 1 C/R: No FS: All electric to all electric | Total commercial ASHP heating | 15 | 2010 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010. |  | 3-3794 | 15 | 15 | AEO 2010 NEMS
995 | Energy Star Specification in 2010 Commercial Electric Cooling | C: Energy Star Electric Cooling (RTU+ASHP) | System | 2+ | 3 | Commercial | Cooling | RTUs/HP | All | SEER | 14.5 | 14 | Yes |  | 3.5476 | 4.3333 | 0.78571 | per sqft, 7.5 ton model, 280 sqft/ton | 1 C/R: No FS: All electric to all electric | Total commercial cooling by RTUs and ASHPs | 15 | 2010 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010. |  | 3-3750 | 15 | 15 | AEO 2010 NEMS
996 | Energy Star Specification in 2010 Commercial Reach-in Solid-door Refrigerators and Freezers (according to CRE rulemaking solid door is the typical unit) | C: Energy Star Refrigeration and Freezers | System | 2+ | 3 | Commercial | Refrigeration | Rfrg/Frz | All | kWh/day | 8.5232 | 12.9676 | Yes | Weighted average cost for Energy Star reach-in solid-door freezers and refrigerators | 4009.8068 | 4024.3805 | 14.5737 | per unit | 1 C/R: No FS: All electric to all electric | All commercial reach-Ins | 15 | 2011 | 1) % savings and incremental installed cost was derived from 2011 data from EIA Technology Forecast 2012 for commercial reach-in refrigerators and freezers. Costs and savings were derived using a weighted average based on installed market base. |  | 3-3502 | 15 | 15 | AEO 2010 NEMS
998 | Energy Star Specification in 2010 for Cooling using Residential Air Source Heat Pumps | R: Energy Star ASHP Cooling | System | 2+ | 3 | Residential | Cooling | A/C | All | SEER | 14.5 | 13 | Yes |  | 4950 | 6450 | 1500 | per home; 36 kBTU/h capacity | 1 C/R: No FS: All electric to all electric | Total residential cooling using ASHP | 17 | 2010 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010. |  | 1-35 | 17 | 17 | AEO 2014 NEMS
1011 | Building Energy Management Open Source Software (BEMOSS) platform was developed by Virginia Tech, which has a user interface for three plug-and-play compatible controllers - one each for HVAC, lighting and plug load control. The BEMOSS platform is expected to improve energy efficiency and demand response implementation. | C: BEMOSS (<50,000SF) | Controls | 2+ | 3 | Commercial | All End Uses | All | All small commercial buildings (<50,000 ft2) | Energy Savings (%) | 30% | 0% | Yes | Not available; assumed 5 year simple payback | 0 | 5.45 | 5.45 | per square foot | 60 C: No FS: All fuels/end-uses | All HVAC and lighting energy use in small commercial buildings <50,000 ft | 10 | 2014 | 1) Energy reduction estimate of approximately 30% - this is the sum of all the EUI reductions shown on page 104 of the "Status Update" document, which simulated the effect of advanced control options in small EPlus offices. 2) Installed cost: the "SmallMediumBuildingControlsScopingStudy" document gives two estimates on page 48-49 which would yield a 3 and 5 year payback for an owner. We used the one associated with the 20,000 square feet commercial building (5 year payback), to be consistent with the energy savings estimate. This is listed as $109,000 (or $5.45/sf). |  | 3-3485 | 10 | 10 | AEO 2010 NEMS
1012 | CRADA with Hill Phoenix: Transcritical CO2 Market Refrigeration System (Advansor System) | C: Transcritical CO2 Refrigeration System | System | 2+ | 3 | Commercial | Refrigeration | Rfrg/Frz | All | Energy Savings (%) | 25% | 0% | Yes | Not available; assumed 5 year simple payback |  |  | 628008 | per unit | 1 C/R: No FS: All electric to all electric | All supermarket refrigeration systems (cond, comp, walk-ins, & display) | 12 | 2013 | 1) Energy Savings: 25% from High Efficiency Low Emission Refrigeration System. 2014 BTO Peer Review Presentation. ORNL. From Tony Bouza: Developed prototype system (CO2 transcritical booster) and fabricated prototype refrigeration system. CRADA partner (Hill Phoenix) plans to deploy low emission, high efficiency systems in 2014 (Potential for transcritical CO2 system: 39% more efficient and 78% less emissions than baseline systems). 2) No cost data. Incremental cost was calculated based on a 5 year simple payback. |  | 3-3507 | 12 | 12 | AEO 2010 NEMS
1013 | Engine Driven Heat Pump in commercial buildings. This measure is similar to #680, except it's performance is based on NextAire Packaged Gas Heat Pump developed by IntelliChoice Energy, with assistance from Southwest Gas Corporation and ORNL, commercialized in 2010. | C: NextAire Engine Driven HP (FS to gas) | System | 2+ | 3 | Commercial | Heating & Cooling | Heat pump | Replace all electric HVAC systems in commercial buildings | COP | 1.3 | 3.2 | Yes | Measure will be about double the cost of an RTU | 9.4 | 18.8 | 9.4 | per square foot; 1 ton per 280 sq. ft. | 3 C/R: FS: All electric to all gas | Total commercial electric heating and proportion of cooling in buildings with electric heating | 15 | 2010 | 1) COP performance of 1.4 for heating and 1.1 for cooling from Buildings R&D Breakthroughs: Technologies and Products Supported by the BTP. may 2011. Page C-8. NextAire Packaged Gas Heat Pump. 2) Cost data is based on measure #680 ( Omar Abdelaziz. Oak Ridge National Laboratory. 2011. Personal communicationBaseline cost from RS Means Assemblies Cost Data, 33rd Edition ($9.4/ft2 for twenty single-zone RTUs, 2 tons each, including ductwork and controls) |  | 3-3804 | 15 | 15 | AEO 2010 NEMS
1014 | Energy Star Specification in 2010 for Cooling using Residential Geothermal Heat Pumps | R: Energy Star GSHP Cooling | System | 2+ | 3 | Residential | Cooling | GSHP | All | EER | 16.1 | 13.4 | Yes |  | 10000 | 11000 | 1000 | per home; 36 kBTU/h capacity | 1 C/R: No FS: All electric to all electric | Total residential cooling using GSHP | 25 | 2010 | 1) % savings, incremental installed cost, and lifetime from EIA Technology Forecast 2010. |  | 1-36 | 25 | 25 | AEO 2014 NEMS
1015 | Energy Star Specification in 2010 for Heating using Residential Geothermal Heat Pumps | R: Energy Star GSHP Heating | System | 2+ | 3 | Residential | Heating | GSHP | All | COP | 3.5 | 3.1 | Yes |  | 10000 | 11000 | 1000 | per home; 36 kBTU/h capacity | 1 C/R: No FS: All electric to all electric | Total residential heating using GSHP | 25 | 2010 | 1) % savings, incremental installed cost, and lifetime from EIA Technology Forecast 2010. |  | 1-50 | 25 | 25 | AEO 2014 NEMS
1016 | Energy Star Specification in 2010 Residential LPG Heating (furnaces and boilers) | R: Energy Star LPG Furnace | System | 2+ | 3 | Residential | Heating | Furnace/ boiler | All | AFUE | 0.88 | 0.79 | Yes | $9/kBTU/hr | 2900 | 3500 | 600 | per unit | 61 Manual | Total residential heating using LPG furnaces or other LPG heating equipment | 15 | 2010 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010. |  | 1-51 | 15 | 15 | AEO 2014 NEMS
1017 | Energy Star Specification in 2010 Residential Solar with Electric Back-Up Water Heating | R: Energy Star Solar WH, Electric BU | System | 5 | 3 | Residential | Water Heating | Solar WH: indirect, active | All | Solar Fraction (SF) | 0.5 | 1 | Yes |  | 575 | 8800 | 8225 | per unit | 1 C/R: No FS: All electric to all electric | Total electric water heating energy consumption | 13 | 2010 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010. |  | 1-53 | 13 | 13 | AEO 2014 NEMS
1018 | Energy Star Specification in 2010 Residential Solar with Gas Back-Up Water Heating | R: Energy Star Solar WH, Gas BU | System | 5 | 3 | Residential | Water Heating | Solar WH: indirect, active | All | Solar Fraction (SF) | 0.5 | 1 | Yes |  | 940 | 8800 | 8225 | per unit | 2 C/R: No FS: All gas to all gas | Total gas water heating energy consumption | 13 | 2010 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010. |  | 1-61 | 13 | 13 | AEO 2014 NEMS
1019 | Residential Energy Star Clothes Washer 2010 Specifications for machine energy use and hot water energy consumption | R: Energy Star CW (machine+hot water) | System | 5 | 3 | Residential | Washing & Drying | Clothes Washer |  | Energy Usage, kWh/yr | 0.5 | 1 | Yes |  | 500 | 725 | 225 | per unit | 61 Manual | Total residential clothes washer and its water heating energy use | 11 | 2010 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010. |  | 1-159 | 11 | 11 | AEO 2014 NEMS
1020 | Residential Energy Star 2010 Dishwasher for machine energy use and hot water energy consumption | R: Energy Star DW (machine+hot water) | System | 5 | 3 | Residential | Dishwashing | Dishwasher |  | Energy Usage, kWh/yr | 324 | 355 | Yes |  | 350 | 800 | 450 | per unit | 50 R: No FS: Dishwashing and its associated water heating energy use | All residential dishwashing and its water heating energy use | 19 | 2010 | 1) % savings and incremental installed cost from EIA Technology Forecast 2010. |  | 1-90 | 19 | 19 | AEO 2014 NEMS
1021 | Increase deployment of Energy Star 2011 CFL Reflectors for residential lighting in place of incandescents and halogen reflectors | R: Energy Star CFL Reflectors | Lamp | 5 | 5 | Residential | Lighting | Lamp | Incandescent and halogen | lumens/watt | 40 | 10.5561 | Yes | Typical residential luminaire provides 630 lumens lumens. First cost of a CFL reflector is estimated at $8.83/klm, while an incandescent is $5.36/klm and $9.72/klm for halogen. | 22.1569 | 8.83 | -13.3269 | per lamp | 1 C/R: No FS: All electric to all electric | Total residential incandescent and halogen reflector lighting | 2 | 2010 | 1) 2010 U.S. Lighting Market Characterization; 2012 Energy Savings Potential of SSL 2) Daily operating hours from the PNNL: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/2012_residential-lighting-study.pdf | 1) Market cost of efficient and standard luminaires are first costs. Incremental cost includes first cost and cost of relamping a standard less efficient unit accounting for its shorter lifetime, which is why the difference in efficent unit and standard unit costs do not match the incremental cost. Detailed calculations see "Lighting Measures_Relamp and Labor Costs_4-2-14". 2) Base and efficient unit performance were slightly adjusted to match EIA Tech Forecast, the costs were not changed because this change was very small. 3) Base unit performance more closely reflects incadescent bulbs, however, halogen is not significantly higher in efficacy, typically 14.7-20.1 lum/watt. The market for these is significantly smaller. | 1-172 | 2 | 6.6 | Navigant Consulting Lighting Market Characterization Database and Projections, created for DOE Solid State Lighting Program
1025 | Increase deployment of Energy Star commercial gas ovens | C: Energy Star Gas Oven | System | 5 | 5 | Commercial | Cooking | Oven | Gas | Energy Savings (%) | 16% | 0% | Yes |  |  |  | 0 | per unit | 2 C/R: No FS: All gas to all gas | All commercial natural gas ovens | 10 | 2010 | 1) % energy savings and incremental cost from ENERGY STAR Qualified Commercial Kitchen Equipment Savings Calculator (Excel file). Retrieved from: http://www.energystar.gov/products/certified-products/detail/commercial-ovens |  | 3-3405 | 10 | 33 | AEO 2010 NEMS
1026 | Increase deployment of Energy Star commercial electric ovens | C: Energy Star Electric Oven | System | 5 | 5 | Commercial | Cooking | Oven | Electric | Energy Savings (%) | 16% | 0% | Yes |  |  |  | 0 | per unit | 1 C/R: No FS: All electric to all electric | All commercial electric ovens | 10 | 2010 | 1) % energy savings and incremental cost from ENERGY STAR Qualified Commercial Kitchen Equipment Savings Calculator (Excel file). Retrieved from: http://www.energystar.gov/products/certified-products/detail/commercial-ovens |  | 3-3397 | 10 | 33 | AEO 2010 NEMS
Note on L48: Abdelaziz, Omar: 26% source energy savings; using site to source ratios ==>3.19 for baseline and 1.15 for measure ==> 1-1.15/3.19*site energy ratio = 0.26 --> site energy savings = -105.3%!! i.e. site energy consumption is doubled!
Note on L49: Abdelaziz, Omar: based on Navigant' study the source energy saving is 48%; using 2010 site to source conversion factors result in site energy increase of 44.24%
Note on M87: Oxana Petritchenko: Baseline DHW electric use: 2,700 (kWh/unit); savings per unit: 1,700 (kWh/unit); 163 apartments; total building's SF: 117,500. (Pg. vi)
Note on M88: Oxana Petritchenko: Baseline DHW electric use: 2,700 (kWh/unit); savings per unit: 1,700 (kWh/unit); 163 apartments; total building's SF: 117,500. (Pg. vi)
Note on L111: Navigant: Regular CFL from Mary 53.
Note on U164: Oxana Petritchenko: Market does not match measure description
Note on L191: Abdelaziz, Omar: ICE predict up to 40% due to improved part load performance!
Note on K215: Oxana Petritchenko: =(0.4*NEMSConsFcast3!$L$672(cooling total) *'Additional data'!$L$13 (window solar heat gain during cooling season) +0.46* (NEMSConsFcast3!$L$341(heating total)*'Additional data'!$I$12 (window conduction during heating season)+NEMSConsFcast3!L$672(cooling total)*NEMSConsFcast3!$AR$3647(cooling load% load)) / (NEMSConsFcast3!$L$341(heating total)*'Additional data'!$I$12(window conduction during heating season)+NEMSConsFcast3!$L$672 (cooling total)*'Additional data'!$L$13 (window conduction during cooling season)+NEMSConsFcast3!L$672(cooling total)*NEMSConsFcast3!$AR$3647(cooling load% load))
Note on M247: Oxana Petritchenko: Based on 05/2012 rulemaking, in May 2013, this should be 307 kwh/yr; however, current AEO 2010 baseline doesn't capture it (standard updated in2012)
Note on L370: Abdelaziz, Omar: source energy savings of 87% site to source for baseline is 3.19 and measure 1.74 --> 1-1.74/3.19*site energy ratio = 87% --> site energy savings = 76.2%
Note on L371: Abdelaziz, Omar: source energy savings of 67% site to source for baseline is 3.19 and measure 1.74 --> 1-1.74/3.19*site energy ratio = 67% --> site energy savings = 39.5%
Note on B403: Oxana Petritchenko: Market was changed from ft^2 to # lamps, hence incremental cost need to be adjusted.
Note on M428: Oxana Petritchenko: Converted from primary EF to site EF.
Note on L432: Abdelaziz, Omar: 30-45%
Note on P479: Oxana Petritchenko: equipment cost
Note on M481: Oxana Petritchenko: Need to average this out
Note on M482: Oxana Petritchenko: Need to average this out
Note on M562: Oxana Petritchenko: Based on 05/2012 rulemaking, in May 2013, this should be 307 kwh/yr; however, current AEO 2010 baseline doesn't capture it (standard updated in2012)