## Instructions
Title Block
Test Report Template Name: | Consumer Boiler
Version Number: | v1.1
Latest Template Revision: | 2019-09-13
Tab Name: | Instructions
File Name: | Consumer Boiler - v1.1.xlsx
Reference Test Procedures
10 CFR 430 Subpart B Appendix N: Uniform Test Method for Measuring the Energy Consumption of Furnaces and Boilers
Table of Contents
Tab | Contents
Instructions | Instructions and Table of Contents
Max Input Data | Raw data for the Max Test
Reduced Input Data | Raw data for the Reduced Test
Optional Test Data | Raw data for the Optional Test
General Info & Test Results | Lab information, product information and test results
Instrumentation | Instrumentation requirements and space for sensor placement descriptions
Test Conditions | Table of test condition requirements for each test
Max Test | Calculates values at the maximum input rating
Reduced Test | Calculates values at the reduced input rating
Photos | Inputs for photographs
Test Data Inputs & Calculations | Measurement inputs and automated calculations
Comments | Inputs for report template user to provide comments
Report Sign-Off Block | Report review history
Drop-Downs & Tables | Drop downs used and tables referenced
Version Control | Revision history
LEGEND
Tabs | Tabs with input cells
Tabs with space to paste raw data
Cells | Input cell
Auto-populated cell
Provided data
Tolerance Check
NOT USED
Instructions for Completing this Template
Follow the steps below, filling in all input cells (shaded light blue) in each tab you are instructed to complete. Using TAB to "hop" from input cell to input cell is useful, but does not ensure that all input cells are reached. To guarantee that you enter all required information, you must visually scan for light blue cells in the entire area bounded by yellow-shaded cells.
Important: Start with a clean (unused) template copy for each new report. Enter only data and information that are unique to the unit tested and the current test of that unit. All abbreviations and variable names should be consistent with the reference test procedure.
STEP: | FILL IN INPUT CELLS IN THIS TAB:
Step 1 | General Info & Test Results
Step 2 | Instrumentation
Step 3 | Import raw data into the appropriate data tabs (see instructions directly below)
Step 4 | Test Conditions
Step 5 | Jacket Loss
Step 6 | Max Test
Step 7 | Reduced Test
Step 8 | Calculations
Step 9 | Photos
Step 10 | Comments
Step 11 | Report Sign-off Block
Raw Data Import Instructions
Input raw data from the efficient tests into the corresponding tabs located immediately after the Instructions tab.
Include the following as a function of time for at least the duration of the steady state period and all test periods:
• Watts
• Watt-hours
• Volts
• Amps
• Temperatures from thermocouple grid
• Temperatures from jacket surface
• Temperatures from ambient thermocouples

## General Info & Test Results
Title Block
Test Report Template Name: | Consumer Boiler
Version Number: | v1.1 |  | Back to Instructions tab
Latest Template Revision: | 2019-09-13
Tab Name: | General Info & Test Results
File Name: | Consumer Boiler - v1.1.xlsx
Test Completion Date: | 0
Lab Information |  |  | Test Results
Lab Name: |  |  | Variable | Result | Units
Lab Location (City, State): |  |  | Steady State Efficiency |  | % (0-100)
|  |  | Heating Seasonal Efficiency |  | % (0-100)
Test Information |  |  | Annual Fuel Utilization Efficiency |  | % (0-100)
Date Test Started:
Date Test Finished:
Product Information
Brand: |  |  | NOTE: This is only a copy; sign off is done in the Report Sign-Off Block tab
Manufacturer: |  |  | Test Report Sign-Off Block
Manufacturer model number: |  |  | We certify that the information and data in this report: (1) were obtained from the specific test unit under test; (2) were obtained during the specific test being reported; (3) were not copied from any other source, except where instructed to do so; and (4) were not altered or modified in any way.
Serial number:
Date of Manufacture (if available):
Date Product Received: |  |  | Role |  | Date | Entity
Condition as received: |  |  | Test Completion |  | 0 | [Test Lab Name]
Product Class: | Fill in Product CharacteristicsBoiler |  | Template Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Nameplate Voltage (V): |  |  | Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Nameplate Maximum Input (Btu/h or kW): |  |  | Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Nameplate Reduced Input (Btu/h or kW):
Manufacturer Recommended CO2 Reading:
Product Characteristics
System Number: | Product Characteristics not filled in correctly
Product | Boiler
Energy Source
Heating Fuel Used:
Heating Medium:
Finned-Tube Boiler?
Burner Type: |  | (Used to determine System Number)
Power Burner Option
Ignition:
Draft Equipment: |  | (Used to determine System Number)
Not used
Stack Damper: |  | (Used to determine System Number)
Burner Inlet or Flue Damper? |  | (Used to determine System Number)
Installation: |  | (Used to determine System Number)
Direct Vent? (Indoor Installations Only) |  | (Used to determine System Number)
Flue Gas: (Condensing or Non-Condensing)
Control Type:
Reduced Test Required? | Fill in Control Type

## Instrumentation
Title Block
Test Report Template Name: | Consumer Boiler
Version Number: | v1.1 |  | Back to Instructions tab
Latest Template Revision: | 2019-09-13
Tab Name: | Instrumentation
File Name: | Consumer Boiler - v1.1.xlsx
Test Completion Date: | 0
Setup (This table should include instrumentation, sensors, and all equipment used during testing)
Measurement | Instrument Type | Brand | Model # | Sensor Location | Accuracy |  |  |  | Test Procedure required Accuracy | Meets required Accuracy? | Date of Last Calibration | Deadline for Next Calibration | Dates Valid?
[5 empty] | Value | TP required units for specified measurements | Units for measurements other than specified by TP | Further Description
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
[11 empty] | [MM/DD/YYYY] | [MM/DD/YYYY]
Describe placement of thermocouple grid:
If additional sensors were used, describe placement:

## Test Conditions
Title Block
Test Report Template Name: | Consumer Boiler
Version Number: | v1.1 |  | Back to Instructions tab
Latest Template Revision: | 2019-09-13
Tab Name: | Test Conditions
File Name: | Consumer Boiler - v1.1.xlsx
Test Completion Date: | 0
Fuel Supply Characteristics
Appendix N, Section 7.1: Fuel supply, gas. In conducting the tests specified herein, gases with characteristics as shown in Table 1 of ASHRAE 103-1993 shall be used. Maintain the gas supply, ahead of all controls for a furnace, at a test pressure between the normal and increased values shown in Table 1 of ASHRAE 103-1993. Maintain the regulator outlet pressure at a level approximating that recommended in the I&O manual, as defined in section 2.6 of this appendix, or, in the absence of such recommendation, to the nominal regulator settings used when the product is shipped by the manufacturer. Use a gas having a specific gravity as shown in Table 1 of ASHRAE 103-1993 and with a higher heating value within ±5% of the higher heating value shown in Table 1 of ASHRAE 103-1993. Determine the actual higher heating value in Btu per standard cubic foot for the gas to be used in the test within an error no greater than 1%.
Measurements |  | Tested Value | Tolerance |  | Unit | Tolerance Met?
|  |  | Min | Max
Test Pressure Range - Max Test |  |  | N/A | N/A | in. WC | Select Fuel Type
Test Pressure Range - Reduced Test |  |  | N/A | N/A | in. WC | Select Fuel Type
Higher Heating Value (HHV) |  |  | N/A | N/A | Btu/ft3 | Select Fuel Type
Specific Gravity |  |  | N/A | N/A | - | Select Fuel Type
Appendix N, Section 7.3: Gas Burner Adjust the burners of gas-fired furnaces and boilers to their maximum Btu input ratings at the normal test pressure specified by section 7.1 of this appendix. Correct the burner input rate to reflect gas characteristics at a temperature of 60°F and atmospheric pressure of 30 in of Hg and adjust down to within ±2 percent of the hourly Btu nameplate input rating specified by the manufacturer as measured during the steady-state performance test in section 8 of this appendix. Set the primary air shutters in accordance with the I&O manual to give a good flame at this condition. If, however, the setting results in the deposit of carbon on the burners during any test specified herein, the tester shall adjust the shutters and burners until no more carbon is deposited and shall perform the tests again with the new settings (see Figure 9 of ASHRAE 103-1993). After the steady-state performance test has been started, do not make additional adjustments to the burners during the required series of performance tests specified in section 9 of ASHRAE 103-1993. If a vent-limiting means is provided on a gas pressure regulator, keep it in place during all tests.
Appendix N, Section 7.4: Modulating Gas Burner Adjustment at Reduced Input Rate For gas-fired furnaces and boilers equipped with modulating-type controls, adjust the controls to operate the unit at the nameplate minimum input rate. If the modulating control is of a non-automatic type, adjust the control to the setting recommended in the I&O manual. In the absence of such recommendation, the midpoint setting of the non-automatic control shall be used as the setting for determining the reduced fuel input rate. Start the furnace or boiler by turning the safety control valve to the “ON” position. For boilers, use a supply water temperature that will allow for continuous operation without shutoff by the control. If necessary to achieve such continuous operation, supply water may be increased above 120°F; in such cases, gradually increase the supply water temperature to determine what minimum supply water temperature, with a 20°F temperature rise across the boiler, will be needed to adjust for the minimum input rate at the reduced input rate control setting. Monitor regulated gas pressure out of the modulating control valve (or entering the burner) to determine when no further reduction of gas pressure results. The flow rate of water through the boiler shall be adjusted to achieve a 20°F temperature rise.
Appendix N, Section 7.5: Oil Burner Adjust the burners of oil-fired furnaces or boilers to give a CO2 reading specified in the I&O manual and an hourly Btu input during the steady-state performance test described in section 8 of this appendix. Ensure the hourly BTU input is within ±2% of the normal hourly Btu input rating as specified in the I&O manual. Smoke in the flue may not exceed a No. 1 smoke during the steady-state performance test as measured by the procedure in ASTM D2156R13. Maintain the average draft over the fire and in the flue during the steady-state performance test at the value specified in the I&O manual. Do not allow draft fluctuations exceeding 0.005 in. water. Do not make additional adjustments to the burner during the required series of performance tests. The instruments and measuring apparatus for this test are described in section 6 of this appendix and shown in Figure 8 of ASHRAE 103-1993.
| Maximum Test | Reduced Test
Nameplate Rate (Btu/h)
Measured Rate (Btu/h)
Condition Met?
Not Used
Not Used
Not Used
Input Voltage
ASHRAE 103-1993, Section 8.2.1.4: Electric Supply Maintain the electrical supply to an auxiliary electric component of a furnace or boiler within 1% of the nameplate voltage for the duration of the test. If a dual voltage is used for nameplate voltage, maintain the electrical supply within 1% of the higher voltage.
|  | Value | Units
Nameplate Voltage |  |  | V
Minimum Voltage |  |  | V
Maximum Voltage |  |  | V
Condition Met? |  |  | -
Jacket Loss Measurement
ASHRAE 103-1993, Section 8.6: Jacket Loss Measurement For units intended to be installed outdoors or in an unheated space (including isolated combustion systems), the jacket loss may be assigned the value of 1% or a jacket loss test may be performed. Conduct the test at steady-state conditions according to 9.1.
Measurements | Maximum Test | Unit | Variable
Jacket Loss Factor Determination Method |  | - | -
Jacket Loss Factor - Calculated from Test |  | % (0-100) | LJ
Jacket Loss Factor |  | % (0-100) | LJ
Tracer Gas Draft Factors
ASHRAE 103-1993, Section 8.8: Methods for Detennining Draft Factor DP, DF, and DS
ASHRAE 103-1993, Section 8.8.1: Standard Method Use Table 6 to determine draft factors DF and DS as required in Section 11, "Calculation of Derived Results from Test Measurements."
ASHRAE 103-1993, Section 8.8.2: Optional Tracer Gas Method for Determining Draft Factors DP, DF, and DS for Systems Equipped with Power Burners or Direct Vent 8.8.2.1 Determine DF (the ratio of gas mass flow rate through the flue during the off-cycle to the gas mass flow rate through the flue during the on-cycle at identical temperatures) during the cool-down test described in 9.7 and the calculation procedures of 11.6 and 11.7. On units with step modulating controls, the optional tracer gas procedure shall be conducted during the cool-down test described in 9.7 at the reduced input rate only. For units with two-stage modulating controls, if the optional tracer gas procedure is conducted during the cool-down test described in 9.7 at the reduced input rate, it shall also be conducted at the maximum input rate and vice versa. 8.8.2.2 On systems for which the stack damper is to be closed during the cool-down test described in 9.5, determine DP (the ratio of the rate of flue gas mass flow through the furnace during the off-period to the rate of flue gas mass flow through the furnace during the on-period) during a separate cool-down test. Conduct this separate cool-down test by running the unit after the heat-up test until steady-state conditions are reached (see 9.1) and then shutting the unit off with the stack damper controls bypassed or adjusted so that the stack damper remains open during the resulting cool-down period. If a draft was maintained in the flue pipe during the steady-state performance test described in 9.1, maintain the same draft (within ±0.005 in. water of the average steady-state draft) during this cool-down period. Measure the flue gas mass flow rate (MF,OFF) during the cool-down test described above at a specific off-period flue gas temperature described in 9.5 and correct (as described in 11.6.3) to obtain its value at the steady-state flue gas temperature (TF,SS) using 9.5. 8.8.2.3 Units with integral dampers as described in 7.4 shall be tested as described in 8.8.2.1.
ASHRAE 103-1993, Section 8.8.3: Additional Optional Method of Testing for Determining DP and DF for Furnaces and Boilers On units whose design is such that there is absolutely no chance of airflow through the combustion chamber and heat exchanger when the bumer(s) is off, DF and DP may be set equal to 0.05.
Appendix N, Section 7.10: Additional Optional Method of Testing for Determining DP and DF for Furnaces and Boilers On units whose design is such that there is no measurable airflow through the combustion chamber and heat exchanger when the burner(s) is (are) off as determined by the optional test procedure in section 7.10.1 of this appendix, DF and DP may be set equal to 0.05.
Appendix N, Section 7.10.1: Optional Test Method for Indicating the Absence of Flow Through the Heat Exchanger Manufacturers may use the following test protocol to determine whether air flows through the combustion chamber and heat exchanger when the burner(s) is (are) off. The minimum default draft factor (as allowed per sections 8.8.3 and 9.10 of ASHRAE 103-1993) may be used only for units determined pursuant to this protocol to have no airflow through the combustion chamber and heat exchanger.
Appendix N, Section 7.10.1.1: Test Apparatus Use a smoke stick that produces smoke that is easily visible and has a density less than or approximately equal to air. Use a smoke stick that produces smoke that is non-toxic to the test personnel and produces gas that is unreactive with the environment in the test chamber.
Appendix N, Section 7.10.1.2: Test Conditions Minimize all air currents and drafts in the test chamber, including turning off ventilation if the test chamber is mechanically ventilated. Wait at least two minutes following the termination of the furnace or boiler on-cycle before beginning the optional test method for indicating the absence of flow through the heat exchanger.
Appendix N, Section 7.10.1.3: Location of the Test Apparatus After all air currents and drafts in the test chamber have been eliminated or minimized, position the smoke stick based on the following equipment configuration: (a) For horizontal combustion air intakes, approximately 4 inches from the vertical plane at the termination of the intake vent and 4 inches below the bottom edge of the combustion air intake; or (b) for vertical combustion air intakes, approximately 4 inches horizontal from vent perimeter at the termination of the intake vent and 4 inches down (parallel to the vertical axis of the vent). In the instance where the boiler combustion air intake is closer than 4 inches to the floor, place the smoke device directly on the floor without impeding the flow of smoke.
Appendix N, Section 7.10.1.4: Duration of Test Establish the presence of smoke from the smoke stick and then monitor the direction of the smoke flow for no less than 30 seconds.
Appendix N, Section 7.10.1.5: Test Results During visual assessment, determine whether there is any draw of smoke into the combustion air intake vent. If absolutely no smoke is drawn into the combustion air intake, the furnace or boiler meets the requirements to allow use of the minimum default draft factor pursuant to section 8.8.3 and/or section 9.10 of ASHRAE 103-1993. If there is any smoke drawn into the intake, proceed with the methods of testing as prescribed in section 8.8 of ASHRAE 103-1993.
Is there any chance of airflow through the combustion chamber and heat exchanger when the burner(s) is off? |  |  | Fill Drop-Down
Optional Tracer Gas Procedure from ASHRAE 103-1993, Section 8.8.2 Used? If Yes is selected, DF=DP. If No is selected, constants from Table 6 are used for DF. |  |  | Fill Drop-Down
Was airflow through the heat exchanger observed when performing procedure from Appendix N, Section 7.10.1? |  |  | Fill Drop-Down
Measurements |  | Value |  | Variable
|  | Maximum Test | Reduced Test
Off-Cycle Draft Factor for Flue Gas Flow |  | #N/A | #N/A | DF
Off-Cycle Stack Gas Draft Factor |  | #N/A | #N/A | DS
Power Burner Draft Factor |  | #N/A | #N/A | DP
End: Tracer Gas Draft Factors
Stack Damper Effectiveness Factor (DO) of Automatic Stack Damper
ASHRAE 103-1993, Section 8.8.4: Methods of Measurement for Determining DO of Automatic Stack Damper
8.8.4.1 Measure the cross-sectional area of the stack (AS), the net area of the damper plate (AD), which is the area of the damper plate minus the area of any holes in the plate, and the angle (Ω) the damper plate makes when closed with a plane perpendicular to the axis of the stack. Note that the area AS is the cross-sectional area of the stack pipe, not the area inside any ring that is attached to the inside of the stack pipe. Measure the area of any holes or cutouts in the stack damper plate, AO,D, and either measure, or obtain from the manufacturer of the stack damper, the leakage area, AO,L, at the damper shaft and around the damper edge when the damper is at the closed position. Both areas shall be measured at the plane of the damper. 8.8.4.2 Determine the time it takes for the damper to be energized following burner shutdown, ts. Also determine the time interval, td, it takes from when the damper is energized to when the damper blade stops moving.
Measurements | Value | Units | Variable
Cross-Sectional Area of the Stack |  | in2 | AS
Net Area of a Stack Damper Plate |  | in2 | AD
Angle the Damper Makes, When Closed, With a Plane Perpendicular to the Axis of the Stack |  | Radians | Ω
Open Area (Holes and Cutouts) in Stack Damper Plate |  | in2 | AO,D
Leakage Area Around Stack Damper Shaft and Damper Edges |  | in2 | AO,L
Time When Damper Starts to Close |  | min | ts
Duration of Damper Closing |  | min | td
Time When Damper Finishes Closing |  | min | te
Minimum Opening (including Leakage) Area of the Damper When Closed |  | min | AO
|  | min | DE
"Standby" and "Off" Power Measurement
Appendix N, Section 8.11: Measurement of electrical standby and off mode power.
Appendix N, Section 8.11.1: Standby Power Measurement With all electrical auxiliaries of the furnace or boiler not activated, measure the standby power (PW,SB) in accordance with the procedures in IEC 62301, except that section 8.5, Room Ambient Temperature, of ASHRAE 103-1993 and the voltage provision of section 8.2.1.4, Electrical Supply, of ASHRAE 103-1993 shall apply in lieu of the corresponding provisions of IEC 62301 at section 4.2, Test room, and the voltage specification of section 4.3, Power supply. Frequency shall be 60Hz. Clarifying further, IEC 62301 section 4.4, Power measurement instruments, and section 5, Measurements, apply in lieu of ASHRAE 103-1993 section 6.10, Energy Flow Rate. Measure the wattage so that all possible standby mode wattage for the entire appliance is recorded, not just the standby mode wattage of a single auxiliary. Round the recorded standby power (PW,SB) to the second decimal place, except for loads greater than or equal to 10W, which must be recorded to at least three significant figures.
Appendix N, Section 8.11.2: Off mode power measurement. If the unit is equipped with an off switch or there is an expected difference between off mode power and standby mode power, measure off mode power (PW,OFF) in accordance with the standby power procedures in IEC 62301, except that section 8.5, Room Ambient Temperature, of ASHRAE 103-1993 and the voltage provision of section 8.2.1.4, Electrical Supply, of ASHRAE 103-1993 shall apply in lieu of the corresponding provisions of IEC 62301 at section 4.2, Test room, and the voltage specification of section 4.3, Power supply. Frequency shall be 60Hz. Clarifying further, IEC 62301 section 4.4, Power measurement instruments, and section 5, Measurements, apply for this measurement in lieu of ASHRAE 103-1993 section 6.10, Energy Flow Rate. Measure the wattage so that all possible off mode wattage for the entire appliance is recorded, not just the off mode wattage of a single auxiliary. If there is no expected difference in off mode power and standby mode power, let PW,OFF = PW,SB, in which case no separate measurement of off mode power is necessary. Round the recorded off mode power (PW,OFF) to the second decimal place, except for loads greater than or equal to 10W, in which case round the recorded value to at least three significant figures.
Measurements | Value | Unit | Variable
Standby Mode Power |  | W | PW,SB
Off Mode Power |  | W | PW,OFF
Power Burner Motor Efficiency - NOT USED FOR THIS TEST
Measurements | Value | Unit | Variable
Nameplate Power Burner Motor Efficiency |  | % | Effmotor
Nameplate Power Burner Motor Efficiency Used | 0 | % | Effmotor

## Jacket Loss
Title Block
Test Report Template Name: | Consumer Boiler
Version Number: | v1.1 |  | Back to Instructions tab
Latest Template Revision: | 2019-09-13
Tab Name: | Jacket Loss
File Name: | Consumer Boiler - v1.1.xlsx
Test Completion Date: | 0
Jacket Loss Test
Appendix N, Section 7.8: Measurement of Jacket Surface Temperature. Divide the jacket of the furnace or boiler into 6-inch squares when practical, and otherwise into 36-square-inch regions comprising 4 inch by 9 inch or 3 inch by 12 inch sections, and determine the surface temperature at the center of each square or section with a surface thermocouple. Record the surface temperature of the 36-square-inch areas in groups where the temperature differential of the 36-square-inch areas is less than 10°F for temperature up to 100°F above room temperature, and less than 20°F for temperatures more than 100°F above room temperature. For forced-air central furnaces, the circulating air blower compartment is considered as part of the duct system, and no surface temperature measurement of the blower compartment needs to be recorded for the purpose of this test. For downflow furnaces, measure all cabinet surface temperatures of the heat exchanger and combustion section, including the bottom around the outlet duct and the burner door, using the 36-square-inch thermocouple grid. The cabinet surface temperatures around the blower section do not need to be measured (See Figure 3-E of ASHRAE 103-1993).
ASHRAE 103-1993, Section 8.6: Jacket Loss Measurement For units intended to be installed outdoors or in an unheated space (including isolated combustion systems), the jacket loss may be assigned the value of 1% or a jacket loss test may be performed. Conduct the test at steady-state conditions according to 9.1. For modulating units, run the test at maximum input only. The jacket loss (LJ) is measured in accordance with the following paragraphs.
ASHRAE 103-1993, Section 8.6.1: Gas-Fueled Gravity Furnaces, Forced-Air Central Furnaces, and Low-Pressure Steam and Hot Water Boilers
8.6.1.1 The jacket of the furnace or boiler shall be subdivided into 6-inch squares when practical (otherwise use 36-square-inch regions comprising 4 in. X 9 in. or 3 in. x 12 in. sections) and the surface temperature at the center of each square determined with a surface thermocouple. The 36-square-inch areas shall be recorded in groups where the temperature differential of the 36-square-inch areas is less than 10°F for temperatures up to 100°F above room temperature and less than 20°F for temperatures more than 100°F above room temperature. For forced-air central furnaces, the circulating air blower compartment is considered as part of the duct system and no surface temperature of the blower compartment needs to be recorded for the purpose of this test. For units with ventilation air openings on the top, front, or sides of the unit, those openings from which the ventilation air exits from the cabinet shall be taped or sealed with aluminum tape during this test. A smoke test during a steady-state test may be used to determine the openings where the ventilation air exits from the cabinet. On the taped openings, subdivide the area into the normal 36-square-inch grids and measure the surface temperatures in each grid with a surface thermocouple. Install the thermocouple over the aluminum tape if necessary. For downflow furnaces, measure all cabinet surface temperatures of the heat exchanger and combustion section, including the burner door and the bottom around the outlet duct, using the 36-square-inch thermocouple grid. If the burner door is louvered to allow for combustion air to enter, measure temperatures on the metal strips between the louvers using the normal 36-square-inch grid. The cabinet surface temperatures around the blower section do not need to be measured (see Figure 3e), and the taping of the ventilation air openings shall be as described above.
8.6.1.2 Any casing panel at any angle of 45° or less from the vertical shall be considered as a vertical surface. An exposed flue collector (breeching) or flue outlet forming an integral part of the furnace shall not be included in casing surface temperature measurements. Average room temperature (TRA) shall be determined by not less than four readings at approximately equal intervals during the test. The value of hC for a recorded group may be found from the curves shown in Figure 20. The value of hri for a recorded group may be found from the curves shown in Figure 21. Since Figure 21 is based on an emissivity of 1.0, the coefficient hri obtained therefrom should be multiplied by the emissivity of the surface under consideration to obtain the correct coefficient for the surface hrs. Emissivities as given in the literature for some common jacket materials are 0.23: galvanized sheet iron, bright 0.28: galvanized sheet iron, oxidized 0.93: asbestos paper 0.87: miscellaneous paint finishes Thus, hrs for a painted surface is equal to hri multiplied by 0.87.
8.6.1.3 The hourly heat loss through the jacket, HS, shall be the sum of the hourly heat loss, ΣHS, where HS is the hourly heat loss for each recorded group as computed from the formula HS = (hrs + hC) AG (TS - TRA) where HS = hourly heat loss through jacket in Btu per each recorded group; hrs = coefficient of radiation for the surface, Btu/(h· ft2 °F); hC = coefficient of convection, Btu/(b·ft2 °F); AG = area of group, ft2; TS = temperature of surface, °F; TRA = temperature of room, °F. The percent jacket loss, LJ, shall be the hourly heat loss through the jacket, HS, divided by the hourly input, QIN, and multiplied by 100.
ASHRAE 103-1993, Section 8.6.2: Oil-Fueled Forced-Air Central Furnaces and Low-Pressure Steam and Hot Water Boilers The jacket loss measurement is the same as in 8.6.1.
8.6.2.1 Surface temperature measurements on the oil burner, burner mounting plate, and inspection or access door panels may be omitted for the purposes of this test. The surface temperatures of the casing adjacent to these items shall be measured at points not less than 2 inches from the edges of each frame or panel.
ASHRAE 103-1993, Section 8.6.3: Electric Forced-Air Central Furnaces and Low-Pressure Steam and Hot Water Boilers The jacket loss measurement is the same as in 8.6.1.
Description | Variable | Value | Units
Top Coefficient of Convection | hC |  | Btu/h/sq ft/°F
Bottom Coefficient of Convection | hC |  | Btu/h/sq ft/°F
Side Coefficient of Convection | hC |  | Btu/h/sq ft/°F
Coefficient of Radiation, ε=1.0 | hri |  | Btu/h/sq ft/°F
Emissivity of the Surface | - |  | -
Coefficient of Radiation, surface | hrs |  | Btu/h/sq ft/°F
Room Temperature | TRA |  | °F
Top Surface Hourly Heat Loss | - |  | Btu/h
Bottom Surface Hourly Heat Loss | - |  | Btu/h
Side Surfaces Hourly Heat Loss | - |  | Btu/h
Jacket Loss - Calculation | LJ |  | % (0-100)
Jacket Loss - Manual Entry | LJ |  | % (0-100)
Jacket Loss - Used | LJ |  | % (0-100)
Minimum Surface Temperature | - |  | °F
Maximum Surface Temperature | - |  | °F
Difference in Max Surface and Room Temperatures | - |  | °F
Maximum Differential | - |  | °F
Maximum Differential Condition Met? | - |  | -
| Top Surface |  |  | Bottom Surface |  |  | Side Surfaces
| Group Area (sq ft) | Surface Temp (°F) | Temp Difference (°F) | Group Area (sq ft) | Surface Temp (°F) | Temp Difference (°F) | Group Area (sq ft) | Surface Temp (°F) | Temp Difference (°F)
Area 1 |  |  | 0 |  |  | 0 |  |  | 0
Area 2 |  |  | 0 |  |  | 0 |  |  | 0
Area 3 |  |  | 0 |  |  | 0 |  |  | 0
Area 4 |  |  | 0 |  |  | 0 |  |  | 0
Area 5 |  |  | 0 |  |  | 0 |  |  | 0
Area 6 |  |  | 0 |  |  | 0 |  |  | 0
Area 7 |  |  | 0 |  |  | 0 |  |  | 0
Area 8 |  |  | 0 |  |  | 0 |  |  | 0
Area 9 |  |  | 0 |  |  | 0 |  |  | 0
Area 10 |  |  | 0 |  |  | 0 |  |  | 0
Area 11 |  |  | 0 |  |  | 0 |  |  | 0
Area 12 |  |  | 0 |  |  | 0 |  |  | 0
Area 13 |  |  | 0 |  |  | 0 |  |  | 0
Area 14 |  |  | 0 |  |  | 0 |  |  | 0
Area 15 |  |  | 0 |  |  | 0 |  |  | 0
Area 16 |  |  | 0 |  |  | 0 |  |  | 0
Area 17 |  |  | 0 |  |  | 0 |  |  | 0
Area 18 |  |  | 0 |  |  | 0 |  |  | 0
Area 19 |  |  | 0 |  |  | 0 |  |  | 0
Area 20 |  |  | 0 |  |  | 0 |  |  | 0
Area 21 |  |  | 0 |  |  | 0 |  |  | 0
Area 22 |  |  | 0 |  |  | 0 |  |  | 0
Area 23 |  |  | 0 |  |  | 0 |  |  | 0
Area 24 |  |  | 0 |  |  | 0 |  |  | 0
Area 25 |  |  | 0 |  |  | 0 |  |  | 0
Area 26 |  |  | 0 |  |  | 0 |  |  | 0
Area 27 |  |  | 0 |  |  | 0 |  |  | 0
Area 28 |  |  | 0 |  |  | 0 |  |  | 0
Area 29 |  |  | 0 |  |  | 0 |  |  | 0
Area 30 |  |  | 0 |  |  | 0 |  |  | 0
Area 31 |  |  | 0 |  |  | 0 |  |  | 0
Area 32 |  |  | 0 |  |  | 0 |  |  | 0
Area 33 |  |  | 0 |  |  | 0 |  |  | 0
Area 34 |  |  | 0 |  |  | 0 |  |  | 0
Area 35 |  |  | 0 |  |  | 0 |  |  | 0
Area 36 |  |  | 0 |  |  | 0 |  |  | 0
Area 37 |  |  | 0 |  |  | 0 |  |  | 0
Area 38 |  |  | 0 |  |  | 0 |  |  | 0
Area 39 |  |  | 0 |  |  | 0 |  |  | 0
Area 40 |  |  | 0 |  |  | 0 |  |  | 0
Area 41 |  |  | 0 |  |  | 0 |  |  | 0
Area 42 |  |  | 0 |  |  | 0 |  |  | 0
Area 43 |  |  | 0 |  |  | 0 |  |  | 0
Area 44 |  |  | 0 |  |  | 0 |  |  | 0
Area 45 |  |  | 0 |  |  | 0 |  |  | 0
Area 46 |  |  | 0 |  |  | 0 |  |  | 0
Area 47 |  |  | 0 |  |  | 0 |  |  | 0
Area 48 |  |  | 0 |  |  | 0 |  |  | 0
Area 49 |  |  | 0 |  |  | 0 |  |  | 0
Area 50 |  |  | 0 |  |  | 0 |  |  | 0
Area 51 |  |  | 0 |  |  | 0 |  |  | 0
Area 52 |  |  | 0 |  |  | 0 |  |  | 0
Area 53 |  |  | 0 |  |  | 0 |  |  | 0
Area 54 |  |  | 0 |  |  | 0 |  |  | 0
Area 55 |  |  | 0 |  |  | 0 |  |  | 0
Area 56 |  |  | 0 |  |  | 0 |  |  | 0
Area 57 |  |  | 0 |  |  | 0 |  |  | 0
Area 58 |  |  | 0 |  |  | 0 |  |  | 0
Area 59 |  |  | 0 |  |  | 0 |  |  | 0
Area 60 |  |  | 0 |  |  | 0 |  |  | 0
Area 61 |  |  | 0 |  |  | 0 |  |  | 0
Area 62 |  |  | 0 |  |  | 0 |  |  | 0
Area 63 |  |  | 0 |  |  | 0 |  |  | 0
Area 64 |  |  | 0 |  |  | 0 |  |  | 0
Area 65 |  |  | 0 |  |  | 0 |  |  | 0
Area 66 |  |  | 0 |  |  | 0 |  |  | 0
Area 67 |  |  | 0 |  |  | 0 |  |  | 0
Area 68 |  |  | 0 |  |  | 0 |  |  | 0
Area 69 |  |  | 0 |  |  | 0 |  |  | 0
Area 70 |  |  | 0 |  |  | 0 |  |  | 0
Area 71 |  |  | 0 |  |  | 0 |  |  | 0
Area 72 |  |  | 0 |  |  | 0 |  |  | 0
Area 73 |  |  | 0 |  |  | 0 |  |  | 0
Area 74 |  |  | 0 |  |  | 0 |  |  | 0
Area 75 |  |  | 0 |  |  | 0 |  |  | 0
Area 76 |  |  | 0 |  |  | 0 |  |  | 0
Area 77 |  |  | 0 |  |  | 0 |  |  | 0
Area 78 |  |  | 0 |  |  | 0 |  |  | 0
Area 79 |  |  | 0 |  |  | 0 |  |  | 0
Area 80 |  |  | 0 |  |  | 0 |  |  | 0
Area 81 |  |  | 0 |  |  | 0 |  |  | 0
Area 82 |  |  | 0 |  |  | 0 |  |  | 0
Area 83 |  |  | 0 |  |  | 0 |  |  | 0
Area 84 |  |  | 0 |  |  | 0 |  |  | 0
Area 85 |  |  | 0 |  |  | 0 |  |  | 0
Area 86 |  |  | 0 |  |  | 0 |  |  | 0
Area 87 |  |  | 0 |  |  | 0 |  |  | 0
Area 88 |  |  | 0 |  |  | 0 |  |  | 0
Area 89 |  |  | 0 |  |  | 0 |  |  | 0
Area 90 |  |  | 0 |  |  | 0 |  |  | 0
Area 91 |  |  | 0 |  |  | 0 |  |  | 0
Area 92 |  |  | 0 |  |  | 0 |  |  | 0
Area 93 |  |  | 0 |  |  | 0 |  |  | 0
Area 94 |  |  | 0 |  |  | 0 |  |  | 0
Area 95 |  |  | 0 |  |  | 0 |  |  | 0
Area 96 |  |  | 0 |  |  | 0 |  |  | 0
Area 97 |  |  | 0 |  |  | 0 |  |  | 0
Area 98 |  |  | 0 |  |  | 0 |  |  | 0
Area 99 |  |  | 0 |  |  | 0 |  |  | 0
Area 100 |  |  | 0 |  |  | 0 |  |  | 0

## Max Test
Title Block
Test Report Template Name: | Consumer Boiler
Version Number: | v1.1 |  |  | Back to Instructions tab
Latest Template Revision: | 2019-09-13
Tab Name: | Max Test
File Name: | Consumer Boiler - v1.1.xlsx
Test Completion Date: | 0
Steady-State Test
Appendix N, Section 8.0: Test procedure. Conduct testing and measurements as specified in section 9 of ASHRAE 103-1993 except for sections 9.1.2.2.1, 9.1.2.2.2 and as specified in sections 8.1 through 8.3 of this appendix.
Appendix N, Section 8.1: Fuel input. For gas units, measure and record the steady-state gas input rate in Btu/hr, including pilot gas, corrected to standard conditions of 60 °F and 30 in. Hg. Use measured values of gas temperature and pressure at the meter and barometric pressure to correct the metered gas flow rate to the above standard conditions. For oil units, measure and record the steady-state fuel input rate.
Measurements | Value | Unit | Variable
Nameplate Input Rate |  | Btu/h | QIN | (including any pilot light input)
Appendix N, Section 8.2: Electrical Input. For furnaces and boilers, during the steady-state test, perform a single measurement of all of the electrical power involved in burner operation (PE), including energizing the ignition system, controls, gas valve or oil control valve, and draft inducer, if applicable. For boilers, the measurement of PE must include the boiler pump if so equipped. If the boiler pump does not operate during the measurement of PE, add the boiler pump nameplate power to the measurement of PE. If the boiler pump nameplate power is not available, use 0.13 kW. For furnaces, during the steady-state test, perform a single measurement of the electrical power to the circulating air blower (BE). For hot water boilers, use the circulating water pump nameplate power for BE, or if the pump nameplate power is not available, use 0.13 kW.
Measurements | Value | Unit | Variable
Steady State Electrical Power to Burner (including energizing the ignition system, controls, gas valve or oil control valve, draft inducer, and boiler pump) |  | kW | -
Boiler Pump Nameplate Power, if applicable (enter 0.13 if not available) |  | kW | BE
Was the boiler pump electrical usage captured in the steady-state measurement? |  | - | -
Steady State Electrical Power to Burner |  | kW | PE
Appendix N, Section 8.3: Input to Interrupted Ignition Device. For burners equipped with an interrupted ignition device, record the nameplate electric power used by the ignition device, PEIG, or record that PEIG = 0.4 kW if no nameplate power input is provided. Record the nameplate ignition device on-time interval, tIG, or, if the nameplate does not provide the ignition device on-time interval, measure the on-time interval with a stopwatch at the beginning of the test, starting when the burner is turned on. Set tIG = 0 and PEIG = 0 if the device on-time interval is less than or equal to 5 seconds after the burner is on.
Measurements | Value | Unit | Variable
Electrical Power Input to Interrupted Ignition Device |  | kW | PEIG
Nameplate Ignition Device On-time Interval |  | min | tIG
ASHRAE 103-1993, Section 8.4.2.3: Gas and Oil-Fueled Low-Pressure Steam and Hot Water Boilers (including Direct Vent Systems) For non-condensing hot water boilers, the water flow rate shall be adjusted to produce a water temperature rise of 19°F to 24°F during the steady-state test described in Section 9. During the steady-state and heat-up tests, the hot water boiler shall be supplied with water having a temperature of at least 120°F but not more than 124°F. 8.4.2.3.1 For steam boilers, the steam pressure shall be at atmospheric or at any pressure not exceeding 2 psig during the steady-state test. 8.4.2.3.2 For condensing hot water boilers, the water flow rate shall be adjusted to produce a water temperature rise between 19.5°F and 20.5°F during the steady-state test described in 9.1. During the steady-state and heat-up tests, the condensing boiler shall be supplied with return water having a temperature of 120°F. The maximum permissible variation of the return water temperature from the required value during the steady-state and heat-up tests shall not exceed ±2°F, except during the first 30 seconds after start-up, when it shall not exceed ± 10°F, and between 30 and 60 seconds after start-up, when it shall not exceed ±5°F.
ASHRAE 103-1993, Section 8.4.2.5: Electric Boilers Adjust the flow of water or steam as specified in 8.4.2.3 for gas and oil-fueled boilers.
Non-Condensing or Electric Hot Water Boilers - NOT REQUIRED FOR THIS TEST
Measurements | Tested Value |  | Tolerance |  | Unit | Tolerance Met?
| Min | Max | Min | Max
Supply Water Temperature | N/A | N/A | N/A | N/A | °F | N/A
Temperature Rise | N/A | N/A | N/A | N/A | °F | N/A
Condensing Hot Water Boilers - NOT REQUIRED FOR THIS TEST
Measurements | Tested Value |  | Tolerance |  | Unit | Tolerance Met?
| Min | Max | Min | Max
Return Water Temperature (second 0 to second 30) |  |  | N/A | N/A | °F | N/A
Return Water Temperature (second 30 to second 60) |  |  | N/A | N/A | °F | N/A
Return Water Temperature (second 60 to end of test) |  |  | N/A | N/A | °F | N/A
Temperature Rise | N/A | N/A | N/A | N/A | °F | N/A
Steam Boilers - NOT REQUIRED FOR THIS TEST
Measurements | Tested Value |  | Tolerance |  | Unit | Tolerance Met?
| Min | Max | Min | Max
Steam Pressure |  |  |  |  | psig | N/A
ASHRAE 103-1993, Section 8.5: Room Ambient Temperature (TRA)
ASHRAE 103-1993, Section 8.5.1: Measurement Room temperature shall be the arithmetic average temperature of the test area, determined by measurement with four No. 24 AWG bead-type thermocouples with junctions shielded against radiation, located approximately at 90° positions on a circle circumscribing the appliance or appliance enclosure under test, in a horizontal plane approximately at the vertical midpoint of the appliance or test enclosure, and with the junctions approximately 24 in. from the sides of the appliance or test enclosure and located so as not to be affected by other than room air. The temperature of the air for combustion and the air for draft control shall not differ more than ±5°F from the room temperature as measured above. Where there is less than 5°F stratification, one room air thermocouple may be used.
ASHRAE 103-1993, Section 8.5.2: Limitations During the time required to perform all the testing and measuring procedures specified in Section 9, maintain the room temperature within ±5°F of the air temperature value measured at the end of the steady-state performance test (TRA). During these tests, the room temperature may not fall below 65°F or exceed 100°F, except that for condensing furnaces and boilers, it shall not exceed 85°F.
ASHRAE 103-1993, Section 9.1.2: Steady-State Conditions and Requirements
ASHRAE 103-1993, Section 9.1.2.1: Conditions Begin the steady-state performance test by operating the burner and the circulating air blower or water pump until steady-state conditions are attained as indicated by a temperature variation in three successive readings, taken 15 minutes apart, of not more than (1) 3°F in the stack gas temperature for furnaces and boilers equipped with draft diverters; (2) 5°F in the flue gas temperature for furnaces and boilers equipped with either draft hoods, direct exhaust, or direct vent systems; (3) 4 °F in the outlet water temperature for hot water boilers; (4) 1°F in the flue gas temperature for condensing furnaces and boilers; and (5) 1°F in the flue gas and supply (outlet) water temperatures for condensing hot water boilers.
ASHRAE 103-1993, Section: 9.1.2.2 Input (Replaced by Appendix N Sections 8.1-8.3, which are addressed above)
ASHRAE 103-1993, Section 9.1.2.3: Measurements
9.1.2.3.1 On units employing draft hoods or direct exhaust or direct vent systems, measure the room temperature (TRA) as described in 8.5 and measure the steady-state flue gas temperature (TF,SS,X) using the thermocouple grid located in the flue pipe. Secure a sample of the flue gas in the plane of temperature measurement. Determine the concentration by volume of CO2 (XCO2F) present in dry flue gas (see Figures 3c, 3d, and 4). On units employing a draft hood, secure a sample of the stack gases at either a horizontal plane in the stack 12 in. downstream of the draft hood or in a horizontal plane 6 in. from the top of the test stack. Make sure that there are no holes or air leaks in the section of the stack from the draft hood up to the location where the stack gas is sampled. Determine the concentration by volume of carbon dioxide (XCO2S) present in the dry stack gas. Use Figures 3a and 3b (test stack for units with draft diverter) as reference for the location of CO2 measurement.
9.1.2.3.2 On units employing draft diverters, measure the room temperature (TRA) as described in 8.5 and measure the steady-state stack gas temperature (TS,SS,X) using the thermocouple grid located in the 5-ft test stack as described in 8.2.1.5 or 8.3.1.5. Secure a sample of the stack gases either at the plane where TS,SS,X is measured or in a horizontal plane 6 in. from the top of the test stack. (If the stack gas is sampled at this latter location, be sure that there are no holes or air leaks between this location and the plane where the TS,SS,X is measured.) Determine the concentration by volume of carbon dioxide (XCO2S) present in dry stack gas (see Figures 3a and 3b). After the above test measurements have been completed on units employing integral draft diverters, secure a sample of the flue gases at the inlet to the draft diverter and determine the concentration of flue CO2 (XCO2F) present (see Figures 3a and 3b). In obtaining this sample of flue gas, move the sampling probe around to ensure that an average value is obtained for the CO2 concentration. For units with multiple heat exchanger outlets, draw a sample of equal size from each outlet to obtain the average CO2 concentration for the unit.
9.1.2.3.3 On units employing barometric draft regulators, measure the room air temperature (TRA). Measure the steady-state flue gas temperature (TF,SS) using the thermocouple grid located in the flue pipe. Secure a sample of the flue gas in the plane of temperature measurement and determine the concentration by volume of CO2 (XCO2F) present in dry flue gas (see Figure 5).
Measurements | Value | Unit | Variable
Room Temperature |  | °F | TRA
N/A |  | °F | TF,SS
N/A |  | % (0-100) | XCO2,F
N/A |  | °F | TS,SS,X
N/A |  | % (0-100) | XCO2,S
Tolerances
Variation
Min
Max
Tolerances met?
Time (Minutes) | Room Ambient Temperature (°F) | Combustion/Draft Air Temperature (°F) | Flue Gas Temperature (°F) | Stack Gas Temperature (°F) | Outlet Water Temperature (°F) | Inlet Water Temperature (°F) | Water Temperature Rise (°F) | Flue CO2 Concentration (%) | Stack CO2 Concentration (%)
0
15
30
End: Steady-State Test
ASHRAE 103-1993, Section 9.1.3: Direct Measurement of the S/F Factors for Furnaces and Boilers with Barometric Draft Regulators - NOT REQUIRED FOR THIS TEST
For furnaces and boilers that are marketed and sold with attached barometric draft regulators, the S/F factor shall be determined either by using assigned factors in Table 6 or by the following test procedure. To directly measure the S/F factor, seal the barometric damper plate in the closed position. Operate the furnace or boiler until steady-state temperatures are attained. Adjust the draft in the flue within one foot of the heat exchanger exit to be between 0.075 and 0.085 in. water. A mechanical draft inducer or a natural draft developed by adjusting the height of the test stack may he used. Remove the seal from the barometric draft regulator and adjust the damper gate to achieve proper draft, as specified by the manufacturer. If the draft over the fire is specified as a range, adjust the draft to the mid-point of that range. After steady-state conditions are again achieved with the draft adjusted as specified, measure CO2 before and after dilution at points marked A and B in Figure 22. To ensure that the sample is well mixed after dilution, obtain a representative sample of stack gas by sampling from several points on a horizontal plane through the cross section of the stack. The test setup shown in Figure 22 enhances the mixing of dilution air and flue gases. Alternatively, a straight length of stack or other flue piping arrangement may be used with stack samples taken sufficiently downstream after dilution in order to obtain a well mixed sample.
Measurements for this procedure are recorded in the Steady-State Test.
ASHRAE 103-1993, Section 9.2 OR Appendix N, Section 8.4: Condensing Furnaces and Boilers, Measurement of Condensate Under Steady-State Conditions
For units with step-modulating or two-stage controls, conduct the test at both the maximum and reduced inputs. Begin a steady-state condensate collection immediately after the steady-state test has been completed as specified in 9.1.2 OR in lieu of collecting the condensate immediately after the steady state conditions have been reached as required by section 9.2 of ASHRAE 103-1993, condensate may be collected during the establishment of steady state conditions as defined by section 9.1.2.1 of ASHRAE 103-1993. Perform condensate collection for at least 30 minutes. Measure condensate mass immediately at the end of the collection period to prevent evaporation loss from the sample. Record fuel input for the 30-minute condensate collection test period. Observe and record fuel higher heating value (HHV), temperature, and pressures necessary for determining fuel energy input (QC,SS). Measure the fuel quantity and HHV with errors no greater than 1%. The humidity for the room air shall at no time exceed 80%. Determine the mass of condensate for the establishment of steady state conditions (MC,SS) in pounds by subtracting the tare container weight from the total container and condensate weight measured at the end of the 30-minute condensate collection test period.
Measurements | Value | Unit | Variable
Maximum Humidity During Steady-State Condensate Collection |  | % (0-100) | -
Humidity Condition Met? |  | - | -
Fuel Higher Heating Value |  | Btu/ft3 | HHV
Fuel Energy Input During Steady State Condensate Collection Period |  | Btu | QC,SS
Total Container and Condensate Weight |  | lb | -
Tare Container Weight |  | lb | -
Mass of Condensate Collected During Steady State Condensate Collection Period |  | lb | MC,SS
ASHRAE 103-1993, Section 9.4: Electric Boilers
Operate the boiler until steady-state conditions are reached as indicated by a temperature variation of not more than 4°F in the outlet water temperature in three successive readings taken 15 minutes apart. Take three measurements of the total power input to the boiler at 10-minute intervals, and average to determine the rated power input (EIN) in watts.
Measurements | Value | Unit | Variable
Power Input |  | Btu/h | EIN
Steady-State Conditions Met? |  | - | -
Time (Minutes) | Outlet Water Temperature (°F)
0
15
30
Cool-Down Test
ASHRAE 103-1993, Section 9.9.2: Furnaces and Boilers Equipped with Stack Dampers, Cool-Down Test Conduct the cool-down test as prescribed in 9.5, with the following modifications. 9.9.2.1 For units with integral draft diverters or draft hoods, bypass the damper control so the damper remains open during the test. 9.9.2.2 For units with barometric draft regulators, the stack damper shall be permitted to close in the normal manner as it responds to the controls.
Appendix N, Section 8.7: Cool-down test for Gas- and Oil-Fueled Boilers Without Stack Dampers After steady-state testing has been completed, turn the main burner(s) “OFF” and measure the flue gas temperature at 3.75 minutes (temperature designated as TF,OFF(t3)) and 22.5 minutes (temperature designated as TF,OFF(t4)) after the burner shut-off using the thermocouple grid described in section 7.6 of ASHRAE 103-1993. a. During this off-period, for units that do not have pump delay after shut-off, do not allow any water to circulate through the hot water boilers. b. For units that have pump delay on shut-off, except those having pump controls sensing water temperature, the unit control must stop the pump. Measure and record the time between burner shut-off and pump shut-off (t+) to the nearest second. c. For units having pump delay controls that sense water temperature, operate the pump for 15 minutes and record t+ as 15 minutes. While the pump is operating, maintain the inlet water temperature and flow rate at the same values as used during the steady-state test, as specified in sections 9.1 and 8.4.2.3 of ASHRAE 103-1993. d. For boilers that employ post-purge, measure the length of the post-purge period with a stopwatch. Record the time from burner “OFF” to combustion blower “OFF” (electrically de-energized) as tP. If tP is prescribed by the I&O manual or measured to be greater than 180 seconds, stop the combustion blower at 180 seconds and use that value for tP. Measure the flue gas temperature by means of the thermocouple grid described in section 7.6 of ASHRAE 103-1993 at the end of the post-purge period tP (TF,OFF(tP)) and at (3.75 + tP) minutes (TF,OFF(t3)) and (22.5 + tP) minutes (TF,OFF(t4)) after the main burner shuts off. If the measured tP is less than or equal to 30 seconds, record tP as 0 and conduct the cool-down test as if there is no post-purge.
Measurements | Value | Unit | Variable
Does the boiler have a pump delay? |  | - | -
Time delay between burner shut-off and pump shut-off |  | min | t+
Does the boiler employ a post-purge? |  | - | -
Post Purge Time |  | sec | tp | (Enter 0 if less than or equal to 30 seconds and 180 if greater than or equal to 180 seconds)
Temperature at the end of the post-purge period |  | °F | TF,OFF(tp)
Temperature 3.75 minutes after end of post-purge period |  | °F | TF,OFF(t3)
Temperature 22.5 minutes after end of post-purge period |  | °F | TF,OFF(t4)
ASHRAE 103-1993, Sections 9.5.2.2 - 9.5.2.5 9.5.2.2 Make a third flue gas temperature measurement 45 minutes after the burner shuts off to determine the off-period minimum flue gas temperature (TF,OFF(t5)). 9.5.2.3 During this cool-down test, measure the energy input rate to the pilot light (Qp), if the unit is so equipped, to within an error no larger than ±3 %. Record all measured values. For oil-fueled or power gas burner units employing barometric dampers for draft control and not equipped with stack dampers, maintain the draft in the flue within the same ranges specified in 9.5.1.2. 9.5.2.4 For boilers equipped with step modulating controls, the cool-down test shall be conducted after steady-state conditions have been reached at the reduced input rate, as specified in 8.4.1.1.2. 9.5.2.5 For boilers equipped with two-stage controls, separate cool-down tests shall be conducted after steady-state conditions have been reached at both the reduced and maximum fuel input rates.
Measurements | Value | Unit | Variable
Off Period Minimum Flue Gas Temperature (Equilibrium) |  | °F | TF,OFF(t5)
Fuel Energy Input Rate to Pilot Light |  | Btu/h | QP
End Cool-Down Test
Heat-Up Test
ASHRAE 103-1993, Sections 9.6.2: Flue Gas Temperature Measurement - Heat-Up Test, Gas and Oil-Fueled Boilers Approximately 50 minutes after the main burner(s) is turned off for the cool-down test, turn on the steam or hot water boiler and measure the flue gas temperature at 1.0 (TF,ON(t1)) and 5.5 (TF,ON(t2)) minutes after the main burner(s) comes on. The pump circulating the water through the hot water boiler shall be started simultaneously with the main burner(s). The water flow rate shall be the same as that maintained during the steady-state test. During the heat-up test for boilers with barometric draft regulators, maintain the draft in the flue pipe within ±0.01 in. water of the manufacturer's recommended on-period draft. Record the measured temperatures. 9.6.2.1 For boilers equipped with step modulating controls, the heat-up test shall be conducted at the reduced fuel input rate. 9.6.2.2 For boilers equipped with two-stage controls, separate heat-up tests shall be conducted at both the reduced and maximum fuel input rates.
Measurements | Value | Unit | Variable
Flue Gas Temperature at 1.0 minutes after main burner comes on |  | °F | TF,ON(t1)
Flue Gas Temperature at 5.5 minutes after main burner comes on |  | °F | TF,ON(t2)
ASHRAE 103-1993, Section 8.4.2.3: Gas and Oil-Fueled Low-Pressure Steam and Hot Water Boilers (including Direct Vent Systems) For non-condensing hot water boilers, the water flow rate shall be adjusted to produce a water temperature rise of 19°F to 24°F during the steady-state test described in Section 9. During the steady-state and heat-up tests, the hot water boiler shall be supplied with water having a temperature of at least 120°F but not more than 124°F. 8.4.2.3.1 For steam boilers, the steam pressure shall be at atmospheric or at any pressure not exceeding 2 psig during the steady-state test. 8.4.2.3.2 For condensing hot water boilers, the water flow rate shall be adjusted to produce a water temperature rise between 19.5°F and 20.5°F during the steady-state test described in 9.1. During the steady-state and heat-up tests, the condensing boiler shall be supplied with return water having a temperature of 120°F. The maximum permissible variation of the return water temperature from the required value during the steady-state and heat-up tests shall not exceed ±2°F, except during the first 30 seconds after start-up, when it shall not exceed ± 10°F, and between 30 and 60 seconds after start-up, when it shall not exceed ±5°F.
ASHRAE 103-1993, Section 8.4.2.5: Electric Boilers Adjust the flow of water or steam as specified in 8.4.2.3 for gas and oil-fueled boilers.
Non-Condensing Hot Water Boilers - NOT REQUIRED FOR THIS TEST
Measurements | Tested Value |  | Tolerance |  | Unit | Tolerance Met?
| Min | Max | Min | Max
Supply Water Temperature |  |  | N/A | N/A | °F | N/A
Condensing Hot Water Boilers - NOT REQUIRED FOR THIS TEST
Measurements | Tested Value |  | Tolerance |  | Unit | Tolerance Met?
| Min | Max | Min | Max
Return Water Temperature (second 0 to second 30) |  |  |  |  | °F | N/A
Return Water Temperature (second 30 to second 60) |  |  |  |  | °F | N/A
Return Water Temperature (second 60 to end of test) |  |  |  |  | °F | N/A
End: Heat-Up Test
ASHRAE 103-1993, Section 9.7: Optional Tracer Gas Test Procedures for Determining Draft Factors for D_P, D_F, and D_S for Systems Equipped with Power Burners or Direct Vent and Not Equipped with Stack Dampers
Measurements | Value | Unit | Variable
Was a draft imposed during the steady-state or cool-down tests? |  | - | -
ASHRAE 103-1993, Section 9.7.1: Feeding Tracer Gas The tracer gas chosen for this task should have a density that is less than or approximately equal to the density of air. Use a gas that is of a different chemical species or different concentration from the flue gas to be measured and unreactive with the environment to be encountered. Within one minute after the power burner or draft inducer is shut off to start the cool-down test for determining DP, begin feeding a tracer gas into the combustion chamber at a constant flow rate, VT, and at a point that will allow for the best possible mixing with the air flowing through the chamber. (On units equipped with an oil-fired power burner, the best location for injecting this tracer gas appears to be through a hole drilled in the air tube.) Periodically measure the value of VT with an instantaneously reading flowmeter having an accuracy of ±3 % of the quantity measured and maintain that value at less than 1 % of the airflow rate through the furnace. If a combustible tracer gas is used, there should be a delay period between the time the unit is shut off and the time the tracer gas is first injected to prevent ignition of the tracer gas.
Measurements | Value | Unit | Variable
Flow Rate of Tracer Gas into Heat Exchanger during the Measurement Period |  | cfm | VT
ASHRAE 103-1993, Section 9.7.2: Measurement Obtain the concentration of tracer gas present in the flue gas sample (CT) using an instrument that will result in an accuracy of ±2 % in the measured value. If the use of a continuously reading type instrument results in a delay time between the drawing of a sample and its analysis, take this delay into account so the temperature measurement and the measurement of tracer gas concentration coincide. Determine the temperature of the tracer gas entering the flowmeter (TT) and the barometric pressure (PB).
Measurements | Value | Unit | Variable
Percent by Volume of Measured Tracer Gas in the Flue Gas Sample |  | % (0-100) | CT
Percent by Volume of Measureable Tracer Gas in the Standard Tracer Gas Mixture |  | % (0-100) | CTM
Temperature of Tracer Gas Entering the Flowmeter |  | °F | TT
Barometric Pressure |  | in. HG | PB
Density of Flue Gas at TT |  | lb/ft3 | ρF
ASHRAE 103-1993, Section 9.7.3: Timing Between 5 and 6 minutes after the unit is shut off to start the cool-down test, measure the percent volumetric concentration of tracer gas present in the diluted flue gas sample, CT At the same time, for units where draft is not maintained, measure the flue gas temperature, TF,OFF, using the thermocouple grid described in 7.6. For systems that employ post purge, with a post-purge time period tP, measure the percent volumetric concentration of the tracer gas present in the diluted flue gas sample, CT, at between (5 + tP) and (6 + tP) minutes after the burner is shut off. During the same time period, for units where draft is not maintained, measure the flue gas temperature, TF,OFF, using the thermocouple grid described in 7.6.
Measurements | Value | Unit | Variable
Flue Gas Tempearture When Sampled |  | °F | TF,OFF
Appendix N, Section 8.9: Calculation options. The rate of the flue gas mass flow through the furnace and the factors DP, DF, and DS are calculated by the equations in sections 11.6.1, 11.6.2, 11.6.3, 11.6.4, 11.7.1, and 11.7.2 of ASHRAE 103-1993. On units whose design is such that there is no measurable airflow through the combustion chamber and heat exchanger when the burner(s) is (are) off (as determined by the optional test procedure in section 7.10 of this appendix), DF and DP may be set equal to 0.05.
ASHRAE 103-1993, Section 9.7.5: Modulating Units For units with two-stage modulating controls, the optional tracer gas test shall be conducted at both the maximum and the reduced inputs. For units with step modulating controls, the optional tracer gas test shall be conducted at the reduced input only.
End: Optional Tracer Gas Test Procedures for Determining Draft Factors for DP, DF, and DS for Systems Equipped with Power Burners or Direct Vent and Not Equipped with Stack Dampers
ASHRAE 103-1993, Section 9.7.6: Tracer Gas Test Procedures for Determining Off-Cycle Loss Factor K_L for Atmospheric Systems with Integral Draft Diverter or Draft Hood and Equipped with Either an Electro-Mechanical Inlet or Flue Damper That Restricts the Flow Through the Heat Exchanger in the Off-Cycle - NOT REQUIRED FOR THIS TEST
9.7.6.1 The tracer gas chosen for this task should have a density that is less than or approximately equal to the density of air. Use a gas that is of a different chemical species or different concentration from the flue gas to be measured and unreactive with the environment to be encountered. Obtain the concentration of tracer gas present in the flue gas sample (Cr) using an analyzer or instrument that will result in an accuracy of ±2 % in the measured value. Determine the temperature of the tracer gas entering the flowmeter (Tr) and the barometric pressure (PB).
Measurements | With Damper Closed | With Damper Open | Unit | Variable
Percent by Volume of Measured Tracer Gas in the Flue Gas Sample |  |  | % (0-100) | CT
Temperature of Tracer Gas Entering the Flowmeter |  |  | °F | TT
Barometric Pressure |  |  | in. HG | PB
Density of Flue Gas at TT |  |  | lb/ft3 | ρF
9.7.6.2 After the completion of the heat-up test in 9.6, tum the burner OFF. On units equipped with integral draft diverters, remove the blocking over the draft diverter and the restriction in the test stack that were installed during the steady-state test in 9.1.4. Do not remove the insulation covering the draft diverter surfaces. On units equipped with a draft hood, cover the 5-ft stack with insulation having an R-value not less than 7 and an outer layer of aluminum foil as described in 8.8.5. In the meantime, sample and feed the ambient air to the tracer gas analyzer and record the background concentration CTB of the tracer gas to be used for the test. (One data point is usually sufficient.)
Measurements | With Damper Closed | With Damper Open | Unit | Variable
Background concentration of the tracer gas |  |  | % (0-100) | CTB
9.7.6.3 Tum the burner ON until steady-state conditions are again achieved as specified in 9 .1.2.1. Turn the burner OFF for a 10-minute cool-down period. Adjust or bypass the electro-mechanical damper (inlet damper or flue damper) so that it remains open during this cool-down period. Within one minute after the unit is shut off to start this cool-down test, begin feeding a tracer gas with a known, certified concentration CTM at a constant flow rate VT into the lower part of the test stack just above the test plane where the stack thermocouple grid is located (see 8.2.1.5.1). Periodically measure the value of VT with an instantaneously reading flowmeter having an accuracy of ±3 % of the quantity measured and maintain that value of tracer gas flow rate at less than 1 % of the airflow rate through the test stack.
Measurements | With Damper Closed | With Damper Open | Unit | Variable
Percent by volume of measureable tracer gas in the standard tracer gas mixture |  |  | % (0-100) | CTM
Flow Rate of Tracer Gas into Heat Exchanger during the Measurement Period |  |  | cfm | VT
9.7.6.4 Within one minute after the tracer gas flow is started, connect the tracer gas sampling line to the sampling probe located at a plane inside and 6 in. below the top exit of the test stack. Measure the transport delay time that is equal to the time between the connecting of the sampling line and the initial response of the tracer gas analyzer. Add to this transport time the time required for the analyzer to reach 90% of its steady-state value as specified in the analyzer's operation manual. The sum of these two values is the tracer gas sample delay time needed to match the concentration measurement to the temperature measurement in the off-period loss calculation. Make sure that a well-mixed sample is collected by using a multi-hole sampling probe, as recommended in Appendix D, section B. Return the sample gas (after exiting the gas analyzer) to the top of the test stack downstream of the plane of collection.
9.7.6.5 At five minutes after the unit is shut off to start the cool-down test, measure and record the percent volumetric concentration of tracer gas present in the stack gas sample, CT, at the location specified in 9.7.6.4. At the same time, measure the stack gas temperature, TS,OFF, using the thermocouple grid in the test plane (see 8.2.1.5.1). The data measurement and recording should be done at a time interval, Δt, of five seconds for the next two to three minutes. The exact length of time required for the tracer gas data measurement is equal to the tracer gas sample delay time (see 9.7.6.4) plus one minute. (Even though only one minute of tracer gas data is required for the computation of the off-cycle loss, the longer time is needed to take into account the time delay between the concentration data and the temperature data.) Stop the tracer gas injection and sampling after the required data are measured and recorded. Disconnect the tracer gas sampling line from the sample probe and sample the ambient air to clear the line.
Measurements | With Damper Closed | With Damper Open | Unit | Variable
Stack gas tempearture |  |  | °F | TS,OFF
9.7.6.6 At the end of the 10-minute cool-down period, tum on the burner until steady-state conditions are again achieved as specified in 9.1.2.1. Tum the burner OFF for another 10-minute cool-down period. Let the electro-mechanical damper (inlet damper or flue damper) close the way it is designed to. Repeat the test steps of 9.7.6.3 through 9.7.6.5 except that the electro-mechanical damper is to remain closed. Note that the tracer gas feeding rate, VT, may have to be adjusted to a lower rate to keep the sample concentration within the range of the gas analyzer used. 9.7.6.7 The rate of the stack gas flow through the stack, the cycle sensible loss rate, and the loss factor KL are calculated by the equations in 11.8.1.
Measurements | With Damper Closed | With Damper Open | Unit | Variable
Off-Cycle Sensible Loss |  |  | Btu | QS,OFF
End: Tracer Gas Test Procedures for Determining Off-Cycle Loss Factor KL
ASHRAE 103-1993, Section 9.8: Condensing Furnaces and Boilers-Measurement of Condensate Heat Loss Under Cyclic Conditions
For units with modulating controls, the following applies: (a) for step modulating units, the test is conducted at reduced input rate only; (b) for two-stage units, the test is conducted at both maximum and reduced input rates.
9.8.1 Preparation for Test Control devices shall be installed to allow cyclical operation of the unit and return water or airflows as described in 9.2. The test unit shall be leveled prior to the test. Humidity of the room air shall at no time exceed 80%.
9.8.2 Condensate Collection Containers The condensing furnace or boiler shall be tested by the flue loss method in accordance with the provisions for condensing units, as specified in Section 8. The condensate collection containers shall be dried prior to each use and shall be at room ambient temperature prior to a sample collection. Tare weight of the collection container must be measured and recorded prior to each sample collection.
9.8.3 Test Requirements The unit shall be operated in a cyclical manner until flue gas temperatures at the end of each on-cycle are within 5°F of each other for two consecutive cycles. On-cycle and off-cycle times are listed in Table 9. Control of ON or OFF operation actions shall be within ±6 seconds of the scheduled time. Begin three test cycles. Return air temperature for furnaces shall be as specified in 8.5.2. Return water temperature for boilers shall be as specified in 8.4.2.3. Operation of the furnace blower shall conform to the time delay requirements specified in 9.5.1 for cool-down and heat-up tests. Operation of the boiler pump shall conform to the time delay requirements specified in 9.6.1.
9.8.4 Condensate Collection Begin condensate collection at one minute before the on-cycle period of the first test cycle. The container shall be removed one minute before the end of each off-cycle period. Condensate mass shall be measured for each test cycle.
9.8.5 Measurements Fuel input shall be recorded during the entire test period starting at the beginning of the on-time period of the first cycle to the beginning of the ontime period of the second cycle, etc., for each of the test cycles. Fuel higher heating value (HHV), temperature, and pressures necessary for determining fuel energy input (QC) shall be recorded. Determine the mass of condensate for each cycle (MC) in pounds. If at the end of three cycles, the sample standard deviation is within 20% of the mean value for three cycles, use total condensate collected in the three cycles as MC, if not, continue collection for an additional three cycles and use the total condensate collected for the six cycles as MC. Determine the fuel energy input during the three or six test cycles (QC) expressed in Btu.
Measurements | Value | Unit | Variable
Maximum Humidity During Test |  | % (0-100) | -
Humidity Condition Met? |  | - | -
Flue Gas Temperature (Cycle 1) |  | °F | -
Flue Gas Temperature (Cycle 2) |  | °F | -
Flue Gas Temperature Condition Met? |  | - | -
Room Air Temperature |  | °F | -
Fuel Higher Heating Value |  | Btu/lb | HHV
Condensate Mass Condition Met? |  | - | -
Fuel Energy Input |  | Btu | QC
Total Condensate Collected |  | lb | MC
| Fuel Energy Input | Mass of Condensate
Test Cycle | Btu | lb
1
2
3
4, if necessary
5, if necessary
6, if necessary
Appendix N, Section 8.10: Optional test procedures for condensing furnaces and boilers that have no off-period flue losses.
For units that have applied the test method in section 7.10 of this appendix to determine that no measurable airflow exists through the combustion chamber and heat exchanger during the burner off-period and having post-purge periods of less than 5 seconds, the cool-down and heat-up tests specified in sections 9.5 and 9.6 of ASHRAE 103-1993 may be omitted. In lieu of conducting the cool-down and heat-up tests, the tester may use the losses determined during the steady-state test described in section 9.1 of ASHRAE 103-1993 when calculating heating seasonal efficiency, EffyHS.
Measurements | Value | Unit | Variable
Is post purge time <5 seconds? |  | - | -
Was optional tracer gas test performed that indicates no flow through the heat exchanger when the burner is off? | Fill in Tracer Gas Draft Factors table on Test Conditions tab | - | -
If the answer to the two above questions is "Yes" for both, the heat-up and cool-down tests are optional. Were the heat-up and cool-down tests performed? |  | - | -

## Reduced Test
Title Block
Test Report Template Name: | Consumer Boiler
Version Number: | v1.1 |  |  | Back to Instructions tab
Latest Template Revision: | 2019-09-13
Tab Name: | Reduced Test
File Name: | Consumer Boiler - v1.1.xlsx
Test Completion Date: | 0
ASHRAE 103-1993, Section 9.1: Steady-State Test, All Gas and Oil-Fired Units (except Electric) AND Appendix N, Sections 8.1 - 8.3
Appendix N, Section 8.0: Test procedure. Conduct testing and measurements as specified in section 9 of ASHRAE 103-1993 except for sections 9.1.2.2.1, 9.1.2.2.2 and as specified in sections 8.1 through 8.3 of this appendix.
Appendix N, Section 8.1: Fuel input. For gas units, measure and record the steady-state gas input rate in Btu/hr, including pilot gas, corrected to standard conditions of 60 °F and 30 in. Hg. Use measured values of gas temperature and pressure at the meter and barometric pressure to correct the metered gas flow rate to the above standard conditions. For oil units, measure and record the steady-state fuel input rate.
Measurements | Value | Unit | Variable
Nameplate Input Rate |  | Btu/h | QIN | (including any pilot light input)
Appendix N, Section 8.2: Electrical input. For furnaces and boilers, during the steady-state test, perform a single measurement of all of the electrical power involved in burner operation (PE), including energizing the ignition system, controls, gas valve or oil control valve, and draft inducer, if applicable. For boilers, the measurement of PE must include the boiler pump if so equipped. If the boiler pump does not operate during the measurement of PE, add the boiler pump nameplate power to the measurement of PE. If the boiler pump nameplate power is not available, use 0.13 kW.
Measurements | Value | Unit | Variable
Steady State Electrical Power to Burner (including energizing the ignition system, controls, gas valve or oil control valve, draft inducer, and boiler pump) |  | kW | -
Boiler Pump Nameplate Power, if applicable (enter 0.13 if not available) |  | kW | BE
Was the boiler pump electrical usage captured in the steady-state measurement? |  | - | -
Steady State Electrical Power to Burner |  | kW | PE
Appendix N, Section 8.3: Input to interrupted ignition device. For burners equipped with an interrupted ignition device, record the nameplate electric power used by the ignition device, PEIG, or record that PEIG = 0.4 kW if no nameplate power input is provided. Record the nameplate ignition device on-time interval, tIG, or, if the nameplate does not provide the ignition device on-time interval, measure the on-time interval with a stopwatch at the beginning of the test, starting when the burner is turned on. Set tIG = 0 and PEIG = 0 if the device on-time interval is less than or equal to 5 seconds after the burner is on.
Measurements | Value | Unit | Variable
Electrical Power Input to Interrupted Ignition Device |  | kW | PEIG
Nameplate Ignition Device On-time Interval |  | min | tIG
ASHRAE 103-1993, Section 8.4.2.3: Gas and Oil-Fueled Low-Pressure Steam and Hot Water Boilers (including Direct Vent Systems) For non-condensing hot water boilers, the water flow rate shall be adjusted to produce a water temperature rise of 19°F to 24°F during the steady-state test described in Section 9. During the steady-state and heat-up tests, the hot water boiler shall be supplied with water having a temperature of at least 120°F but not more than 124°F. 8.4.2.3.1 For steam boilers, the steam pressure shall be at atmospheric or at any pressure not exceeding 2 psig during the steady-state test. 8.4.2.3.2 For condensing hot water boilers, the water flow rate shall be adjusted to produce a water temperature rise between 19.5°F and 20.5°F during the steady-state test described in 9.1. During the steady-state and heat-up tests, the condensing boiler shall be supplied with return water having a temperature of 120°F. The maximum permissible variation of the return water temperature from the required value during the steady-state and heat-up tests shall not exceed ±2°F, except during the first 30 seconds after start-up, when it shall not exceed ± 10°F, and between 30 and 60 seconds after start-up, when it shall not exceed ±5°F.
ASHRAE 103-1993, Section 8.4.2.5: Electric Boilers Adjust the flow of water or steam as specified in 8.4.2.3 for gas and oil-fueled boilers.
Non-Condensing Hot Water Boilers - NOT REQUIRED FOR THIS TEST
Measurements | Tested Value |  | Tolerance |  | Unit | Tolerance Met?
| Min | Max | Min | Max
Supply Water Temperature | N/A | N/A | N/A | N/A | °F | N/A
Temperature Rise | N/A | N/A | N/A | N/A | °F | N/A
Condensing Hot Water Boilers - NOT REQUIRED FOR THIS TEST
Measurements | Tested Value |  | Tolerance |  | Unit | Tolerance Met?
| Min | Max | Min | Max
Return Water Temperature (second 0 to second 30) |  |  |  |  | °F | N/A
Return Water Temperature (second 30 to second 60) |  |  |  |  | °F | N/A
Return Water Temperature (second 60 to end of test) |  |  |  |  | °F | N/A
Temperature Rise | N/A | N/A | N/A | N/A | °F | N/A
Steam Boilers - NOT REQUIRED FOR THIS TEST
Measurements | Tested Value |  | Tolerance |  | Unit | Tolerance Met?
| Min | Max | Min | Max
Steam Pressure |  |  |  |  | psig | N/A
ASHRAE 103-1993, Section 8.5: Room Ambient Temperature (TRA)
ASHRAE 103-1993, Section 8.5.1: Measurement Room temperature shall be the arithmetic average temperature of the test area, determined by measurement with four No. 24 AWG bead-type thermocouples with junctions shielded against radiation, located approximately at 90° positions on a circle circumscribing the appliance or appliance enclosure under test, in a horizontal plane approximately at the vertical midpoint of the appliance or test enclosure, and with the junctions approximately 24 in. from the sides of the appliance or test enclosure and located so as not to be affected by other than room air. The temperature of the air for combustion and the air for draft control shall not differ more than ±5°F from the room temperature as measured above. Where there is less than 5°F stratification, one room air thermocouple may be used.
ASHRAE 103-1993, Section 8.5.2: Limitations During the time required to perform all the testing and measuring procedures specified in Section 9, maintain the room temperature within ±5°F of the air temperature value measured at the end of the steady-state performance test (TRA). During these tests, the room temperature may not fall below 65°F or exceed 100°F, except that for condensing furnaces and boilers, it shall not exceed 85°F.
ASHRAE 103-1993, Section 9.1.2: Steady-State Conditions and Requirements
ASHRAE 103-1993, Section 9.1.2.1: Conditions Begin the steady-state performance test by operating the burner and the circulating air blower or water pump until steady-state conditions are attained as indicated by a temperature variation in three successive readings, taken 15 minutes apart, of not more than (1) 3°F in the stack gas temperature for furnaces and boilers equipped with draft diverters; (2) 5°F in the flue gas temperature for furnaces and boilers equipped with either draft hoods, direct exhaust, or direct vent systems; (3) 4 °F in the outlet water temperature for hot water boilers; (4) 1°F in the flue gas temperature for condensing furnaces and boilers; and (5) 1°F in the flue gas and supply (outlet) water temperatures for condensing hot water boilers.
ASHRAE 103-1993, Section: 9.1.2.2 Input (Replaced by Appendix N Sections 8.1-8.3, which are addressed above)
ASHRAE 103-1993, Section 9.1.2.3: Measurements
9.1.2.3.1 On units employing draft hoods or direct exhaust or direct vent systems, measure the room temperature (TRA) as described in 8.5 and measure the steady-state flue gas temperature (TF,SS,X) using the thermocouple grid located in the flue pipe. Secure a sample of the flue gas in the plane of temperature measurement. Determine the concentration by volume of CO2 (XCO2F) present in dry flue gas (see Figures 3c, 3d, and 4). On units employing a draft hood, secure a sample of the stack gases at either a horizontal plane in the stack 12 in. downstream of the draft hood or in a horizontal plane 6 in. from the top of the test stack. Make sure that there are no holes or air leaks in the section of the stack from the draft hood up to the location where the stack gas is sampled. Determine the concentration by volume of carbon dioxide (XCO2S) present in the dry stack gas. Use Figures 3a and 3b (test stack for units with draft diverter) as reference for the location of CO2 measurement.
9.1.2.3.2 On units employing draft diverters, measure the room temperature (TRA) as described in 8.5 and measure the steady-state stack gas temperature (TS,SS,X) using the thermocouple grid located in the 5-ft test stack as described in 8.2.1.5 or 8.3.1.5. Secure a sample of the stack gases either at the plane where TS,SS,X is measured or in a horizontal plane 6 in. from the top of the test stack. (If the stack gas is sampled at this latter location, be sure that there are no holes or air leaks between this location and the plane where the TS,SS,X is measured.) Determine the concentration by volume of carbon dioxide (XCO2S) present in dry stack gas (see Figures 3a and 3b). After the above test measurements have been completed on units employing integral draft diverters, secure a sample of the flue gases at the inlet to the draft diverter and determine the concentration of flue CO2 (XCO2F) present (see Figures 3a and 3b). In obtaining this sample of flue gas, move the sampling probe around to ensure that an average value is obtained for the CO2 concentration. For units with multiple heat exchanger outlets, draw a sample of equal size from each outlet to obtain the average CO2 concentration for the unit.
9.1.2.3.3 On units employing barometric draft regulators, measure the room air temperature (TRA). Measure the steady-state flue gas temperature (TF,SS) using the thermocouple grid located in the flue pipe. Secure a sample of the flue gas in the plane of temperature measurement and determine the concentration by volume of CO2 (XCO2F) present in dry flue gas (see Figure 5).
Measurements | Value | Unit | Variable
Room Temperature |  | °F | TRA
N/A |  | °F | TF,SS
N/A |  | % (0-100) | XCO2,F
N/A |  | °F | TS,SS,X
N/A |  | % (0-100) | XCO2,S
Tolerances
Variation
Min
Max
Tolerances met?
Time (Minutes) | Room Ambient Temperature (°F) | Combustion/Draft Air Temperature (°F) | Flue Gas Temperature (°F) | Stack Gas Temperature (°F) | Outlet Water Temperature (°F) | Inlet Water Temperature (°F) | Water Temperature Rise (°F) | Flue CO2 Concentration (%) | Stack CO2 Concentration (%)
0
15
30
End: Steady-State Test
ASHRAE 103-1993, Section 9.1.3: Direct Measurement of the S/F Factors for Furnaces and Boilers with Barometric Draft Regulators - NOT REQUIRED FOR THIS TEST
For furnaces and boilers that are marketed and sold with attached barometric draft regulators, the S/F factor shall be determined either by using assigned factors in Table 6 or by the following test procedure. To directly measure the S/F factor, seal the barometric damper plate in the closed position. Operate the furnace or boiler until steady-state temperatures are attained. Adjust the draft in the flue within one foot of the heat exchanger exit to be between 0.075 and 0.085 in. water. A mechanical draft inducer or a natural draft developed by adjusting the height of the test stack may he used. Remove the seal from the barometric draft regulator and adjust the damper gate to achieve proper draft, as specified by the manufacturer. If the draft over the fire is specified as a range, adjust the draft to the mid-point of that range. After steady-state conditions are again achieved with the draft adjusted as specified, measure CO2 before and after dilution at points marked A and B in Figure 22. To ensure that the sample is well mixed after dilution, obtain a representative sample of stack gas by sampling from several points on a horizontal plane through the cross section of the stack. The test setup shown in Figure 22 enhances the mixing of dilution air and flue gases. Alternatively, a straight length of stack or other flue piping arrangement may be used with stack samples taken sufficiently downstream after dilution in order to obtain a well mixed sample.
Measurements for this procedure are recorded in the Steady-State Test.
ASHRAE 103-1993, Section 9.2 OR Appendix N, Section 8.4: Condensing Furnaces and Boilers, Measurement of Condensate Under Steady-State Conditions
For units with step-modulating or two-stage controls, conduct the test at both the maximum and reduced inputs. Begin a steady-state condensate collection immediately after the steady-state test has been completed as specified in 9.1.2 OR in lieu of collecting the condensate immediately after the steady state conditions have been reached as required by section 9.2 of ASHRAE 103-1993, condensate may be collected during the establishment of steady state conditions as defined by section 9.1.2.1 of ASHRAE 103-1993. Perform condensate collection for at least 30 minutes. Measure condensate mass immediately at the end of the collection period to prevent evaporation loss from the sample. Record fuel input for the 30-minute condensate collection test period. Observe and record fuel higher heating value (HHV), temperature, and pressures necessary for determining fuel energy input (QC,SS). Measure the fuel quantity and HHV with errors no greater than 1%. The humidity for the room air shall at no time exceed 80%. Determine the mass of condensate for the establishment of steady state conditions (MC,SS) in pounds by subtracting the tare container weight from the total container and condensate weight measured at the end of the 30-minute condensate collection test period.
Measurements | Value | Unit | Variable
Maximum Humidity During Steady-State Condensate Collection |  | % (0-100) | -
Humidity Condition Met? |  | - | -
Fuel Higher Heating Value |  | Btu/ft3 | HHV
Fuel Energy Input During Steady State Condensate Collection Period |  | Btu | QC,SS
Total Container and Condensate Weight |  | lb | -
Tare Container Weight |  | lb | -
Mass of Condensate Collected During Steady State Condensate Collection Period |  | lb | MC,SS
ASHRAE 103-1993, Section 9.4: Electric Boilers
Operate the boiler until steady-state conditions are reached as indicated by a temperature variation of not more than 4°F in the outlet water temperature in three successive readings taken 15 minutes apart. Take three measurements of the total power input to the boiler at 10-minute intervals, and average to determine the rated power input (EIN) in watts.
Measurements | Value | Unit | Variable
Power Input |  | Btu/h | EIN
Steady-State Conditions Met? |  | - | -
Time (Minutes) | Outlet Water Temperature (°F)
0
15
30
Cool-Down Test
ASHRAE 103-1993, Section 9.9.2: Furnaces and Boilers Equipped with Stack Dampers, Cool-Down Test Conduct the cool-down test as prescribed in 9.5, with the following modifications. 9.9.2.1 For units with integral draft diverters or draft hoods, bypass the damper control so the damper remains open during the test. 9.9.2.2 For units with barometric draft regulators, the stack damper shall be permitted to close in the normal manner as it responds to the controls.
Appendix N, Section 8.7: Cool-down test for gas- and oil-fueled boilers After steady-state testing has been completed, turn the main burner(s) “OFF” and measure the flue gas temperature at 3.75 minutes (temperature designated as TF,OFF(t3)) and 22.5 minutes (temperature designated as TF,OFF(t4)) after the burner shut-off using the thermocouple grid described in section 7.6 of ASHRAE 103-1993. a. During this off-period, for units that do not have pump delay after shut-off, do not allow any water to circulate through the hot water boilers. b. For units that have pump delay on shut-off, except those having pump controls sensing water temperature, the unit control must stop the pump. Measure and record the time between burner shut-off and pump shut-off (t+) to the nearest second. c. For units having pump delay controls that sense water temperature, operate the pump for 15 minutes and record t+ as 15 minutes. While the pump is operating, maintain the inlet water temperature and flow rate at the same values as used during the steady-state test, as specified in sections 9.1 and 8.4.2.3 of ASHRAE 103-1993. d. For boilers that employ post-purge, measure the length of the post-purge period with a stopwatch. Record the time from burner “OFF” to combustion blower “OFF” (electrically de-energized) as tP. If tP is prescribed by the I&O manual or measured to be greater than 180 seconds, stop the combustion blower at 180 seconds and use that value for tP. Measure the flue gas temperature by means of the thermocouple grid described in section 7.6 of ASHRAE 103-1993 at the end of the post-purge period tP (TF,OFF(tP)) and at (3.75 + tP) minutes (TF,OFF(t3)) and (22.5 + tP) minutes (TF,OFF(t4)) after the main burner shuts off. If the measured tP is less than or equal to 30 seconds, record tP as 0 and conduct the cool-down test as if there is no post-purge.
Measurements | Value | Unit | Variable
Does the boiler have a pump delay? |  | - | -
Time delay between burner shut-off and pump shut-off |  | min | t+
Does the boiler employ a post-purge? |  | - | -
Post Purge Time |  | sec | tp | (Enter 0 if less than or equal to 30 seconds and 180 if greater than or equal to 180 seconds)
Temperature at the end of the post-purge period |  | °F | TF,OFF(tp)
Temperature 3.75 minutes after end of post-purge period |  | °F | TF,OFF(t3)
Temperature 22.5 minutes after end of post-purge period |  | °F | TF,OFF(t4)
ASHRAE 103-1993, Sections 9.5.2.2 - 9.5.2.5 9.5.2.2 Make a third flue gas temperature measurement 45 minutes after the burner shuts off to determine the off-period minimum flue gas temperature (TF,OFF(t5)). 9.5.2.3 During this cool-down test, measure the energy input rate to the pilot light (Qp), if the unit is so equipped, to within an error no larger than ±3 %. Record all measured values. For oil-fueled or power gas burner units employing barometric dampers for draft control and not equipped with stack dampers, maintain the draft in the flue within the same ranges specified in 9.5.1.2. 9.5.2.4 For boilers equipped with step modulating controls, the cool-down test shall be conducted after steady-state conditions have been reached at the reduced input rate, as specified in 8.4.1.1.2. 9.5.2.5 For boilers equipped with two-stage controls, separate cool-down tests shall be conducted after steady-state conditions have been reached at both the reduced and maximum fuel input rates.
Measurements | Value | Unit | Variable
Off Period Minimum Flue Gas Temperature (Equilibrium) |  | °F | TF,OFF(t5)
Fuel Energy Input Rate to Pilot Light |  | Btu/h | QP
End Cool-Down Test
Heat-Up Test
ASHRAE 103-1993, Sections 9.6.2: Flue Gas Temperature Measurement - Heat-Up Test, Gas and Oil-Fueled Boilers Approximately 50 minutes after the main burner(s) is turned off for the cool-down test, turn on the steam or hot water boiler and measure the flue gas temperature at 1.0 (TF,ON(t1)) and 5.5 (TF,ON(t2)) minutes after the main burner(s) comes on. The pump circulating the water through the hot water boiler shall be started simultaneously with the main burner(s). The water flow rate shall be the same as that maintained during the steady-state test. During the heat-up test for boilers with barometric draft regulators, maintain the draft in the flue pipe within ±0.01 in. water of the manufacturer's recommended on-period draft. Record the measured temperatures. 9.6.2.1 For boilers equipped with step modulating controls, the heat-up test shall be conducted at the reduced fuel input rate. 9.6.2.2 For boilers equipped with two-stage controls, separate heat-up tests shall be conducted at both the reduced and maximum fuel input rates.
Measurements | Value | Unit | Variable
Flue Gas Temperature at 1.0 minutes after main burner comes on |  | °F | TF,ON(t1)
Flue Gas Temperature at 5.5 minutes after main burner comes on |  | °F | TF,ON(t2)
ASHRAE 103-1993, Section 8.4.2.3: Gas and Oil-Fueled Low-Pressure Steam and Hot Water Boilers (including Direct Vent Systems) For non-condensing hot water boilers, the water flow rate shall be adjusted to produce a water temperature rise of 19°F to 24°F during the steady-state test described in Section 9. During the steady-state and heat-up tests, the hot water boiler shall be supplied with water having a temperature of at least 120°F but not more than 124°F. 8.4.2.3.1 For steam boilers, the steam pressure shall be at atmospheric or at any pressure not exceeding 2 psig during the steady-state test. 8.4.2.3.2 For condensing hot water boilers, the water flow rate shall be adjusted to produce a water temperature rise between 19.5°F and 20.5°F during the steady-state test described in 9.1. During the steady-state and heat-up tests, the condensing boiler shall be supplied with return water having a temperature of 120°F. The maximum permissible variation of the return water temperature from the required value during the steady-state and heat-up tests shall not exceed ±2°F, except during the first 30 seconds after start-up, when it shall not exceed ± 10°F, and between 30 and 60 seconds after start-up, when it shall not exceed ±5°F.
ASHRAE 103-1993, Section 8.4.2.5: Electric Boilers Adjust the flow of water or steam as specified in 8.4.2.3 for gas and oil-fueled boilers.
Non-Condensing Hot Water Boilers - NOT REQUIRED FOR THIS TEST
Measurements | Tested Value |  | Tolerance |  | Unit | Tolerance Met?
| Min | Max | Min | Max
Supply Water Temperature |  |  | N/A | N/A | °F | N/A
Condensing Hot Water Boilers - NOT REQUIRED FOR THIS TEST
Measurements | Tested Value |  | Tolerance |  | Unit | Tolerance Met?
| Min | Max | Min | Max
Return Water Temperature (second 0 to second 30) |  |  |  |  | °F | N/A
Return Water Temperature (second 30 to second 60) |  |  |  |  | °F | N/A
Return Water Temperature (second 60 to end of test) |  |  |  |  | °F | N/A
End: Heat-Up Test
ASHRAE 103-1993, Section 9.7: Optional Tracer Gas Test Procedures for Determining Draft Factors for D_P, D_F, and D_S for Systems Equipped with Power Burners or Direct Vent and Not Equipped with Stack Dampers
Measurements | Value | Unit | Variable
Was a draft imposed during the steady-state or cool-down tests? |  | - | -
ASHRAE 103-1993, Section 9.7.1: Feeding Tracer Gas The tracer gas chosen for this task should have a density that is less than or approximately equal to the density of air. Use a gas that is of a different chemical species or different concentration from the flue gas to be measured and unreactive with the environment to be encountered. Within one minute after the power burner or draft inducer is shut off to start the cool-down test for determining DP, begin feeding a tracer gas into the combustion chamber at a constant flow rate, VT, and at a point that will allow for the best possible mixing with the air flowing through the chamber. (On units equipped with an oil-fired power burner, the best location for injecting this tracer gas appears to be through a hole drilled in the air tube.) Periodically measure the value of VT with an instantaneously reading flowmeter having an accuracy of ±3 % of the quantity measured and maintain that value at less than 1 % of the airflow rate through the furnace. If a combustible tracer gas is used, there should be a delay period between the time the unit is shut off and the time the tracer gas is first injected to prevent ignition of the tracer gas.
Measurements | Value | Unit | Variable
Flow rate of tracer gas into heat exchanger during the measurement period |  | cfm | VT
ASHRAE 103-1993, Section 9.7.2: Measurement Obtain the concentration of tracer gas present in the flue gas sample (CT) using an instrument that will result in an accuracy of ±2 % in the measured value. If the use of a continuously reading type instrument results in a delay time between the drawing of a sample and its analysis, take this delay into account so the temperature measurement and the measurement of tracer gas concentration coincide. Determine the temperature of the tracer gas entering the flowmeter (TT) and the barometric pressure (PB).
Measurements | Value | Unit | Variable
Percent by volume of measured tracer gas in the flue gas sample |  | % (0-100) | CT
Percent by volume of measureable tracer gas in the standard tracer gas mixture |  | % (0-100) | CTM
Temperature of tracer gas entering the flowmeter |  | °F | TT
Barometric Pressure |  | in. HG | PB
Density of flue gas at TT |  | lb/ft3 | ρF
ASHRAE 103-1993, Section 9.7.3: Timing Between 5 and 6 minutes after the unit is shut off to start the cool-down test, measure the percent volumetric concentration of tracer gas present in the diluted flue gas sample, CT At the same time, for units where draft is not maintained, measure the flue gas temperature, TF,OFF, using the thermocouple grid described in 7.6. For systems that employ post purge, with a post-purge time period tP, measure the percent volumetric concentration of the tracer gas present in the diluted flue gas sample, CT, at between (5 + tP) and (6 + tP) minutes after the burner is shut off. During the same time period, for units where draft is not maintained, measure the flue gas temperature, TF,OFF, using the thermocouple grid described in 7.6.
Measurements | Value | Unit | Variable
Flue gas tempearture when sampled |  | °F | TF,OFF
Appendix N, Section 8.9: Calculation options. The rate of the flue gas mass flow through the furnace and the factors DP, DF, and DS are calculated by the equations in sections 11.6.1, 11.6.2, 11.6.3, 11.6.4, 11.7.1, and 11.7.2 of ASHRAE 103-1993. On units whose design is such that there is no measurable airflow through the combustion chamber and heat exchanger when the burner(s) is (are) off (as determined by the optional test procedure in section 7.10 of this appendix), DF and DP may be set equal to 0.05.
ASHRAE 103-1993, Section 9.7.5: Modulating Units For units with two-stage modulating controls, the optional tracer gas test shall be conducted at both the maximum and the reduced inputs. For units with step modulating controls, the optional tracer gas test shall be conducted at the reduced input only.
End: Optional Tracer Gas Test Procedures for Determining Draft Factors for DP, DF, and DS for Systems Equipped with Power Burners or Direct Vent and Not Equipped with Stack Dampers
ASHRAE 103-1993, Section 9.7.6: Tracer Gas Test Procedures for Determining Off-Cycle Loss Factor K_L for Atmospheric Systems with Integral Draft Diverter or Draft Hood and Equipped with Either an Electro-Mechanical Inlet or Flue Damper That Restricts the Flow Through the Heat Exchanger in the Off-Cycle - NOT REQUIRED FOR THIS TEST
9.7.6.1 The tracer gas chosen for this task should have a density that is less than or approximately equal to the density of air. Use a gas that is of a different chemical species or different concentration from the flue gas to be measured and unreactive with the environment to be encountered. Obtain the concentration of tracer gas present in the flue gas sample (Cr) using an analyzer or instrument that will result in an accuracy of ±2 % in the measured value. Determine the temperature of the tracer gas entering the flowmeter (Tr) and the barometric pressure (PB).
Measurements | With Damper Closed | With Damper Open | Unit | Variable
Percent by volume of measured tracer gas in the flue gas sample |  |  | % (0-100) | CT
Temperature of tracer gas entering the flowmeter |  |  | °F | TT
Barometric Pressure |  |  | in. HG | PB
Density of flue gas at TT |  |  | lb/ft3 | ρF
9.7.6.2 After the completion of the heat-up test in 9.6, tum the burner OFF. On units equipped with integral draft diverters, remove the blocking over the draft diverter and the restriction in the test stack that were installed during the steady-state test in 9.1.4. Do not remove the insulation covering the draft diverter surfaces. On units equipped with a draft hood, cover the 5-ft stack with insulation having an R-value not less than 7 and an outer layer of aluminum foil as described in 8.8.5. In the meantime, sample and feed the ambient air to the tracer gas analyzer and record the background concentration CTB of the tracer gas to be used for the test. (One data point is usually sufficient.)
Measurements | With Damper Closed | With Damper Open | Unit | Variable
Background concentration of the tracer gas |  |  | % (0-100) | CTB
9.7.6.3 Tum the burner ON until steady-state conditions are again achieved as specified in 9 .1.2.1. Turn the burner OFF for a 10-minute cool-down period. Adjust or bypass the electro-mechanical damper (inlet damper or flue damper) so that it remains open during this cool-down period. Within one minute after the unit is shut off to start this cool-down test, begin feeding a tracer gas with a known, certified concentration CTM at a constant flow rate VT into the lower part of the test stack just above the test plane where the stack thermocouple grid is located (see 8.2.1.5.1). Periodically measure the value of VT with an instantaneously reading flowmeter having an accuracy of ±3 % of the quantity measured and maintain that value of tracer gas flow rate at less than 1 % of the airflow rate through the test stack.
Measurements | With Damper Closed | With Damper Open | Unit | Variable
Percent by volume of measureable tracer gas in the standard tracer gas mixture |  |  | % (0-100) | CTM
Flow rate of tracer gas into heat exchanger during the measurement period |  |  | cfm | VT
9.7.6.4 Within one minute after the tracer gas flow is started, connect the tracer gas sampling line to the sampling probe located at a plane inside and 6 in. below the top exit of the test stack. Measure the transport delay time that is equal to the time between the connecting of the sampling line and the initial response of the tracer gas analyzer. Add to this transport time the time required for the analyzer to reach 90% of its steady-state value as specified in the analyzer's operation manual. The sum of these two values is the tracer gas sample delay time needed to match the concentration measurement to the temperature measurement in the off-period loss calculation. Make sure that a well-mixed sample is collected by using a multi-hole sampling probe, as recommended in Appendix D, section B. Return the sample gas (after exiting the gas analyzer) to the top of the test stack downstream of the plane of collection.
9.7.6.5 At five minutes after the unit is shut off to start the cool-down test, measure and record the percent volumetric concentration of tracer gas present in the stack gas sample, CT, at the location specified in 9.7.6.4. At the same time, measure the stack gas temperature, TS,OFF, using the thermocouple grid in the test plane (see 8.2.1.5.1). The data measurement and recording should be done at a time interval, Δt, of five seconds for the next two to three minutes. The exact length of time required for the tracer gas data measurement is equal to the tracer gas sample delay time (see 9.7.6.4) plus one minute. (Even though only one minute of tracer gas data is required for the computation of the off-cycle loss, the longer time is needed to take into account the time delay between the concentration data and the temperature data.) Stop the tracer gas injection and sampling after the required data are measured and recorded. Disconnect the tracer gas sampling line from the sample probe and sample the ambient air to clear the line.
Measurements | With Damper Closed | With Damper Open | Unit | Variable
Stack gas temperature |  |  | °F | TS,OFF
9.7.6.6 At the end of the 10-minute cool-down period, tum on the burner until steady-state conditions are again achieved as specified in 9.1.2.1. Tum the burner OFF for another 10-minute cool-down period. Let the electro-mechanical damper (inlet damper or flue damper) close the way it is designed to. Repeat the test steps of 9.7.6.3 through 9.7.6.5 except that the electro-mechanical damper is to remain closed. Note that the tracer gas feeding rate, VT, may have to be adjusted to a lower rate to keep the sample concentration within the range of the gas analyzer used. 9.7.6.7 The rate of the stack gas flow through the stack, the cycle sensible loss rate, and the loss factor KL are calculated by the equations in 11.8.1.
Measurements | With Damper Closed | With Damper Open | Unit | Variable
Off-Cycle Sensible Loss |  |  | Btu | QS,OFF
End: Tracer Gas Test Procedures for Determining Off-Cycle Loss Factor KL
ASHRAE 103-1993, Section 9.8: Condensing Furnaces and Boilers-Measurement of Condensate Heat Loss Under Cyclic Conditions
For units with modulating controls, the following applies: (a) for step modulating units, the test is conducted at reduced input rate only; (b) for two-stage units, the test is conducted at both maximum and reduced input rates.
9.8.1 Preparation for Test Control devices shall be installed to allow cyclical operation of the unit and return water or airflows as described in 9.2. The test unit shall be leveled prior to the test. Humidity of the room air shall at no time exceed 80%.
9.8.2 Condensate Collection Containers The condensing furnace or boiler shall be tested by the flue loss method in accordance with the provisions for condensing units, as specified in Section 8. The condensate collection containers shall be dried prior to each use and shall be at room ambient temperature prior to a sample collection. Tare weight of the collection container must be measured and recorded prior to each sample collection.
9.8.3 Test Requirements The unit shall be operated in a cyclical manner until flue gas temperatures at the end of each on-cycle are within 5°F of each other for two consecutive cycles. On-cycle and off-cycle times are listed in Table 9. Control of ON or OFF operation actions shall be within ±6 seconds of the scheduled time. Begin three test cycles. Return air temperature for furnaces shall be as specified in 8.5.2. Return water temperature for boilers shall be as specified in 8.4.2.3. Operation of the furnace blower shall conform to the time delay requirements specified in 9.5.1 for cool-down and heat-up tests. Operation of the boiler pump shall conform to the time delay requirements specified in 9.6.1.
9.8.4 Condensate Collection Begin condensate collection at one minute before the on-cycle period of the first test cycle. The container shall be removed one minute before the end of each off-cycle period. Condensate mass shall be measured for each test cycle.
9.8.5 Measurements Fuel input shall be recorded during the entire test period starting at the beginning of the on-time period of the first cycle to the beginning of the ontime period of the second cycle, etc., for each of the test cycles. Fuel higher heating value (HHV), temperature, and pressures necessary for determining fuel energy input (QC) shall be recorded. Determine the mass of condensate for each cycle (MC) in pounds. If at the end of three cycles, the sample standard deviation is within 20% of the mean value for three cycles, use total condensate collected in the three cycles as MC, if not, continue collection for an additional three cycles and use the total condensate collected for the six cycles as MC. Determine the fuel energy input during the three or six test cycles (QC) expressed in Btu.
Measurements | Value | Unit | Variable
Maximum Humidity During Test |  | % (0-100) | -
Humidity Condition Met? |  | - | -
Flue Gas Temperature (Cycle 1) |  | °F | -
Flue Gas Temperature (Cycle 2) |  | °F | -
Flue Gas Temperature Condition Met? |  | - | -
Room Air Temperature |  | °F | -
Fuel Higher Heating Value |  | Btu/lb | HHV
Condensate Mass Condition Met? |  | - | -
Fuel Energy Input |  | Btu | QC
Total Condensate Collected |  | lb | MC
| Fuel Energy Input | Mass of Condensate
Test Cycle | Btu | lb
1
2
3
4, if necessary
5, if necessary
6, if necessary
Appendix N, Section 8.10: Optional test procedures for condensing furnaces and boilers that have no off-period flue losses.
This only needs to be performed once in the Max Test. Results are shown here also for reference.
Measurements | Value | Unit | Variable
Is post purge time <5 seconds? |  | - | -
Was optional tracer gas test performed that indicates no flow through the heat exchanger when the burner is off? | Fill in Tracer Gas Draft Factors table on Test Conditions tab | - | -
If the answer to the two above questions is "Yes" for both, the heat-up and cool-down tests are optional. Were the heat-up and cool-down tests performed? |  | - | -

## Calculations
Title Block
Test Report Template Name: | Consumer Boiler
Version Number: | v1.1 |  |  |  | Back to Instructions tab
Latest Template Revision: | 2019-09-13
Tab Name: | Calculations
File Name: | Consumer Boiler - v1.1.xlsx
Test Completion Date: | 0
Heating Seasonal Efficiency, Steady-State Efficiency, and AFUE
Variable Name | Variable | Equation Section | Electric Furnaces and Boilers | Non-Condensing and Non-Modulating Gas or Oil Furnaces and Boilers | Non-Modulating and Condensing Gas or Oil Furnaces and Boilers | Modulating and Non-Condensing Gas or Oil Furnaces and Boilers |  | Modulating and Condensing Gas or Oil Furnaces or Boilers |  | Units
[6 empty] | Max Input Rate | Reduced Input Rate | Max Input Rate | Reduced Input Rate
Calculations Subsection | - | Unknown | 11.1 | 11.2 | 11.3 | 11.4 | 11.4 | 11.5 | 11.5 | -
Systems Number
System Number | - | 11.2.1 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Ratio of Combustion Air to Stoichiometric Air
Coefficient for Test Fuel | A | 11.2.2 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Coefficient for Test Fuel | B | 11.2.2 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Concentration by Volume of CO2 Present in Dry Flue Gas | XCO2,F | 11.2.2 |  | N/A | N/A | N/A | N/A | N/A | N/A | % (0-100)
Ratio of Combustion Air to Stoichiometric Air | RT,F | 11.2.2 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Ratio of Combustion and Relief Air to Stoichiometric Air
Concentration by Volume of CO2 Present in Dry Stack Gas | XCO2,S | 11.2.3 |  | N/A |  | N/A | N/A |  |  | % (0-100)
Ratio of Combustion and Relief Air to Stoichiometric Air | RT,S | 11.2.3 |  | N/A |  | N/A | N/A |  |  | -
Average Ratio of Stack Gas Mass Flow Rate to Flue Gas Mass Flow Rate
NOT REQUIRED FOR THIS TEST | - | 11.2.4 | [7 empty] | -
Average Ratio of Stack Gas to Flue Gas Mass Flow Rate | S/F | 11.2.4 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Stack Temperature Rise
Measured Room Temperature of Conditioned Space | TRA | 11.2.5 |  | N/A | N/A | N/A | N/A | N/A | N/A | °F
Measured Stack Gas Temperature at Steady State | TS,SS,X | 11.2.5 |  | N/A |  | N/A | N/A |  |  | °F
Stack Gas Temperature Difference | ΔTS,SS | 11.2.5 |  | N/A |  | N/A | N/A |  |  | °F
Measure Flue Gas Temperature at Steady-State | TF,SS | 11.2.5 |  | N/A | N/A | N/A | N/A | N/A | N/A | °F
Flue Gas Temperature Difference | ΔTF,SS | 11.2.5 |  | N/A | N/A | N/A | N/A | N/A | N/A | °F
Average Sensible Heat Loss at Steady-State Operation
Higher Heating Value of the Fuel | HHVA | 11.2.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | Btu/lb
Mass Ratio of Stoichiometric Air to Fuel | A/F | 11.2.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Average Sensible Heat Loss at Steady-State Operation | LS,SS | 11.2.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | % (0-100)
Steady-State Efficiency
Latent Heat Loss | LL,A | 11.2.7 |  | N/A | N/A | N/A | N/A | N/A | N/A | % (0-100)
Mass of Condensate Collected During Steady State Condensate Collection Period | MC,SS | 11.(3 or 5).7.1 |  |  | N/A |  |  | N/A | N/A | lb
Fuel Energy Input During Steady State Condesnate Collection Period | QC,SS | 11.(3 or 5).7.1 |  |  | N/A |  |  | N/A | N/A | Btu
Latent Heat Gain Due to Condensation Under Steady-State Conditions | LG,SS | 11.(3 or 5).7.1 |  |  | N/A |  |  | N/A | N/A | % (0-100)
Steady-State Heat Loss Due to Hot Condensate Going Down the Drain | LC,SS | 11.(3 or 5).7.2 |  |  | N/A |  |  | N/A | N/A | % (0-100)
Steady-State Efficiency | EffySS | 11.2.7 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | % (0-100)
Heat Capacity and Part-Load Constants
Steady-State Nameplate Input Rate | QIN | 11.2.8.1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Btu/h
Jacket Loss | LJ | 11.2.8.1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | %
Jacket Loss Installation Adjustment Factor | K | 11.2.8.1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -
Maximum Fuel Input Rate Heating Capacity | QOUT | 11.2.8.1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Btu/h
Design Heating Requirement | DHR | 11.2.8.2 | N/A | N/A | N/A | N/A |  |  |  | Btu/h
Oversize Factor | α | 11.2.8.3 |  | N/A | N/A | N/A |  | N/A |  | -
Average Outdoor Temperature | TOA | 11.2.8.4 |  | N/A | N/A | N/A | N/A |  |  | °F
Balance-Point Temperature | TC | 11.2.8.5 |  |  |  | N/A |  | N/A |  | °F
Fraction of Heating Load at Maximun Fuel Input Rate Operating Mode | XH | 11.2.8.6 |  |  |  | N/A |  | N/A |  | -
Fraction of Heating Load at Reduced Fuel Input Rate Operating Mode | XR | 11.2.8.7 |  |  |  |  | N/A |  | N/A | -
Average Steady-State Efficiency for the Modulating Mode for Furnaces and Boilers Equipped with Step Modulating Controls | EffySS,M | 11.2.8.8 |  |  |  | N/A |  | N/A |  | % (0-100)
Weighted-Average Steady-State Efficiency | EffySS,W | 11.2.8.9 |  |  |  | N/A |  | N/A |  | % (0-100)
Average Heat Output Rate for the Modulating Mode for Furnaces and Boilers Equipped with Step Modulating Controls | QOUT,M | 11.2.8.10 |  |  |  | N/A |  | N/A |  | Btu/h
Calculatiom Not Affected by Outside Air
Specific Heat of Air | CP | 11.2.9.1 |  | N/A | N/A | N/A | N/A | N/A | N/A | Btu/(lb °F)
Multiplication Factor for Sensible Heat Loss During Burner On-Cycle | KS,ON | 11.2.9.1 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Infiltration Parameter | φ | 11.2.9.2 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Multiplication Factor for Infiltration Loss During Burner On-Cycle | KI,ON | 11.2.9.2 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Average On-Cycle Infiltration Heat Loss for the Modulating Mode for Furnaces and Boilers Equipped with Step Modulating Controls | LI,ON,M | 11.(4 or 5).9.2.2 |  |  |  | N/A |  | N/A |  | % (0-100)
Average Part-Load Efficiency for the Modulating Mode for Furnaces and Boilers Equipped with Step Modulating Controls | EffyU,M | 11.(4 or 5).9.2.3 |  |  |  | N/A |  | N/A |  | % (0-100)
Equivalent Field Stade Gas Temperature at Full-Load Steady-State Operation | TS,SS | 11.2.9.3 |  | N/A |  | N/A | N/A |  |  | °F
| t1 | 11.2.9.4 |  | N/A | N/A | N/A | N/A | N/A | N/A | min
| t2 | 11.2.9.4 |  | N/A | N/A | N/A | N/A | N/A | N/A | min
Flue Gas Temperature Measured at Time t1 | TF,ON(t1) | 11.2.9.4 |  | N/A | N/A | N/A | N/A | N/A | N/A | °F
Flue Gas Temperature Measured at Time t2 | TF,ON(t2) | 11.2.9.4 |  | N/A | N/A | N/A | N/A | N/A | N/A | °F
On-Cycle Time Constant | τON | 11.2.9.4 |  | N/A | N/A | N/A | N/A | N/A | N/A | min
Effective Flue Gas Temperature Difference at Start-up | θF,O,X | 11.2.9.5 |  | N/A | N/A | N/A | N/A | N/A | N/A | min
| t3 | 11.2.9.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | min
| t4 | 11.2.9.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | min
| t5 | 11.2.9.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | min
Post-Purge Period | tp | 11.2.9.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | min
Flue Gas Temperature Measured at Time t3 | TF,OFF(t3) | 11.2.9.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | °F
Flue Gas Temperature Measured at Time t4 | TF,OFF(t4) | 11.2.9.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | °F
Flue Gas Temperature Measured at Time t5 | TF,OFF(t5) | 11.2.9.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | °F
Off-Cycle Time Constant | τOFF | 11.2.9.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | min
Effective Flue Gas Temperature Difference at Shutdown | ψF,O,X | 11.2.9.7 |  | N/A | N/A | N/A | N/A | N/A | N/A | °F
Minimum Flue Gas Temperature Difference above Room Temperature | ψF,∞,X | 11.2.9.8 |  | N/A | N/A | N/A | N/A | N/A | N/A | °F
Power Burner Draft Factor - USED | DP | 11.2.9.9 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Off-Cycle Flue Gas Draft Factor - USED | DF | 11.2.9.9 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Off-Cycle Stack Gas Draft Factor | DSO | 11.2.9.9 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Minimun Stack Gas Temperature Difference above Room Temperature | ψS,∞,X | 11.2.9.9 |  | N/A | N/A | N/A | N/A | N/A | N/A | °F
Effective Stack Gas Temperature Difference at Shutdown | ψS,O,X | 11.2.9.10 |  | N/A |  | N/A | N/A |  |  | °F
Average Burner On-Time Per Cycle | tON | 11.2.9.11 |  | N/A | N/A | N/A | N/A | N/A | N/A | min
Ratio of Average Burner On-Time Per Cycle to On-Cycle Time Constant | RON | 11.2.9.11 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Average Burner Off-Time Per Cycle | tOFF | 11.2.9.12 |  | N/A | N/A | N/A | N/A | N/A | N/A | min
Ratio of Average Burner Off-Time Per Cycle to Off-Cycle Time Constant | ROFF | 11.2.9.12 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Start-up Burner Cycling Effect Correction Factor | CT,ON | 11.2.9.13 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Correction Factor for Units using Intermittent or Interrupted Ignition Devices | CIID | 11.2.9.14 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Shutdown Burner Cycling Effect Correction Factor | CT,OFF | 11.2.9.14 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Off-Period Correction Factor for Outdoor Units, Units Intended for Installation in Unheated Spaces, or Direct Vent Units | C'S | 11.2.9.15 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Effective Flue Gas Temperature Difference at Burner Shutdown, Corrected for Burner Cycling Effect | ψF,O | 11.2.9.15 |  | N/A | N/A | N/A | N/A | N/A | N/A | °F
Effective Minimun Flue Gas Temperature Difference above Room Temperature, Corrected for Burner Cycling Effect | ψF,∞ | 11.2.9.16 |  | N/A | N/A | N/A | N/A | N/A | N/A | °F
Effective Stack Gas Temperature Difference at Burner Shutdown, Corrected for Burner Cycling Effect | ψS,O | 11.2.9.17 |  | N/A |  | N/A | N/A |  |  | °F
Stack Damper Effectiveness Factor | DO | 11.2.9.18 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Infiltration Correction Factor for Stack Damper Effectiveness | DOI | 11.2.9.18 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Off-Cycle Stack Gas Draft Factor | DS | 11.2.9.18 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Off-Cycle Stack Gas Draft Factor - USED | DS | 11.2.9.18 or 11.7.2 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Off-Cycle Sensible Heat Loss Integration Factors | F3 | 11.2.9.19 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Off-Cycle Sensible Heat Loss Integration Factors | F4 | 11.2.9.19 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Off-Cycle Sensible Heat Loss Integration Factors | F5 | 11.2.9.19 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Off-Cycle Sensible Heat Loss Integration Factors | F6 | 11.2.9.19 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Off-Cycle Infiltration Heat Loss Integration Factors | F7 | 11.2.9.20 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Off-Cycle Infiltration Heat Loss Integration Factors | F8 | 11.2.9.20 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Calculations Affected by Outside Air
Correction Factor That Corrects for the Use of Outside Air for Combustion | CS | 11.2.10.1 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Effective Flue Gas Temperature Difference at Burner Start-Up, Corrected for Burner Cycling Effect | θF,O | 11.2.10.2 |  | N/A | N/A | N/A | N/A | N/A | N/A | °F
Multiplication Factor for Sensible Heat Loss During Burner Off-Cycle | KS,OFF | 11.2.10.3 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Multiplication Factor for Infiltration Loss During Burner Off-Cycle | KI,OFF | 11.2.10.4 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
On-Cycle Sensible Heat Loss | LS,ON | 11.2.10.5 |  | N/A | N/A | N/A | N/A | N/A | N/A | % (0-100)
Does the boiler employ a post-purge? | - | 11.2.10.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Corrected Shutdown Burner Cycling Effect Correction Factor (Variable is not actually named in ANSI/ASHRAE) | CTS | 11.2.10.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Flue Gas Temperature Measured at Time tP | TF,OFF(tP) | 11.2.10.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | °F
Off-Cycle Sensible Heat Loss During the Post-Purge Period | LS,OFF1 | 11.2.10.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | % (0-100)
Off-Cycle Sensible Heat Loss After the Post-Purge Period | LS,OFF2 | 11.2.10.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | % (0-100)
Off-Cycle Sensible Heat Loss | LS,OFF | 11.2.10.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | % (0-100)
On-Cycle Infiltration Heat Loss | LI,ON | 11.2.10.7 |  | N/A | N/A | N/A | N/A | N/A | N/A | % (0-100)
Off-Cycle Infiltration Heat Loss During the Post-Purge Period | LI,OFF1 | 11.2.10.8 |  | N/A | N/A | N/A | N/A | N/A | N/A | % (0-100)
Off-Cycle Infiltration Heat Loss After the Post-Purge Period | LI,OFF2 | 11.2.10.8 |  | N/A | N/A | N/A | N/A | N/A | N/A | % (0-100)
Off-Cycle Infiltration Heat Loss | LI,OFF | 11.2.10.8 |  | N/A | N/A | N/A | N/A | N/A | N/A | % (0-100)
Heating Seasonal Efficiency
Jacket Loss Factor | CJ | 11.2.11 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Pilot Flame Fuel Input Rate | QP | 11.2.11 |  | N/A | N/A | N/A | N/A | N/A | N/A | Btu/h
Mass of Condensate | MC | 11.3.11.1 |  |  | N/A |  |  |  |  | lb
Fuel Energy Input During Entire (3 or 6 test cycles) Cyclic Condensate Collection Test | QC | 11.3.11.1 |  |  | N/A |  |  |  |  | Btu
Latent Heat Gain Under Part-Load Conditions | LG | 11.3.11.1 |  |  | N/A |  |  |  |  | % (0-100)
Part-Load Heat Loss Due to Condensate Going Down the Drain | LC | 11.3.11.2 |  |  | N/A |  |  |  |  | % (0-100)
Part-Load Efficiency at Reduced Fuel Input Rate | EffyU,R | 11.(4 or 5).11.1 |  |  |  |  | N/A |  | N/A | % (0-100)
Part-Load Efficiency at Maximum Fuel Input Rate | EffyU,H | 11.(4 or 5).11.2 |  |  |  | N/A |  | N/A |  | % (0-100)
Heating Seasonal Efficiency | EffyHS | 11.2.11 | N/A | N/A | N/A | N/A |  | N/A |  | % (0-100)
Annual Fuel Utilization Efficiency
Average Annual Heating Degree-Days | - | 11.2.12 |  | N/A | N/A | N/A |  | N/A |  | °F-days
Average Non-Heating-Season Hours per Year | - | 11.2.12 | N/A | N/A | N/A | N/A |  | N/A |  | h/yr
Heating Degree-Days per Day at 65°F – 5°F divided by 24 h/day | - | 11.2.12 |  | N/A | N/A | N/A |  | N/A |  | °F
Annual Fuel Utilization Efficiency | AFUE | 11.2.12 | N/A | N/A | N/A | N/A |  | N/A |  | % (0-100)
Calculated Result (rounded per significant figures conventions and instrumentation resolution) | AFUE | 11.2.12 | [7 empty] | % (0-100)
Optional Tracer Gas Procedure for Determination of DP for Furnaces or Boilers Employing a Power Burner or Direct Vent
On-Period Mass Flow Rate | MF,ON | 11.6.1 |  | N/A | N/A | N/A | N/A | N/A | N/A | lb/min
Flow rate of tracer gas into heat exchanger during the measurement period | VT | 11.6.2 |  | N/A | N/A | N/A | N/A | N/A | N/A | cfm
Percent by volume of measured tracer gas in the flue gas sample | CT | 11.6.2 |  | N/A | N/A | N/A | N/A | N/A | N/A | % (0-100)
Percent by volume of measureable tracer gas in the standard tracer gas mixture | CTM | 11.6.2 |  | N/A | N/A | N/A | N/A | N/A | N/A | % (0-100)
Density of flue gas at TT | ρF | 11.6.2 |  | N/A | N/A | N/A | N/A | N/A | N/A | lb/ft3
Measured Mass Flow Rate | MF,M | 11.6.2 |  | N/A | N/A | N/A | N/A | N/A | N/A | lb/min
Was a draft maintained during the steady-state or cool-down tests? | - | 11.6.3 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Temperature of the Flue Gas When Sampled | TF,OFF | 11.6.3 |  | N/A | N/A | N/A | N/A | N/A | N/A | °F
Off-Period Mass Flow Rate | MF,OFF | 11.6.3 |  | N/A | N/A | N/A | N/A | N/A | N/A | lb/min
Optionally Determined Power Burner Draft Factor | DP | 11.6.4 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Optional Procedure for Determining Off-Cycle Draft Factors for Furnaces or Boilers Employing a Power Burner or Direct Vent
Optionally Determined Off-Cycle Flue Gas Draft Factor | DF | 11.7.1 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Optionally Determined Off-Cycle Stack Gas Draft Factor | DS | 11.7.2 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Procedure for Determining Off-Cycle Loss Factor and Off-Cycle Draft Factor for Atmospheric Furnaces or Boilers with Integral Draft Diverter or Draft Hood and Equipped with an Electro-Mechanical Inlet or Flue Damper That Restricts the Flow Through the Heat Exchanger During the Off-Cycle
With Damper Closed | QS,OFF | 11.8.1 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
With Damper Open | QS,OFF | 11.8.1 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Off-Cycle Loss Factor | KL | 11.8.1 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
Optionally Determined Power Burner Draft Factor | DP | 11.8.2 |  | N/A | N/A | N/A | N/A | N/A | N/A | -
National Average Number of Burner Operating Hours
Electrical Power to Burner | PE | DOE 10.4.1 |  | N/A | N/A | N/A | N/A | N/A | N/A | kW
Electrical Power to Circulating Air Blower or Water Pump | BE | DOE 10.4.1 |  | N/A | N/A | N/A | N/A | N/A | N/A | kW
Ratio of Power Burner Combustion Blower On-Time to Average Burner On-Time | yp | DOE 10.4.1 |  | N/A | N/A | N/A |  | N/A |  | -
Electrical Power to the Interrupted Ignition Device | PEIG | DOE 10.4.1 |  | N/A | N/A | N/A |  | N/A |  | kW
Electrical Interrupted Ignition Device On-Time | tIG | DOE 10.4.1 |  | N/A | N/A | N/A |  | N/A |  | min
Ratio of Electrical Interrupted Ignition Device On-Time to Average Burner On-Time | yIG | DOE 10.4.1 |  | N/A | N/A | N/A |  | N/A |  | -
Does the boiler have a pump delay? | - | DOE 10.4.1 |  | N/A | N/A | N/A |  | N/A |  | -
Time Delay Between Burner Shut-Off and Pump Shut-Off | t+ | DOE 10.4.1 |  | N/A | N/A | N/A |  | N/A |  | min
Ratio of Blower or Pump On-Time to Average Burner On-Time | y | DOE 10.4.1 |  | N/A | N/A | N/A |  | N/A |  | -
Nameplate Power Burner Motor Efficiency | Effmotor | DOE 10.4.1 |  | N/A | N/A | N/A |  | N/A |  | % (0-100)
| A | DOE 10.4.1 |  | N/A | N/A | N/A |  | N/A |  | -
| B | DOE 10.4.1 |  | N/A | N/A | N/A |  | N/A |  | -
National Average Heating Load Hours | - | DOE 10.4.1 | N/A | N/A | N/A | N/A |  | N/A |  | h
Adjusts the calculated DHR and heating load hours to the actual heating load experienced by the heating system | - | DOE 10.4.1 | N/A | N/A | N/A | N/A |  | N/A |  | -
| R | DOE 10.4.1.1 |  | N/A | N/A | N/A |  | N/A |  | -
National Average Number of Burner Operating Hours | BOHSS | DOE 10.4.1 |  | N/A | N/A | N/A |  | N/A |  | h
Total Number of Hours Per Year | - | DOE 10.4.1.1 |  | N/A | N/A | N/A |  | N/A |  | h/yr
Average Annual Energy Used During the Heating Season | EM | DOE 10.4.1.1 |  | N/A | N/A | N/A |  | N/A |  | Btu
National Average Number of Burner Operating Hours at the Reduced and Maximum Operating Modes | BOH(R,H) | DOE 10.4.1.(2,3) |  | N/A | N/A | N/A | N/A | N/A | N/A | h
Average Heat Input Rate for the Modulating Mode for Furnaces and Boilers Equipped with Step Modulating Controls | QIN,M | DOE 10.4.1.4 |  | N/A | N/A | N/A |  | N/A |  | Btu/h
National Average Number of Burner Operating Hours at the Maximum Operating Mode | BOHM | DOE 10.4.1.4 |  | N/A | N/A | N/A |  | N/A |  | h
Average Annual Fuel Energy Consumption for Gas or Oil Fueled Furnaces or Boilers
Average Annual Fuel Energy Consumption | EF | DOE 10.4.2 |  | N/A | N/A | N/A |  | N/A |  | Btu/yr
Average Annual Auxiliary Electrical Energy Consumption for Gas or Oil-Fueled Furnaces or Boilers
Average Annual Auxiliary Electrical Energy Consumption | EAE | DOE 10.4.3 |  | N/A | N/A | N/A |  | N/A |  | kWh
Average Annual Electric Energy Consumption for Electric Furnaces or Boilers
Average Annual Electric Energy Consumption | EE | DOE 10.5 | N/A | [6 empty] | kWh
Energy Factor
Energy Factor | EF | DOE 10.6.1 | N/A | N/A | N/A | N/A |  | N/A |  | % (0-100)
Average Annual Energy Consumption for Furnaces and Boilers Located in a Different Geographic Region of the United States and in Buildings with Different Design Heating Requirements
Heating Load Hours for a Specific Geographic Region Determined from the Heating Load Hour Map in Figure 1 of the DOE Test Procedure | HLH | DOE 10.7.1 | [7 empty] | heating load hours
Average Annual Fuel Energy Consumption for Units Located in a Different Geographic Region of the United States and in Buildings with Different DHRs. | EFR | DOE 10.7.1 |  | N/A | N/A | N/A |  | N/A |  | Btu/yr
Regional Average Annual Electrical Standby Mode and Off Mode Energy Consumption | ESOR | DOE 10.12 | N/A | N/A | N/A | N/A |  | N/A |  | kWh
Average Annual Auxiliary Electrical Energy Consumption for Units Located in a Different Geographic Region of the United States and in Buildings with Different DHRs. | EAER | DOE 10.7.2 |  | N/A | N/A | N/A |  | N/A |  | kWh
Average Annual Electric Energy Consumption for Units Located in a Different Geographic Region of the United States and in Buildings with Different DHRs. | EER | DOE 10.7.3 | N/A | [6 empty] | kWh
Annual Energy Consumption for Mobile Home Furnaces
Not applicable to this test report template | - | DOE 10.8 | [7 empty] | -
Calculation of Sales Weighted Average Annual Energy Consumption for Mobile Home Furnaces
Not applicable to this test report template | - | DOE 10.9 | [7 empty] | -
Direct Determination of Off-Cycle Losses for Furnaces and Boilers Equipped with Thermal Stack Dampers
[Reserved.] | - | DOE 10.10 | [7 empty] | -
Average Annual Electrical Standby Mode and Off Mode Energy Consumption
Standby Mode Power | PW,SB | DOE 10.11 | N/A | N/A | N/A | N/A |  | N/A |  | W
Off Mode Power | PW,OFF | DOE 10.11 | N/A | N/A | N/A | N/A |  | N/A |  | W
| EIN | DOE 10.11 | N/A | [6 empty] | kW
Total Burner Operating Hours | BOH | DOE 10.11 | N/A | N/A | N/A | N/A |  | N/A |  | h
Average Heating Season Hours per Year | - | DOE 10.11 | N/A | N/A | N/A | N/A |  | N/A |  | h/yr
Conversion Factor from Wh to kWh | K | DOE 10.11 | N/A | N/A | N/A | N/A |  | N/A |  | kWh/Wh
Average Annual Electrical Standby Mode and Off Mode Energy Consumption | ESO | DOE 10.11 | N/A | N/A | N/A | N/A |  | N/A |  | kWh
For use in ANSI/ASHRAE Section Unknown.9.18: Off-Cycle Stack Gas Draft Factor
| Value | Units | Variable | Variable Name
| #N/A | - | - | System Number
| 0 | min | ts | Time When Damper Starts to Close
|  | min | te | Time When Damper Finishes Closing
| #N/A | min | tOFF | Average Burner Off-Time Per Cycle
| #N/A | min | τOFF | Off-Cycle Time Constant
| 100 | - | n | Number of Segments between t/tOFF = 0 to t/tOFF = 1.0
| 0.01 | - | hj | Dimensionless Time Increment Given by 1/n
| #N/A | °F | ψS,∞,X | Minimun Stack Gas Temperature Difference above Room Temperature
| #N/A | °F | ψS,O | Effective Stack Gas Temperature Difference at Burner Shutdown, Corrected for Burner Cycling Effect
| #N/A | °F | ψF,∞ | Effective Minimun Flue Gas Temperature Difference above Room Temperature, Corrected for Burner Cycling Effect
| #N/A | °F | ψF,O | Effective Flue Gas Temperature Difference at Burner Shutdown, Corrected for Burner Cycling Effect
| 0 | in2 | AS | Cross-Sectional Area of the Stack
| 0 | in2 | AD | Net Area of a Stack Damper Plate
| 0 | Radians | Ω | Angle the Damper Makes, When Closed, With a Plane Perpendicular to the Axis of the Stack
|  | min | DE
| #N/A | - | DF | Off-Cycle Flue Gas Draft Factor
| #N/A | - | DSO | Off-Cycle Stack Gas Draft Factor
| #N/A | - | S/F | Average Ratio of Stack Gas to Flue Gas Mass Flow Rate
| #VALUE! | - | DO | Stack Damper Effectiveness Factor
| #VALUE! | - | DOI | Infiltration Correction Factor for Stack Damper Effectiveness
| j | t | G1 | G2 | G3 | G4 | G1j | G2j | G3j | G4j | DS,j | ψS,∞,j | ψS,O,j
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
ANSI/ASHRAE Sections Unknown.9.19 and Unknown.9.20: Off-Cycle Sensible and Infiltration Heat Loss Integration Factors
This calculation uses the Simpson's Rule to approximate the integrals located in Appendix E of the ANSI/ASHRAE test procedure.
| Max Input Rate | Reduced Input Rate | Units | Variable | Variable Name
| #N/A | #N/A | - | - | System Number
| #N/A | #N/A | - | - | Does the boiler employ a post-purge?
| #N/A | #N/A | min | tp | Post-Purge Period
| #N/A | #N/A | min | tOFF | Average Burner Off-Time Per Cycle
| #N/A | #N/A | min | τOFF | Off-Cycle Time Constant
| #N/A | #N/A | - | ROFF | Ratio of Average Burner Off-Time Per Cycle to Off-Cycle Time Constant
| #N/A | #N/A | - | ROFF,Modified | Modified Ratio of Average Burner Off-Time Per Cycle to Off-Cycle Time Constant
| #N/A | #N/A | °F | ψF,O | Effective Flue Gas Temperature Difference at Burner Shutdown, Corrected for Burner Cycling Effect
| #N/A | #N/A | °F | ψS,O | Effective Stack Gas Temperature Difference at Burner Shutdown, Corrected for Burner Cycling Effect
| 1000 | 1000 | - | - | Total Number of Time Steps
| #N/A | #N/A | - | Δt | Time Step
Max Input Rate
| ROFF Used | ψ Used | f(0) | f(1000) | Integration Factor
| #N/A | #N/A | #N/A | #N/A | #N/A | F3
| #N/A | #N/A | #N/A | #N/A | #N/A | F4
| #N/A | #N/A | #N/A | #N/A | #N/A | F5
| #N/A | #N/A | #N/A | #N/A | #N/A | F6
| #N/A | #N/A | #N/A | #N/A | #N/A | F7
| #N/A | #N/A | #N/A | #N/A | #N/A | F8
Reduced Input Rate
| ROFF Used | ψ Used | f(0) | f(1000) | Integration Factor
| #N/A | #N/A | #N/A | #N/A | #N/A | F3
| #N/A | #N/A | #N/A | #N/A | #N/A | F4
| #N/A | #N/A | #N/A | #N/A | #N/A | F5
| #N/A | #N/A | #N/A | #N/A | #N/A | F6
| #N/A | #N/A | #N/A | #N/A | #N/A | F7
| #N/A | #N/A | #N/A | #N/A | #N/A | F8
| Time Step | t/τoff
| 0 | #N/A
| 1 | #N/A
| 2 | #N/A
| 3 | #N/A
| 4 | #N/A
| 5 | #N/A
| 6 | #N/A
| 7 | #N/A
| 8 | #N/A
| 9 | #N/A
| 10 | #N/A
| 11 | #N/A
| 12 | #N/A
| 13 | #N/A
| 14 | #N/A
| 15 | #N/A
| 16 | #N/A
| 17 | #N/A
| 18 | #N/A
| 19 | #N/A
| 20 | #N/A
| 21 | #N/A
| 22 | #N/A
| 23 | #N/A
| 24 | #N/A
| 25 | #N/A
| 26 | #N/A
| 27 | #N/A
| 28 | #N/A
| 29 | #N/A
| 30 | #N/A
| 31 | #N/A
| 32 | #N/A
| 33 | #N/A
| 34 | #N/A
| 35 | #N/A
| 36 | #N/A
| 37 | #N/A
| 38 | #N/A
| 39 | #N/A
| 40 | #N/A
| 41 | #N/A
| 42 | #N/A
| 43 | #N/A
| 44 | #N/A
| 45 | #N/A
| 46 | #N/A
| 47 | #N/A
| 48 | #N/A
| 49 | #N/A
| 50 | #N/A
| 51 | #N/A
| 52 | #N/A
| 53 | #N/A
| 54 | #N/A
| 55 | #N/A
| 56 | #N/A
| 57 | #N/A
| 58 | #N/A
| 59 | #N/A
| 60 | #N/A
| 61 | #N/A
| 62 | #N/A
| 63 | #N/A
| 64 | #N/A
| 65 | #N/A
| 66 | #N/A
| 67 | #N/A
| 68 | #N/A
| 69 | #N/A
| 70 | #N/A
| 71 | #N/A
| 72 | #N/A
| 73 | #N/A
| 74 | #N/A
| 75 | #N/A
| 76 | #N/A
| 77 | #N/A
| 78 | #N/A
| 79 | #N/A
| 80 | #N/A
| 81 | #N/A
| 82 | #N/A
| 83 | #N/A
| 84 | #N/A
| 85 | #N/A
| 86 | #N/A
| 87 | #N/A
| 88 | #N/A
| 89 | #N/A
| 90 | #N/A
| 91 | #N/A
| 92 | #N/A
| 93 | #N/A
| 94 | #N/A
| 95 | #N/A
| 96 | #N/A
| 97 | #N/A
| 98 | #N/A
| 99 | #N/A
| 100 | #N/A
| 101 | #N/A
| 102 | #N/A
| 103 | #N/A
| 104 | #N/A
| 105 | #N/A
| 106 | #N/A
| 107 | #N/A
| 108 | #N/A
| 109 | #N/A
| 110 | #N/A
| 111 | #N/A
| 112 | #N/A
| 113 | #N/A
| 114 | #N/A
| 115 | #N/A
| 116 | #N/A
| 117 | #N/A
| 118 | #N/A
| 119 | #N/A
| 120 | #N/A
| 121 | #N/A
| 122 | #N/A
| 123 | #N/A
| 124 | #N/A
| 125 | #N/A
| 126 | #N/A
| 127 | #N/A
| 128 | #N/A
| 129 | #N/A
| 130 | #N/A
| 131 | #N/A
| 132 | #N/A
| 133 | #N/A
| 134 | #N/A
| 135 | #N/A
| 136 | #N/A
| 137 | #N/A
| 138 | #N/A
| 139 | #N/A
| 140 | #N/A
| 141 | #N/A
| 142 | #N/A
| 143 | #N/A
| 144 | #N/A
| 145 | #N/A
| 146 | #N/A
| 147 | #N/A
| 148 | #N/A
| 149 | #N/A
| 150 | #N/A
| 151 | #N/A
| 152 | #N/A
| 153 | #N/A
| 154 | #N/A
| 155 | #N/A
| 156 | #N/A
| 157 | #N/A
| 158 | #N/A
| 159 | #N/A
| 160 | #N/A
| 161 | #N/A
| 162 | #N/A
| 163 | #N/A
| 164 | #N/A
| 165 | #N/A
| 166 | #N/A
| 167 | #N/A
| 168 | #N/A
| 169 | #N/A
| 170 | #N/A
| 171 | #N/A
| 172 | #N/A
| 173 | #N/A
| 174 | #N/A
| 175 | #N/A
| 176 | #N/A
| 177 | #N/A
| 178 | #N/A
| 179 | #N/A
| 180 | #N/A
| 181 | #N/A
| 182 | #N/A
| 183 | #N/A
| 184 | #N/A
| 185 | #N/A
| 186 | #N/A
| 187 | #N/A
| 188 | #N/A
| 189 | #N/A
| 190 | #N/A
| 191 | #N/A
| 192 | #N/A
| 193 | #N/A
| 194 | #N/A
| 195 | #N/A
| 196 | #N/A
| 197 | #N/A
| 198 | #N/A
| 199 | #N/A
| 200 | #N/A
| 201 | #N/A
| 202 | #N/A
| 203 | #N/A
| 204 | #N/A
| 205 | #N/A
| 206 | #N/A
| 207 | #N/A
| 208 | #N/A
| 209 | #N/A
| 210 | #N/A
| 211 | #N/A
| 212 | #N/A
| 213 | #N/A
| 214 | #N/A
| 215 | #N/A
| 216 | #N/A
| 217 | #N/A
| 218 | #N/A
| 219 | #N/A
| 220 | #N/A
| 221 | #N/A
| 222 | #N/A
| 223 | #N/A
| 224 | #N/A
| 225 | #N/A
| 226 | #N/A
| 227 | #N/A
| 228 | #N/A
| 229 | #N/A
| 230 | #N/A
| 231 | #N/A
| 232 | #N/A
| 233 | #N/A
| 234 | #N/A
| 235 | #N/A
| 236 | #N/A
| 237 | #N/A
| 238 | #N/A
| 239 | #N/A
| 240 | #N/A
| 241 | #N/A
| 242 | #N/A
| 243 | #N/A
| 244 | #N/A
| 245 | #N/A
| 246 | #N/A
| 247 | #N/A
| 248 | #N/A
| 249 | #N/A
| 250 | #N/A
| 251 | #N/A
| 252 | #N/A
| 253 | #N/A
| 254 | #N/A
| 255 | #N/A
| 256 | #N/A
| 257 | #N/A
| 258 | #N/A
| 259 | #N/A
| 260 | #N/A
| 261 | #N/A
| 262 | #N/A
| 263 | #N/A
| 264 | #N/A
| 265 | #N/A
| 266 | #N/A
| 267 | #N/A
| 268 | #N/A
| 269 | #N/A
| 270 | #N/A
| 271 | #N/A
| 272 | #N/A
| 273 | #N/A
| 274 | #N/A
| 275 | #N/A
| 276 | #N/A
| 277 | #N/A
| 278 | #N/A
| 279 | #N/A
| 280 | #N/A
| 281 | #N/A
| 282 | #N/A
| 283 | #N/A
| 284 | #N/A
| 285 | #N/A
| 286 | #N/A
| 287 | #N/A
| 288 | #N/A
| 289 | #N/A
| 290 | #N/A
| 291 | #N/A
| 292 | #N/A
| 293 | #N/A
| 294 | #N/A
| 295 | #N/A
| 296 | #N/A
| 297 | #N/A
| 298 | #N/A
| 299 | #N/A
| 300 | #N/A
| 301 | #N/A
| 302 | #N/A
| 303 | #N/A
| 304 | #N/A
| 305 | #N/A
| 306 | #N/A
| 307 | #N/A
| 308 | #N/A
| 309 | #N/A
| 310 | #N/A
| 311 | #N/A
| 312 | #N/A
| 313 | #N/A
| 314 | #N/A
| 315 | #N/A
| 316 | #N/A
| 317 | #N/A
| 318 | #N/A
| 319 | #N/A
| 320 | #N/A
| 321 | #N/A
| 322 | #N/A
| 323 | #N/A
| 324 | #N/A
| 325 | #N/A
| 326 | #N/A
| 327 | #N/A
| 328 | #N/A
| 329 | #N/A
| 330 | #N/A
| 331 | #N/A
| 332 | #N/A
| 333 | #N/A
| 334 | #N/A
| 335 | #N/A
| 336 | #N/A
| 337 | #N/A
| 338 | #N/A
| 339 | #N/A
| 340 | #N/A
| 341 | #N/A
| 342 | #N/A
| 343 | #N/A
| 344 | #N/A
| 345 | #N/A
| 346 | #N/A
| 347 | #N/A
| 348 | #N/A
| 349 | #N/A
| 350 | #N/A
| 351 | #N/A
| 352 | #N/A
| 353 | #N/A
| 354 | #N/A
| 355 | #N/A
| 356 | #N/A
| 357 | #N/A
| 358 | #N/A
| 359 | #N/A
| 360 | #N/A
| 361 | #N/A
| 362 | #N/A
| 363 | #N/A
| 364 | #N/A
| 365 | #N/A
| 366 | #N/A
| 367 | #N/A
| 368 | #N/A
| 369 | #N/A
| 370 | #N/A
| 371 | #N/A
| 372 | #N/A
| 373 | #N/A
| 374 | #N/A
| 375 | #N/A
| 376 | #N/A
| 377 | #N/A
| 378 | #N/A
| 379 | #N/A
| 380 | #N/A
| 381 | #N/A
| 382 | #N/A
| 383 | #N/A
| 384 | #N/A
| 385 | #N/A
| 386 | #N/A
| 387 | #N/A
| 388 | #N/A
| 389 | #N/A
| 390 | #N/A
| 391 | #N/A
| 392 | #N/A
| 393 | #N/A
| 394 | #N/A
| 395 | #N/A
| 396 | #N/A
| 397 | #N/A
| 398 | #N/A
| 399 | #N/A
| 400 | #N/A
| 401 | #N/A
| 402 | #N/A
| 403 | #N/A
| 404 | #N/A
| 405 | #N/A
| 406 | #N/A
| 407 | #N/A
| 408 | #N/A
| 409 | #N/A
| 410 | #N/A
| 411 | #N/A
| 412 | #N/A
| 413 | #N/A
| 414 | #N/A
| 415 | #N/A
| 416 | #N/A
| 417 | #N/A
| 418 | #N/A
| 419 | #N/A
| 420 | #N/A
| 421 | #N/A
| 422 | #N/A
| 423 | #N/A
| 424 | #N/A
| 425 | #N/A
| 426 | #N/A
| 427 | #N/A
| 428 | #N/A
| 429 | #N/A
| 430 | #N/A
| 431 | #N/A
| 432 | #N/A
| 433 | #N/A
| 434 | #N/A
| 435 | #N/A
| 436 | #N/A
| 437 | #N/A
| 438 | #N/A
| 439 | #N/A
| 440 | #N/A
| 441 | #N/A
| 442 | #N/A
| 443 | #N/A
| 444 | #N/A
| 445 | #N/A
| 446 | #N/A
| 447 | #N/A
| 448 | #N/A
| 449 | #N/A
| 450 | #N/A
| 451 | #N/A
| 452 | #N/A
| 453 | #N/A
| 454 | #N/A
| 455 | #N/A
| 456 | #N/A
| 457 | #N/A
| 458 | #N/A
| 459 | #N/A
| 460 | #N/A
| 461 | #N/A
| 462 | #N/A
| 463 | #N/A
| 464 | #N/A
| 465 | #N/A
| 466 | #N/A
| 467 | #N/A
| 468 | #N/A
| 469 | #N/A
| 470 | #N/A
| 471 | #N/A
| 472 | #N/A
| 473 | #N/A
| 474 | #N/A
| 475 | #N/A
| 476 | #N/A
| 477 | #N/A
| 478 | #N/A
| 479 | #N/A
| 480 | #N/A
| 481 | #N/A
| 482 | #N/A
| 483 | #N/A
| 484 | #N/A
| 485 | #N/A
| 486 | #N/A
| 487 | #N/A
| 488 | #N/A
| 489 | #N/A
| 490 | #N/A
| 491 | #N/A
| 492 | #N/A
| 493 | #N/A
| 494 | #N/A
| 495 | #N/A
| 496 | #N/A
| 497 | #N/A
| 498 | #N/A
| 499 | #N/A
| 500 | #N/A
| 501 | #N/A
| 502 | #N/A
| 503 | #N/A
| 504 | #N/A
| 505 | #N/A
| 506 | #N/A
| 507 | #N/A
| 508 | #N/A
| 509 | #N/A
| 510 | #N/A
| 511 | #N/A
| 512 | #N/A
| 513 | #N/A
| 514 | #N/A
| 515 | #N/A
| 516 | #N/A
| 517 | #N/A
| 518 | #N/A
| 519 | #N/A
| 520 | #N/A
| 521 | #N/A
| 522 | #N/A
| 523 | #N/A
| 524 | #N/A
| 525 | #N/A
| 526 | #N/A
| 527 | #N/A
| 528 | #N/A
| 529 | #N/A
| 530 | #N/A
| 531 | #N/A
| 532 | #N/A
| 533 | #N/A
| 534 | #N/A
| 535 | #N/A
| 536 | #N/A
| 537 | #N/A
| 538 | #N/A
| 539 | #N/A
| 540 | #N/A
| 541 | #N/A
| 542 | #N/A
| 543 | #N/A
| 544 | #N/A
| 545 | #N/A
| 546 | #N/A
| 547 | #N/A
| 548 | #N/A
| 549 | #N/A
| 550 | #N/A
| 551 | #N/A
| 552 | #N/A
| 553 | #N/A
| 554 | #N/A
| 555 | #N/A
| 556 | #N/A
| 557 | #N/A
| 558 | #N/A
| 559 | #N/A
| 560 | #N/A
| 561 | #N/A
| 562 | #N/A
| 563 | #N/A
| 564 | #N/A
| 565 | #N/A
| 566 | #N/A
| 567 | #N/A
| 568 | #N/A
| 569 | #N/A
| 570 | #N/A
| 571 | #N/A
| 572 | #N/A
| 573 | #N/A
| 574 | #N/A
| 575 | #N/A
| 576 | #N/A
| 577 | #N/A
| 578 | #N/A
| 579 | #N/A
| 580 | #N/A
| 581 | #N/A
| 582 | #N/A
| 583 | #N/A
| 584 | #N/A
| 585 | #N/A
| 586 | #N/A
| 587 | #N/A
| 588 | #N/A
| 589 | #N/A
| 590 | #N/A
| 591 | #N/A
| 592 | #N/A
| 593 | #N/A
| 594 | #N/A
| 595 | #N/A
| 596 | #N/A
| 597 | #N/A
| 598 | #N/A
| 599 | #N/A
| 600 | #N/A
| 601 | #N/A
| 602 | #N/A
| 603 | #N/A
| 604 | #N/A
| 605 | #N/A
| 606 | #N/A
| 607 | #N/A
| 608 | #N/A
| 609 | #N/A
| 610 | #N/A
| 611 | #N/A
| 612 | #N/A
| 613 | #N/A
| 614 | #N/A
| 615 | #N/A
| 616 | #N/A
| 617 | #N/A
| 618 | #N/A
| 619 | #N/A
| 620 | #N/A
| 621 | #N/A
| 622 | #N/A
| 623 | #N/A
| 624 | #N/A
| 625 | #N/A
| 626 | #N/A
| 627 | #N/A
| 628 | #N/A
| 629 | #N/A
| 630 | #N/A
| 631 | #N/A
| 632 | #N/A
| 633 | #N/A
| 634 | #N/A
| 635 | #N/A
| 636 | #N/A
| 637 | #N/A
| 638 | #N/A
| 639 | #N/A
| 640 | #N/A
| 641 | #N/A
| 642 | #N/A
| 643 | #N/A
| 644 | #N/A
| 645 | #N/A
| 646 | #N/A
| 647 | #N/A
| 648 | #N/A
| 649 | #N/A
| 650 | #N/A
| 651 | #N/A
| 652 | #N/A
| 653 | #N/A
| 654 | #N/A
| 655 | #N/A
| 656 | #N/A
| 657 | #N/A
| 658 | #N/A
| 659 | #N/A
| 660 | #N/A
| 661 | #N/A
| 662 | #N/A
| 663 | #N/A
| 664 | #N/A
| 665 | #N/A
| 666 | #N/A
| 667 | #N/A
| 668 | #N/A
| 669 | #N/A
| 670 | #N/A
| 671 | #N/A
| 672 | #N/A
| 673 | #N/A
| 674 | #N/A
| 675 | #N/A
| 676 | #N/A
| 677 | #N/A
| 678 | #N/A
| 679 | #N/A
| 680 | #N/A
| 681 | #N/A
| 682 | #N/A
| 683 | #N/A
| 684 | #N/A
| 685 | #N/A
| 686 | #N/A
| 687 | #N/A
| 688 | #N/A
| 689 | #N/A
| 690 | #N/A
| 691 | #N/A
| 692 | #N/A
| 693 | #N/A
| 694 | #N/A
| 695 | #N/A
| 696 | #N/A
| 697 | #N/A
| 698 | #N/A
| 699 | #N/A
| 700 | #N/A
| 701 | #N/A
| 702 | #N/A
| 703 | #N/A
| 704 | #N/A
| 705 | #N/A
| 706 | #N/A
| 707 | #N/A
| 708 | #N/A
| 709 | #N/A
| 710 | #N/A
| 711 | #N/A
| 712 | #N/A
| 713 | #N/A
| 714 | #N/A
| 715 | #N/A
| 716 | #N/A
| 717 | #N/A
| 718 | #N/A
| 719 | #N/A
| 720 | #N/A
| 721 | #N/A
| 722 | #N/A
| 723 | #N/A
| 724 | #N/A
| 725 | #N/A
| 726 | #N/A
| 727 | #N/A
| 728 | #N/A
| 729 | #N/A
| 730 | #N/A
| 731 | #N/A
| 732 | #N/A
| 733 | #N/A
| 734 | #N/A
| 735 | #N/A
| 736 | #N/A
| 737 | #N/A
| 738 | #N/A
| 739 | #N/A
| 740 | #N/A
| 741 | #N/A
| 742 | #N/A
| 743 | #N/A
| 744 | #N/A
| 745 | #N/A
| 746 | #N/A
| 747 | #N/A
| 748 | #N/A
| 749 | #N/A
| 750 | #N/A
| 751 | #N/A
| 752 | #N/A
| 753 | #N/A
| 754 | #N/A
| 755 | #N/A
| 756 | #N/A
| 757 | #N/A
| 758 | #N/A
| 759 | #N/A
| 760 | #N/A
| 761 | #N/A
| 762 | #N/A
| 763 | #N/A
| 764 | #N/A
| 765 | #N/A
| 766 | #N/A
| 767 | #N/A
| 768 | #N/A
| 769 | #N/A
| 770 | #N/A
| 771 | #N/A
| 772 | #N/A
| 773 | #N/A
| 774 | #N/A
| 775 | #N/A
| 776 | #N/A
| 777 | #N/A
| 778 | #N/A
| 779 | #N/A
| 780 | #N/A
| 781 | #N/A
| 782 | #N/A
| 783 | #N/A
| 784 | #N/A
| 785 | #N/A
| 786 | #N/A
| 787 | #N/A
| 788 | #N/A
| 789 | #N/A
| 790 | #N/A
| 791 | #N/A
| 792 | #N/A
| 793 | #N/A
| 794 | #N/A
| 795 | #N/A
| 796 | #N/A
| 797 | #N/A
| 798 | #N/A
| 799 | #N/A
| 800 | #N/A
| 801 | #N/A
| 802 | #N/A
| 803 | #N/A
| 804 | #N/A
| 805 | #N/A
| 806 | #N/A
| 807 | #N/A
| 808 | #N/A
| 809 | #N/A
| 810 | #N/A
| 811 | #N/A
| 812 | #N/A
| 813 | #N/A
| 814 | #N/A
| 815 | #N/A
| 816 | #N/A
| 817 | #N/A
| 818 | #N/A
| 819 | #N/A
| 820 | #N/A
| 821 | #N/A
| 822 | #N/A
| 823 | #N/A
| 824 | #N/A
| 825 | #N/A
| 826 | #N/A
| 827 | #N/A
| 828 | #N/A
| 829 | #N/A
| 830 | #N/A
| 831 | #N/A
| 832 | #N/A
| 833 | #N/A
| 834 | #N/A
| 835 | #N/A
| 836 | #N/A
| 837 | #N/A
| 838 | #N/A
| 839 | #N/A
| 840 | #N/A
| 841 | #N/A
| 842 | #N/A
| 843 | #N/A
| 844 | #N/A
| 845 | #N/A
| 846 | #N/A
| 847 | #N/A
| 848 | #N/A
| 849 | #N/A
| 850 | #N/A
| 851 | #N/A
| 852 | #N/A
| 853 | #N/A
| 854 | #N/A
| 855 | #N/A
| 856 | #N/A
| 857 | #N/A
| 858 | #N/A
| 859 | #N/A
| 860 | #N/A
| 861 | #N/A
| 862 | #N/A
| 863 | #N/A
| 864 | #N/A
| 865 | #N/A
| 866 | #N/A
| 867 | #N/A
| 868 | #N/A
| 869 | #N/A
| 870 | #N/A
| 871 | #N/A
| 872 | #N/A
| 873 | #N/A
| 874 | #N/A
| 875 | #N/A
| 876 | #N/A
| 877 | #N/A
| 878 | #N/A
| 879 | #N/A
| 880 | #N/A
| 881 | #N/A
| 882 | #N/A
| 883 | #N/A
| 884 | #N/A
| 885 | #N/A
| 886 | #N/A
| 887 | #N/A
| 888 | #N/A
| 889 | #N/A
| 890 | #N/A
| 891 | #N/A
| 892 | #N/A
| 893 | #N/A
| 894 | #N/A
| 895 | #N/A
| 896 | #N/A
| 897 | #N/A
| 898 | #N/A
| 899 | #N/A
| 900 | #N/A
| 901 | #N/A
| 902 | #N/A
| 903 | #N/A
| 904 | #N/A
| 905 | #N/A
| 906 | #N/A
| 907 | #N/A
| 908 | #N/A
| 909 | #N/A
| 910 | #N/A
| 911 | #N/A
| 912 | #N/A
| 913 | #N/A
| 914 | #N/A
| 915 | #N/A
| 916 | #N/A
| 917 | #N/A
| 918 | #N/A
| 919 | #N/A
| 920 | #N/A
| 921 | #N/A
| 922 | #N/A
| 923 | #N/A
| 924 | #N/A
| 925 | #N/A
| 926 | #N/A
| 927 | #N/A
| 928 | #N/A
| 929 | #N/A
| 930 | #N/A
| 931 | #N/A
| 932 | #N/A
| 933 | #N/A
| 934 | #N/A
| 935 | #N/A
| 936 | #N/A
| 937 | #N/A
| 938 | #N/A
| 939 | #N/A
| 940 | #N/A
| 941 | #N/A
| 942 | #N/A
| 943 | #N/A
| 944 | #N/A
| 945 | #N/A
| 946 | #N/A
| 947 | #N/A
| 948 | #N/A
| 949 | #N/A
| 950 | #N/A
| 951 | #N/A
| 952 | #N/A
| 953 | #N/A
| 954 | #N/A
| 955 | #N/A
| 956 | #N/A
| 957 | #N/A
| 958 | #N/A
| 959 | #N/A
| 960 | #N/A
| 961 | #N/A
| 962 | #N/A
| 963 | #N/A
| 964 | #N/A
| 965 | #N/A
| 966 | #N/A
| 967 | #N/A
| 968 | #N/A
| 969 | #N/A
| 970 | #N/A
| 971 | #N/A
| 972 | #N/A
| 973 | #N/A
| 974 | #N/A
| 975 | #N/A
| 976 | #N/A
| 977 | #N/A
| 978 | #N/A
| 979 | #N/A
| 980 | #N/A
| 981 | #N/A
| 982 | #N/A
| 983 | #N/A
| 984 | #N/A
| 985 | #N/A
| 986 | #N/A
| 987 | #N/A
| 988 | #N/A
| 989 | #N/A
| 990 | #N/A
| 991 | #N/A
| 992 | #N/A
| 993 | #N/A
| 994 | #N/A
| 995 | #N/A
| 996 | #N/A
| 997 | #N/A
| 998 | #N/A
| 999 | #N/A
| 1000 | #N/A

## Photos
Title Block
Test Report Template Name: | Consumer Boiler
Version Number: | v1.1 | Back to Instructions tab
Latest Template Revision: | 2019-09-13
Tab Name: | Photos
File Name: | Consumer Boiler - v1.1.xlsx
Test Completion Date: | 0
1. Nameplate showing model number and serial number (if applicable)
2. FTC EnergyGuide and ENERGY STAR labels (if present)
3. Test unit from all sides (including photo of control panel)
4. Exact placement of all sensors on, in, or around the device
5. Photos of Ducts and Plenums |  |  | 6. Photos of Stack and Thermocouple Grid in Flue
7. Photos of Ambient Temperature Sensors |  |  | 8. Photos of Burner
9. Photo of Controls at Maximum Input |  |  | 10. Photo of Controls at Reduced Input
11. Arrival Photos (if necessary)
12. Additional Photos (if necessary)

## Comments
Title Block
Test Report Template Name: | Consumer Boiler
Version Number: | v1.1 | Back to Instructions tab
Latest Template Revision: | 2019-09-13
Tab Name: | Comments
File Name: | Consumer Boiler - v1.1.xlsx
Test Completion Date: | 0
Enter all anomalies with the test.

## Report Sign-Off Block
Title Block
Test Report Template Name: | Consumer Boiler
Version Number: | v1.1 |  | Back to Instructions tab
Latest Template Revision: | 2019-09-13
Tab Name: | Report Sign-Off Block
File Name: | Consumer Boiler - v1.1.xlsx
Test Completion Date: | 0
Test Report Sign-Off Block
By signing in the space below, we certify that the information and data in this report: (1) were obtained from the specific test unit under test; (2) were obtained during the specific test being reported; (3) were not copied from any other source, except where instructed to do so; and (4) were not altered or modified in any way.
Role |  | Date | Entity
Test Completion |  | 0 | [Test Lab Name]
Template Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]

## Drop-Downs and Tables
Title Block
Test Report Template Name: | Consumer Boiler
Version Number: | v1.1 |  |  |  |  | Back to Instructions tab
Latest Template Revision: | 2019-09-13
Tab Name: | Drop-Downs and Tables
File Name: | Consumer Boiler - v1.1.xlsx
Test Completion Date: | 0
Drop Downs
Product
Furnace
Boiler
Heating Medium
Air
Water
Steam
Circulation
Gravity (air, steam)
Forced (air, water)
Energy Source | Fuel Used
Gas | Natural Gas
Oil | Manufactured Gas
Electricity | Butane Gas
Propane Gas
No. 1 Fuel Oil
No. 2 Fuel Oil
Electricity
Burner Type | Power Burner Type
Atmospheric | N/A
Power | Natural Draft
Forced Draft
Induced Draft
Pulse Combustion
Flue Gas
N/A
Non-Condensing
Condensing
Ignition
N/A
Continuous Burning Pilot
Intermittent or Interrupted Operating Ignition
Draft Equipment
None
Direct Exhaust
Draft Hood
Integral Draft Diverter
Barometric Draft Control
Off_Cycle_Devices
None
Stack Damper
Electro-mechanical Inlet Damper
Electro-Mechanical Flue Damper
Installation | Direct Vent (Indoor Installations Only) | Combustion_Air
Indoor | N/A | Indoor
Outdoor | No | Outdoor
Isolated Combustion System | Yes. With Heat Exchange.
Yes. Without Heat Exchange.
Control
Single Stage
Two-Stage Modulating
Step Modulating
Jacket_Loss
Default Value
Optional Test
Yes_No
Yes
No
Tables from ASHRAE 103-1993
Table 1: (from 8.2.1.3)
Type | Heating Value (Btu/SCF) | Sp. Gr. (Air = 1) | Test Pressure (in. Water)
|  |  | Normal | Increased
Natural Gas | 1025 | 0.65 | 7 | 10.5
Manufactured Gas | 535 | 0.38 | 3.5 | 5.25
Butane Gas | 3175 | 2 | 11 | 13
Propane Gas | 2500 | 1.53 | 11 | 13
Table 2: (from 8.2.2.4.1)
Properties | No. 1 |  | No. 2
| Min | Max | Min | Max
Gravity, degree API* | 38 | 44 | 30 | 35
Viscosity: Saybolt universal at 100°F | - | - | 34 | 37.9
Percent of carbon residue on 10% residum | 0.1 | 0.15 | 0.2 | 0.3
*Gravity and viscosity shall conform to the above limits. Other properties shall conform to the limits of ASTM D396-90A (see Table 3)
**Carbon residue for other than atomizing burners.
Table 3: (from 8.3.1.2)
Grade of Fuel Oil | Flash Point | Pour Point | Water and Sediment | Carbon on 10% Bottoms | Distillation Temperatures |  |  | Saybolt Viscosity |  | Kinematic Viscosity |  | Gravity | Copper Strip Corrosion | Sulfur
[5 empty] | F |  |  | sec |  | centistokes |  | deg API |  | %
| F | F | % by Vol. | % | 10% Point | 90% Point |  | Universal at 100F |  | At 100F
| Min | Max | Max | Max | Min | Min | Max | Min | Max | Min | Max | Min | Max | Max
No. 1 A distillate oil intended for vaporizing pot-type burners and other burners requiring this grade of fuel | 100 | 0 | Trace | 0.15 | 420 | - | 550 | - | - | 1.4 | 2.2 | 35 | No. 3 | 0.5
No. 2 A distillate oil for general purpose domestic heating for use in burners not requiring No. 1 fuel oil | 100 | 20 | 0.05 | 0.35 | ?? | 540 | 640 | 32.6 | 37.93 | 2 | 3.6 | 30 | - | 0.5
a lt is the intent of lhese classifications lhat failure to meet any requirement of a given grade does not automatically place an oil in the next lower grade unless in fact it meets all requirements of the lower grade.
b Outside USA, the sulfur limit for No. 2 shall be 1.0%.
c Legal requirements to be met.
d Lower or higher pour points may be specified whenever required by conditions of storage or use. When point less than 0°F is specified, the minimum viscosity shall be 1.8 cSt (32.0 sec Saybolt Universal) and the minimum 90% point shall be waived.
e The 10% distillation temperature point may be specified at 440°F (226°C) maximum for use in other lhan atomizing burners.
f Viscosity values in parentheses are for information only and not necessarily limiting.
g The amount of water by distillation plus the sediment by extraction shall not exceed 2.00%. The amount of sediment by extraction shall not exceed 0.50%. A deduction in quantity shall be made for all water and sediment in excess of 1.0%.
Table 4: Relation of Furnace input to Minimum External Static Pressure* for Performance and Rating Test Purposes (All tests preformed without a filter)
Input to Furnace Range |  | External Static Pressure (in. water) |  |  | Max Input Falls in range?
Low | High | Oil Furnace with a Temperature Rise Less Than or Equal to 65F | Oil Furnace with a Temperature Rise Greater Than 65F | Gas Furnace
0 | 55000 | 0.38 | 0.18 | 0.18 | No
55001 | 80000 | 0.38 | 0.2 | 0.2 | No
80001 | 100000 | 0.38 | 0.23 | 0.23 | No
100001 | 200000 | 0.48 | 0.28 | 0.28 | No
200001 | 300000 | 0.58 | 0.33 | 0.33 | No
* These static pressures apply for operation at maximum rated input only.
Table 5: Minimum External Static Pressure for Electric Central Furnaces
Standard Air Quantity |  | Min. External Static Pressure
scfm
Low | High | in. water
0 | 849 | 0.12
850 | 1599 | 0.15
1600 | 2599 | 0.2
2600 | 3999 | 0.25
Table 6: System Numbers
Locate the column where all the characteristics arc applicable to the equipment under test. | [9 empty] | System Number
Characteristics | 1 | 2 | 3 | 4 | 5 | 6 | 8 | 9 | 10 | Product Characteristics not filled in correctly
Indoor Combustion Air | X | X | X | X | X | X | X |  |  | X
Outdoor, Direct Vent or Isolated Combust. System | [7 empty] | X | X
Direct Exhaust |  |  | X |  |  |  |  | (May or may not be present. Does not affect the results.) |  | Fill in General Info
Draft Hood or Draft Diverter | X | X |  |  | X | X |  |  |  | Fill in General Info
Barometric Draft Control |  |  |  | X |  |  | X |  |  | Fill in General Info
Electrical/Mechanical Stack Damper |  |  |  |  | X | X | X |  |  | Fill in General Info
Atmospheric Burner | X |  |  |  | X |  |  | X |  | Fill in General Info
Power Burner |  | X | X | X |  | X | X |  | X | Fill in General Info
Burner Inlet Damper or Flue Damper** | X | X | X | X |  |  |  | X | X | Fill in General Info
DF (Constant) | 1 | 0.4 | 0.4 | 0.4 | 1 | 0.4 | 0.4 | 1 | 0.4
DF (Based on DP) | DP+ | DP | DP | DP |  | DP | DP | DP* | DP
DS | 1 | 1 | DF | 0.85 or (0.79+DP)/1.4 | DO | DO | 0.85xDO or (0.79+DP)/1.4xDO
S/F | * | * | 1 | 1.4 or test# | * | * | 1.4 or test#
* Calculated from CO2 values.
* For direct vent or atmospheric burner w/bumer inlet damper or flue damper that closes within 10 seconds after the burner shuts off.
** Power burner may or may not have electro-mechanical inlet or flue damper.
`+ For atmospheric burner w/burner inlet damper or flue damper that closes within 10 seconds after the burner shuts off.
Note: System 7 was intentionally omitted.
Table 7: Fuel Characteristics and Parameters for Calculating Steady-State Sensible Heat Loss{LS,SS} and Steady-State Efficiency {EffySS}
Fuel | HHVA | A/F | LL,A | A | B | 1 | 2 | 3 | 4 | 5
[6 empty] | CF(1) | CF(2) | CF(3) | CF(4) | CF(5)
No. 1 Fuel Oil | 19800 | 14.56 | 6.55 | 0.0679 | 14.22 | 0.24417 | 3.3711e-06 | 8.8906e-09 | -1.3619e-12 | -1.4367e-16
No. 2 Fuel Oil | 19500 | 14.49 | 6.5 | 0.06668 | 14.34 | 0.24361 | 3.6703e-06 | 8.7099e-09 | -1.3094e-12 | 1.5029e-16
Natural Gas | 20120 | 14.45 | 9.55 | 0.09194 | 10.96 | 0.25949 | -4.9476e-06 | 1.3886e-08 | -2.806e-12 | 3.7682e-17
Manufactured Gas | 18500 | 11.81 | 10.14 | 0.09646 | 10.1 | 0.26598 | -7.7561e-06 | 1.5834e-08 | -3.4194e-12 | 1.2159e-16
Propane Gas | 21500 | 15.58 | 7.99 | 0.0841 | 12.6 | 0.25164 | -6.4145e-06 | 1.1315e-08 | -2.0657e-12 | -5.4897e-17
Butane Gas | 20890 | 15.36 | 7.79 | 0.0808 | 12.93 | 0.25011 | 1.7737e-06 | 1.082e-08 | -1.9221e-12 | -7.3013e-17
Air | [5 empty] | 0.25462 | -3.026e-05 | 2.7609e-08 | -7.4253e-12 | 6.4307e-16
Table 8: Output Capacity (Btu/h) DHR (kBtu/h)
Range |  | Average Design Heating Requirements (DHR) | Typical Design Heating Requirements
Low | High | kBtu/h | kBtu/h
5000 | 10000 | 5 | 5
11000 | 16000 | 10 | 5, 10
17000 | 25000 | 15 | 10, 15
26000 | 42000 | 20 | 15, 20, 25
43000 | 59000 | 30 | 25, 30, 35, 40
60000 | 76000 | 40 | 35, 40, 45, 50
77000 | 93000 | 50 | 40, 45, 50, 60
94000 | 110000 | 60 | 50, 60, 70, 80
111000 | 127000 | 70 | 60, 70, 80, 90
127000 | 144000 | 80 | 70, 80, 90, 100
145000 | 161000 | 90 | 80, 90, 100, 110, 120
162000 | 178000 | 100 | 90, 100, 110, 120, 130
179000 | 195000 | 110 | 100, 110, 120, 130, 140
196000 | + | 130 | 120, 130, 140, 150, 160
Table 9: Average Burner On-Time and Off-Time Per Cycle for Furnaces and Boilers (Minutes}
| Furnaces |  | Boilers
Control Type | ton | toff | ton | toff
Single Stage | 3.87 | 13.3 | 9.68 | 33.26
Two Stage | 10 | 10 | 15 | 15
Step Modulating | 10 | 10 | 15 | 15
Table 10: Fractional Heating Loads and Average Outdoor Temperatures for Furnaces and Boilers Equipped with Modulating Controls
Balance Point Temperature Range (F) |  | Fractional Heating Load |  | Average Outdoor Temperature (F)
TC |  | Reduced Rate | Modulating or Maximum Rate | Reduced Rate | Modulating or Maximum Rate
Low | High | XR | XH | TOA,R | TOA,H
6 | 15 | 0.95 | 0.05 | 41 | 9
16 | 20 | 0.9 | 0.1 | 42 | 14
21 | 25 | 0.84 | 0.16 | 43 | 18
26 | 28 | 0.77 | 0.23 | 44 | 22
29 | 31 | 0.7 | 0.3 | 45 | 24
32 | 33 | 0.66 | 0.34 | 46 | 26
34 | 35 | 0.6 | 0.4 | 47 | 27
36 | 37 | 0.54 | 0.46 | 48 | 28
38 | 39 | 0.48 | 0.52 | 48 | 30
40 | 41 | 0.42 | 0.58 | 49 | 31
42 | 43 | 0.35 | 0.65 | 50 | 32
44 | 45 | 0.29 | 0.71 | 51 | 33
46 | 47 | 0.23 | 0.77 | 52 | 35
48 | 49 | 0.18 | 0.82 | 54 | 36
50 | 52 | 0.12 | 0.88 | 55 | 37
53 | 57 | 0.07 | 0.93 | 58 | 39
58 | 62 | 0.02 | 0.98 | 61 | 40
NOTE: This table is based on national average 5,200 degree-days.
ANSI/ASHRAE Section 6: Instruments (Accuracy)
All instruments shall be in working order and be calibrated periodically. Records of periodic calibration shall be kept and they shall contain at a minimum the date of calibration, method of calibration, and reference standard used.
Measurement | Accuracy
Thermometer | ± | 1 | °F
Thermocouple | ± | 2 | °F
Thermocouple Grid | ± | 2 | °F
Gas Pressure | ± | 0.2 | in. H2O
Oil Pressure | ± | 0.5 | psi
Air Pressure | ± | 0.01 | in. H2O
Steam Pressure | ± | 0.2 | in. HG
Draft | ± | 0.005 | in. H2O
CO2 | ± | 0.1 | %
Weight | ± | 0.5 | % of quantity measured
Volume | ± | 0.5 | % of quantity measured
Time | ± | 0.5 | seconds/hour
Smoke | Smoke-measuring instruments shall comply with requirements for smoke meters as outlined in Test Method for Smoke Density in the Flue Gases from Burning Distillate Fuels, ASTM-D-2156-80 (1980).
Tracer Gas Mass Flow Rate | ± | 2 | %
Electrical Energy Flow Rate | ± | 1 | %
Gas Energy Flow Rate | ± | 1 | %
Oil Energy Flow Rate | ± | 1 | %
HHV: Gas | ± | 1 | %
HHV: Oil | ± | 1 | %
Other

## Version Control
Title Block
Test Report Template Name: | Consumer Boiler
Version Number: | v1.1
Latest Template Revision: | 2019-09-13
Tab Name: | Version Control
File Name: | Consumer Boiler - v1.1.xlsx
Test Completion Date: | 0
Revisions List
Version | Date
v0.1 | 2019-02-27
v0.2 | 2019-06-28
v0.3 | 2019-08-08
v1.0 | 2019-08-22
v1.1 | 2019-09-13